National Vocational Diploma level – 5 in

“Automation & Process Control”

Curriculum

Date of validation: 09/11/2020

National Vocational and Technical Training Commission (NAVTTC)

Government of Pakistan

Table of Contents

1. 	Introduction	1

1.1.	Purpose of the training program:	2

1.2.	Overall objectives of training program:	2

1.3.	Competencies to be gained after completion of course:	3

1.4.	Possible available job opportunities available immediately and later in the future	10

1.5.	Entry level of trainees:	10

1.6.	Minimum qualification of trainer/instructor:	11

1.7.	Recommended trainer: trainee ratio	11

1.8.	Medium of instruction i.e. language of instruction:	12

1.9.	Duration of the course (Total time, Theory & Practical time):	12

2.	Overview of the Curriculum for Automation & Process Control Technology:	14

A- Maintain Occupational Health and Safety	22

0714E&A1: Maintain Health and Safety	22

0714E&A2: Perform safety practices at workplace	33

0714E&A3: Develop professionalism.	41

B- Automation Workshop Practice	48

0714E&A4: Connect Tubing and Fittings	48

0714E&A5: Perform Basic Machining Operation.	53

0714E&A6: Perform Arc Welding.	57

C- Basic Electrical Wiring (Single Phase)	62

0714E&A7: Maintain Tools & Equipment.	62

0714E&A8: Make Cable/Wire Joints	64

0714E&A9: Prepare and Install Distribution Boards	67

0714E&A10: Carryout Basic Electrical Installation	69

0714E&A11: Install Simple Electrical Wiring	72

0714E&A12: Perform Testing of Electrical Wiring	77

0714E&A13: Repair/ Maintenance of Electrical Installations	82

0714E&A14: Carry Out Electrical Planning and Estimation	84

D- Basic Electrical Engineering	88

0714E&A31: Operate Measuring Instruments.	88

0714E&A32: Verify Ohm’s Law & Kirchhoff’s Law by Implementing Series/Parallel Circuits.	89

0714E&A33: Measure Electrical Power, Energy, Power Factor & Determine Phase Sequence	92

0714E&A35: Implement Electromagnet to See Various Effects & Verify Faradays Law	95

0714E&A36: Verify Series and Parallel Combination of Capacitors & Determine Break down Voltage of Capacitor	98

E-Engineering Drawing	100

0714E&A44: Perform Basic Manual Drawing.	100

0714E&A45: Construct different Engineering Curves	109

0714E&A46: Construct Multi-View Drawings.	120

0714E&A47: Perform CAD Software.	129

0714E&A48: Develop 2D using CAD software.	131

0714E&A49: Develop 3D drawing using CAD software.	133

0714E&A50: Identify Instrumentation Drawing	135

0714E&A51: Construct Instrumentation Drawing	141

0714E&A52: Construct Instrumentation Loop diagram or Loop sheet	145

G-Basic Electronics (Analog)	147

0714E&A37: Identify Basic Electronics Components	147

0714E&A38: Design Rectifier using Diode	149

0714E&A39: Carry out Diode Application	152

0714E&A40: Implement Bipolar Junction Transistor (BJT) in Different Applications	153

0714E&A41: Implement Field Effect Transistor (FET) in Different Applications	156

0714E&A42: Implement Thyristor Family in Various Application	160

0714E&A43: Application of Operational Amplifier	162

H- Metrology	165

0714E&A53: Take measurements with graduated tools	165

0714E&A54: Take measurements with combination set	168

0714E&A00: Perform Leveling.	171

0714E&A55: Take measurements with gauges	173

0714E&A56: Perform measurements through Micrometer	175

0714E&A57: Measure dimensions with Vernier tools	177

0714E&A58:  Measure angles with angle measuring Instruments.	179

0714E&A00: Measure Threads and Gears	181

J-Sensors & Actuators	183

0714E&A64: Interface of Sensor	183

0714E&A65: Interface of Actuator	188

K-Process Variable Measurements	190

0714E&A66: Calibrate Flow Instrument	190

0714E&A67: Calibrate Pressure Instrument	196

0714E&A68: Calibrate Level Instrument	199

0714E&A69: Calibrate Temperature Instrument	203

L-Digital Electronics	208

0714E&A70: Verify truth table using digital gates.	208

0714E&A71: Construct and verify combinational logic circuits.	212

0714E&A72: Construct and verify functions of flip flop.	217

0714E&A73: Use 555 Timer IC as Multivibrator	219

M- Industrial Electronics	221

0714E&A74: Implement diode and Thyristor in power control application.	221

0714E&A75: Construct single phase and Three phase Inverter	224

0714E&A76: Operate Digital Sensor Switches	226

0714E&A77: Control Speed of DC/AC Motors	228

N- Electrical instrumentation and Calibration	231

0714E&A78: Perform Test / Calibrate Flow Sensor	231

0714E&A79: Perform Test / Calibrate Level Sensor	235

0714E&A80: Perform Test / Calibrate Pressure Sensor	238

0714E&A81: Perform Test / Calibrate Temperature Sensor	241

O- Electrical Machines	245

0714E&A82: Verify Basic Laws of Electrical Machines	245

0714E&A83: Analyze DC Generator	250

0714E&A84: Analyze DC Motors	256

0714E&A85: Perform Tests On DC Motors	259

0714E&A86: Repair/ Maintenance and Service of Dc Motors and Dc Generators.	270

0714E&A87: Operate Single Phase Motors.	275

0714E&A88: Operate Special Purpose Motors	278

0714E&A89: Analyze Three Phase Motors	283

Q-Pneumatics & Hydraulics	298

0714E&A100: Install / service Compressed Air Generating Units	298

Objective: This Module covers the knowledge and skills required to install/operate and service compressed air generating units.	298

0714E&A101:  Install Pneumatic Circuit Elements.	300

0714E&A102:  Install / Service Hydraulic Power Pack	302

R-Programming	309

0714E&A103:  Programming- I	309

0714E&A104: Programming- II	311

0714E&A105: Programming- III	317

S-PLC Supervisor	326

0714E&A106:  Install PLC software and Simulator	326

0714E&A107: Interface PLC with system - I	331

0714E&A108: Program PLC using Ladder Logic	333

0714E&A109: Commissioning and Testing of PLC	336

0714E&A110: Install Relays and Switches in circuits	342

0714E&A111: Carry out Industrial Automation on PLC	345

0714E&A112:  Interface PLC with system-II	350

T-Industrial Instrumentation & Control	353

0714E&A113:  Install Transducers & Transmitters in Industrial Application	353

0714E&A114:  Install the Process regulators	357

0714E&A115:  Install the Variable Frequency Drive	360

0714E&A116:  Install Pneumatic & Hydraulic system in the Industry	361

0714E&A117:  Installation & Setup Procedure for Digital Pressure, Temperature, Level & Flow Controllers	364

U-Repair & Maintenance of Automation Equipment	369

0714E&A118:  Identify Fault in Automation/ Process Equipment Installation.	369

0714E&A119:  Perform Troubleshooting of equipment.	372

0714E&A120:  Perform Preventive Maintenance of Equipment.	373

V-Boiler Instrumentation	375

0714E&A121:  Operate Boiler Control system	375

0714E&A122:  Install the Boiler Control system	379

W-Application of Automation in daily life	383

0714E&A123:  Operate Product Counter	383

0714E&A124:  Operate ON / OFF / Delay Timers	385

0714E&A125:  Operate speed controller	387

0714E&A126:  Operate Level Detector	389

0714E&A127:  Operate Digital Weighing Scale	391

0714E&A128:  Operate Temperature Controller	393

0714E&A129:  Operate Pressure Controller	394

X-Building Automation System Supervisor	396

0714E&A130:  Designing of Building Automation System	396

0714E&A131:  Perform Security Automation	399

0714E&A132:  Perform Energy management and Monitoring	401

0714E&A133:  Perform HVAC inspection & Maintenance	404

0714E&A134:  Perform Elevator Maintenance	407

List of Tools and Equipment:	411

6.	Members of the Curriculum Development Committee	419

7.	Members of the Curriculum Review & Validation Committee	420

# 1. 	Introduction

This qualification introduces “Automation and Process Control” so that the student will have the competence to install and implement automated process control systems. This is done by presenting relevant topics from PLC, sensors, actuators, calibration of instruments and control systems, and computer vision. Python, Raspberry programming is an important part of the course is to ensure that the student acquires skills in kinematics and computer vision systems for automated process control by using computer vision and contact force sensors will be presented.

Students will gain hands on experience in automated process control system installation, calibration, repair & maintenance along with the some fabrication and machining work.

The National Skills Strategy (NSS) aims at achieving a paradigm shift from time-bound   and supply led to competency-based and demand driven training in Pakistan. Competency-based training approach focuses on the demonstration of actual skills required in the workplace/industry. To achieve this strategy, NAVTTC in collaboration with GIZ is involved in the development process of CBT program to ensure competent skilled labor in demand driven vocational trades.

National Vocational Qualification Framework (NVQF) as designed in consultation with the stakeholders including academia, researchers, industry, chambers and TEVTAs. Its aim is to identify knowledge & skills required for a qualification, determine equivalence, provide guidelines for Recognition of Prior Learning (RPL) and assure quality of training. NVQF designed for the Vertical and horizontal progression for learners, recognition of qualification, meeting with the national and international standards, facilitate conversion of informal training to formal training through RPL, improvement in quality of training and increased options for learners for selecting training programs in different trades. Competency Standards are performance specification that identify the knowledge and competencies an individual need to succeed in the workplace.

The National Competency Standards could be used as a referral document for the development of curriculum by training institutions.

## Purpose of the training program:

This qualification will help in the installation and calibration of automated process control systems. The candidate will be able to perform fundamental operations of automated process control functions, systems, understand the concepts of various process control systems, their functions and designs, grasp concepts of various process control systems and their integration with various digital system and there troubleshooting. This qualification will help candidate to assembling, synchronization and construct the automated process control system, identify and implement certain automation components, elaborate linkage between the components and their industrial workability & maintenance of various process equipment and devices.

This course enables the youth with greater employment opportunities and entrepreneurial skills.

  - Overall objectives of training program:

The overall objective of the Automation & Process Control program is to enable students to:

The Automation & Process Control technology qualification consists of level 2-5 theoretical and practical competences, which enabling trainee to learn operational techniques of Robotics technology.

The main objectives of the Automation & Process Control qualification are as follows:

- Maintain Occupational Health and Safety

- Automation Workshop Practice

- Basic Electrical Wiring (Single Phase)

- Basic Electrical Engineering

- Engineering Drawing

- Digital skills

- Basic Electronics (Analog)

- Metrology

- Manage IT Skills

- Sensors & Actuators

- Process Variable Measurements

- Digital Electronics

- Industrial Electronics

- Electrical instrumentation and Calibration

- Electrical Machines

- Manage Soft Skills

- Pneumatics & Hydraulics

- Programming

- PLC Supervisor

- Industrial Instrumentation & Control

- Repair & Maintenance of Automation Equipment

- Boiler Instrumentation

- Application of Automation in daily life

- Building Automation System Supervisor

- Develop Entrepreneur Skills

## Competencies to be gained after completion of course:

At the end of the course, the trainee has attained the following competencies:

National Qualification in Automation & Process Control level 2.

- Maintain Health and Safety

- Perform Safety Practices at Workplace

- Develop Professionalism.

- Connect Tubing and Fittings

- Perform Basic Machining Operations

- Perform Arc Welding

- Maintain Tools & Equipment.

- Make Cable/Wire Joints

- Prepare and Install Distribution Boards

- Carryout Basic Electrical Installation

- Install Simple Electrical Wiring

- Perform Testing of Electrical Wiring

- Repair/ Maintenance of Electrical Installations

- Carryout Estimation and Planning

- Operate Measuring Instruments.

- Verify Ohm’s Law & Kirchhoff’s Law by Implementing Series/Parallel Circuits.

- Measure Electrical Power, Energy, Power Factor & Determine Phase Sequence

- Implement Electromagnet to See Various Effects & Verify Faradays Laws.

- Verify Law of Combination of Capacitor and Determine Break down voltage of Capacitor.

- Perform Basic Manual Drawing

- Construct different Engineering Curves

- Construct multi-view drawings

- Install CAD Software

- Develop 2D CAD drawings

- Develop 3D CAD drawings

- Construct Instrumentation Drawing

- Construct Instrumentation loop diagram or loop sheet

National Qualification in Automation & Process Control level 3

- Install Computer Operating Systems and Hardware

- Operate Word-Processing Applications

- Operate Spreadsheet Applications

- Operate Presentation Packages

- Perform Writing and Editing Tasks

- Perform Computer Operations

- Use Computer Applications

- Create User Documentation

- Create Technical Documentation

- Create Basic Databases

- Operate Digital Media Technology

- Use Social Media Tools for Collaboration and Engagement

- E-Commerce

- Use Digital Devices

- Identify Basic Electronics Components

- Design a Rectifier using Diode

- Carry out Diode Application

- Implement Bipolar Junction Transistor (BJT) in Different Applications

- Implement Field Effect Transistor (FET) in Different Applications

- Implement Thyristor Family in Various Application

- Applications of Operation Amplifier

- Take measurements with graduated tools

- Take measurements with combination set

- Perform Levelling

- Take measurements with gauges

- Perform measurements through Micrometer

- Measure dimensions with Vernier tools

- Measure angles with angle measuring Instruments

- Measure Threads and Gears

National Qualification in Automation & Process Control level 4

- Operate Basic Computer Functions

- Perform Basic computer Application

- Develop computer application skills

- Develop advance computer application skills

- Explore computer application skills for careers

- Interface of Sensor

- Interface of Actuator

- Calibrate Flow instrument

- Calibrate Pressure Instrument

- Calibrate Level Instrument

- Calibrate Temperature Instrument

- Verify the Truth Tables for Logic Gates

- Construct & Verify the Logic Circuits

- Construct the Flip Flops

- Use 555 IC as a Multi-Vibrator

- Implement the Thyristors in Electronic Circuits

- Implement Single Phase and Three Phase Inverter

- Operate Digital Sensor Switches

- Control speed of DC/AC Motor

- Perform Test / Calibrate Flow Sensor

- Perform Test/Calibrate Level Sensor

- Perform Test / Calibrate Pressure Sensor

- Perform Test / Calibrate Temperature Sensor

- Verify Basic Laws of Electrical Machines

- Analyze Dc Generators

- Perform Tests on Dc Generators

- Analyze Dc Motors

- Perform Tests on Dc Motors

- Repair/ Maintenance and Service of Dc Motors and Dc Generators.

- Operate Single Phase Motors.

- Operate Special Purpose Motors

- Analyze Three Phase Motors

- Follow Basic Communication skills

- Perform Basic Communication

- Communicate at workplace

- Perform Advanced Communication

- Perform managerial Communication skills

National Qualification in Automation & Process Control level 5

- Install / Service Compressed Air Generating Units

- Install Pneumatic Circuit Elements

- Install / Service Hydraulic Power Pack

- Programming-I

- Programming-II

- Programming-III

- Install PLC software and Simulator

- Interface PLC with system-I

- Program PLC using Ladder Logic

- Commissioning and Testing of PLC

- Install Relays and Switches in circuits

- Carry out Industrial Automation on PLC

- Interface PLC with system-II

- Install Transducer & Transmitter in Industrial Application

- Install the process Regulators

- Install the Variable Frequency Drive ( VFD )

- Install Pneumatic & Hydraulic systems in industry

- Installation and setup procedure for Digital Pressure, Temperature, Level and Flow Controllers

- Identify Fault in Automation/ Process Equipment Installation

- Perform Troubleshooting

- Perform Preventive maintenance

- Operate a Boiler Control System

- Install the Boiler Control System

- Operate Product Counter

- Operate ON / OFF / Delay Timers

- Operate Speed Controller

- Operate Level Detector

- Operate Digital Weighing Scale

- Operate Temperature Controller

- Operate Pressure Controller

- Designing of Building Automation System

- Perform Security Automation

- Perform Energy management and Monitoring

- Perform HVAC inspection & Maintenance

- Perform Elevator Maintenance

- Investigate Microbusiness Opportunities

- Develop A Micro Business Proposal

- Develop A marketing Plan

- Develop And Review A Business Plan

- Organize Finances For The Micro Business

- Manage Human Resources

- Market Products And Services

- Monitor And Review Business Performance

- Negotiate For Resolving Business Issues

- Manage Personal Finances

- Coordinate A Work Team

- Lead Small Teams

## Possible available job opportunities available immediately and later in the future

Skilled personnel in the field of Automation & Process Control technology usually get hired in areas pertaining to the light, medium and heavy engineering sector. They can become:

- Maintenance Technician

- Industrial Automation Technician

- Process Control Technician

- Building Automation Technician

- Calibration Lab Technician

- Entrepreneur

- Instructor/trainer (Level 4)

- Associate Automation & Process Control Engineer

Some experienced personnel in the field of Automation & Process Control technology achieve a high level of salaries. There are good prospects for travel both within Pakistan and abroad. The employment outlook in this occupation will be influenced by a wide variety of factors including:

- Trends and events affecting overall employment (especially in the manufacturing industry)

- Location in Pakistan

- Employment turnover (work opportunities generated by people leaving existing positions)

- Occupational growth (work opportunities resulting from the creation of new positions that never existed before)

- Size of the industry

- Flexibility of the applicant (concerning location and schedule of work)

## Entry level of trainees:

The entry for National Vocational Certificate level 2-5, in “Automation & Process Contorol” are given below:

| Title | Entry requirements |
| --- | --- |
| National Vocational Certificate level 2, in Automation & Process Control Technology | Entry for assessment for this qualification is open. However, entry into formal training institutes, based on this qualification is candidate having Secondary level (8 grade) and or National Vocational Certificate level 1. |
| National Vocational Certificate level 3, in Automation & Process Control Technology | Entry for assessment for this qualification is open. However, entry into formal training institutes, based on this qualification is candidate having Secondary level (8 grade) and or National Vocational Certificate level 2. |
| National Vocational Certificate level 4, in Automation & Process Control Technology | Entry for assessment for this qualification is open. However, entry into formal training institutes, based on this qualification is candidate having Matriculation (Science) and or National Vocational Certificate level 3. |
| National Vocational Certificate level 5, in Automation & Process Control Technology | Entry for assessment for this qualification is open. However, entry into formal training institutes, based on this qualification is candidate having Matriculation (Science) and or National Vocational Certificate level 4. |

## Minimum qualification of trainer/instructor:

    - Must be a holder of Bachelor of Technology in Electronics/Electrical/Mechanical/Instrumentation or Automation & Process Control (With three years of experience) or Bachelor of Engineering in Electronics/Electrical/Mechanical/Instrumentation or Automation & Process Control (with one years of experience).

    - Must be able to communicate effectively both orally and in written form.

    - Must be able to perform all competences, given in Automation & Process Control Technology Level 5.

## Recommended trainer: trainee ratio

The recommended maximum trainer: trainee ratio for this program is 1 trainer for 20 to 25 trainees.

## Medium of instruction i.e. language of instruction:

Instructions will be in Urdu/ English/ Local language.

## Duration of the course (Total time, Theory & Practical time):

This curriculum comprises 24 modules. The recommended delivery time is 4070 hours. Delivery of the course could therefore be full time, 5or 6 days a week, for 3 years. Training providers are at liberty to develop other models of delivery, including part-time and evening delivery.

The distribution of contact hours is given below:

Total		-	3600 hours.

Theory	-	955 hours (26.5%)

Practical	-	2645 hours (73.5%)

Description and structure of the course

Following is the structure of the course:

| Level 5 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Competency Standards NVQF Level Category Estimated Contact Hours Credit Th Pr Total Hours |  |  |  |  |  |  |
| Install / Service Compressed Air Generating Units | Level 5 | Technical | 6 | 12 | 18 | 1.8 |
| Install Pneumatic Circuit Elements | Level 5 | Technical | 5 | 15 | 20 | 2 |
| Install / Service Hydraulic Power Pack | Level 5 | Technical | 5 | 15 | 20 | 2 |
| Programming-I | Level 5 | Technical | 12 | 21 | 33 | 3.3 |
| Programming-II | Level 5 | Technical | 15 | 21 | 36 | 3.6 |
| Programming-III | Level 5 | Technical | 10 | 30 | 40 | 4 |
| Install PLC software and Simulator | Level 5 | Technical | 12 | 18 | 30 | 3 |
| Interface PLC with system | Level 5 | Technical | 12 | 18 | 30 | 3 |
| Program PLC using Ladder Logic | Level 5 | Technical | 12 | 24 | 36 | 3.6 |
| Commissioning and Testing of PLC | Level 5 | Technical | 12 | 24 | 36 | 3.6 |
| Install Relays and Switches in circuits | Level 5 | Technical | 12 | 18 | 30 | 3 |
| Carry out Industrial Automation on PLC | Level 5 | Technical | 12 | 24 | 36 | 3.6 |
| Interface PLC with system | Level 5 | Technical | 12 | 24 | 36 | 3.6 |
| Install Transducer & Transmitter in Industrial Application | Level 5 | Technical | 12 | 24 | 36 | 3.6 |
| Install the process Regulators | Level 5 | Technical | 6 | 18 | 24 | 2.4 |
| Install the Variable Frequency Drive ( VFD ) | Level 5 | Technical | 6 | 12 | 18 | 1.8 |
| Install Pneumatic & Hydraulic systems in industry | Level 5 | Technical | 9 | 18 | 27 | 2.7 |
| Installation and setup procedure for Digital Pressure, Temperature, Level and Flow Controllers | Level 5 | Technical | 12 | 24 | 36 | 3.6 |
| Identify Fault in Automation/ Process Equipment Installation | Level 5 | Technical | 6 | 18 | 24 | 2.4 |
| Perform Troubleshooting | Level 5 | Technical | 6 | 18 | 24 | 2.4 |
| Perform Preventive maintenance | Level 5 | Technical | 10 | 18 | 28 | 2.8 |
| Operate a Boiler Control System | Level 5 | Technical | 6 | 18 | 24 | 2.4 |
| Install the Boiler Control System | Level 5 | Technical | 6 | 36 | 42 | 4.2 |
| Operate Product Counter | Level 5 | Technical | 6 | 18 | 24 | 2.4 |
| Operate ON / OFF / Delay Timers | Level 5 | Technical | 6 | 18 | 24 | 2.4 |
| Operate Speed Controller | Level 5 | Technical | 6 | 18 | 24 | 2.4 |
| Operate Level Detector | Level 5 | Technical | 6 | 18 | 24 | 2.4 |
| Operate Digital Weighing Scale | Level 5 | Technical | 6 | 18 | 24 | 2.4 |
| Operate Temperature Controller | Level 5 | Technical | 6 | 18 | 24 | 2.4 |
| Operate Pressure Controller | Level 5 | Technical | 6 | 18 | 24 | 2.4 |
| Designing of Building Automation System | Level 5 | Technical | 6 | 27 | 33 | 3.3 |
| Perform Security Automation | Level 5 | Technical | 9 | 18 | 27 | 2.7 |
| Perform Energy management and Monitoring | Level 5 | Technical | 10 | 18 | 28 | 2.8 |
| Perform HVAC inspection & Maintenance | Level 5 | Technical | 9 | 27 | 36 | 3.6 |
| Perform Elevator Maintenance | Level 5 | Technical | 8 | 18 | 26 | 2.6 |
| Develop Entrepreneurial Skills | Level 5 | Entrepreneurial | 8 | 9 | 17 | 1.7 |
| Apply management and communications techniques | Level 5 | Entrepreneurial | 8 | 9 | 17 | 1.7 |
| Create Human Resources Management Plan | Level 5 | Entrepreneurial | 9 | 9 | 18 | 1.8 |
| Plan And Implement Business-To-Business Marketing | Level 5 | Entrepreneurial | 9 | 6 | 15 | 1.5 |
| Manage Finances | Level 5 | Entrepreneurial | 9 | 6 | 15 | 1.5 |
| Develop a Project Management Plan | Level 5 | Entrepreneurial | 20 | 21 | 41 | 4.1 |
| Develop a Sales Plan | Level 5 | Entrepreneurial | 9 | 9 | 18 | 1.8 |
| Conduct research for Customer Needs & Satisfaction | Level 5 | Entrepreneurial | 9 | 9 | 18 | 1.8 |
| Identify & resolve Problems | Level 5 | Entrepreneurial | 19 | 21 | 40 | 4 |
| Level 5 Total Hours | Grand Total |  | 400 | 801 | 1201 | 120.1 |

# 2.	Overview of the Curriculum for Automation & Process Control Technology:

| Module Title and Aim | Learning Units | Theory Days/hours | Workplace Days/hours | Timeframe of Modules |
| --- | --- | --- | --- | --- |
| Module A: Maintain Occupational Health and Safety Aim: The aim of this module is to develop knowledge, skills and understanding to establish and maintain the occupational health and safety system. | LU-1: Maintain Health and Safety LU-2: Perform Safety Practices at Workplace LU-3: Develop Professionalism. | 20 | 70 | 90 |
| Module B: Automation Workshop Practice Aim: The aim of this module is to develop knowledge, skills and understanding to carryout Automation Workshop Practice. | LU-1: Connect Tubing and Fittings LU-2: Perform Basic Machining Operations LU-3: Perform Arc Welding. | 15 | 60 | 75 |
| Module C: Basic Electrical Wiring (Single Phase) Aim: The aim of this module is to develop knowledge, skills and understanding to carryout electrical wiring (Single Phase). | LU-1: Maintain Tools & Equipment. LU-2: Make Cable/Wire Joints LU-3: Prepare and Install Distribution Boards LU-4: Carryout Basic Electrical Installation LU-5: Install Simple Electrical Wiring LU-6: Perform Testing of Electrical Wiring LU-7: Repair/ Maintenance of Electrical Installations LU-8: Carryout Electrical planning and Installation | 30 | 120 | 150 |
| Module D: Basic Electrical Engineering Aim: The aim of this module is to develop knowledge, skills and understanding to Measure and understand the various electrical measuring equipment. | LU1: Operate Measuring Instruments. LU2: Verify Ohm’s Law & Kirchhoff’s Law by Implementing Series/Parallel Circuits. LU3: Measure Electrical Power, Energy, Power Factor & Determine Phase Sequence LU4: Implement Electromagnet to See Various Effects & Verify Faradays Laws. LU5: Verify Law of Combination of Capacitor and Determine Break down voltage of Capacitor. | 25 | 95 | 120 |
| Module E: Engineering Drawing Aim: The aim of this module is to develop knowledge, skills and understanding to perform manual drawing & CAD software operations. | LU-1: Perform Basic Manual Drawing LU-2: Construct different Engineering Curves LU-3: Construct multi-view drawings LU-4: Install CAD Software LU-5: Develop 2D CAD drawings LU-6: Develop 3D CAD drawings LU-7: Construct Instrumentation Drawing LU-8: Construct Instrumentation loop diagram or loop sheet | 35 | 130 | 165 |
| Module F: Digital Skills Aim: The aim of this module is to develop knowledge, skills and understanding to operate computer, use digital devices and computer applications. | LU-1: Install Computer Operating Systems and Hardware LU-2: Operate Word-Processing Applications LU-3: Operate Spreadsheet Applications LU-4: Operate Presentation Packages LU-5: Perform Writing And Editing Tasks LU-6: Perform Computer Operations LU-7: Use Computer Applications LU-8: Create User Documentation LU-9: Create Technical Documentation LU-10: Create Basic Databases LU-11: Operate Digital Media Technology LU-12: Use Social Media Tools For Collaboration And Engagement LU-13: E-Commerce LU-14: Use Digital Devices | 60 | 235 | 295 |
| Module G: Basic Electronics (Analog) Aim: The aim of this module is to develop knowledge, skills and understanding to identify electronic components & Thyrister family application. | LU1: Identify Basic Electronics Components LU2: Design a Rectifier using Diode LU3: Carry out Diode Application LU4: Implement Bipolar Junction Transistor (BJT) in Different Applications LU5: Implement Field Effect Transistor (FET) in Different Applications LU6: Implement Thyristor Family in Various Application LU7: Applications of Operation Amplifier | 35 | 125 | 160 |
| Module H: Metrology Aim: The aim of this module is to develop knowledge, skills and understanding to perform measurements through different measuring tools. | LU-1: Take measurements with graduated tools LU-2: Take measurements with combination set LU-3: Perform Levelling LU-4: Take measurements through various gauges LU-5: Perform measurements through Micrometer LU-6: Measure dimensions with Vernier tools LU-7: Measure angles with angle measuring Instruments LU-8: Measure Threads and Gears | 30 | 115 | 145 |
| Module I: Manage IT Skills Aim: The aim of this module is to develop knowledge, skills and understanding to manage IT Skills. | LU-1: Operate Basic Computer Functions LU-2: Perform Basic computer Application LU-3: Develop computer application skills LU-4: Develop advance computer application skills LU-5: Explore computer application skills for careers | 25 | 90 | 115 |
| Module J: Sensors & Actuators Aim: The aim of this module is to develop knowledge, skills and understanding to perform interfacing with Sensors & Actuators. | LU-1: Interface of Sensor LU-2: Interface of Actuator | 15 | 50 | 65 |
| Module K: Process Variable Measurements Aim: The aim of this module is to develop knowledge, skills and understanding to perform process variables measurements. | LU-1: Calibrate Flow instrument LU-2: Calibrate Pressure Instrument LU-3: Calibrate Level Instrument LU-4: Calibrate Temperature Instrument | 30 | 120 | 150 |
| Module L: Digital Electronics Aim: The aim of this module is to develop knowledge, skills and understanding to construct logic circuits, function of flip flops and design operation of amplifier. | LU-1: Verify truth tables of digital gates LU-2: Construct & Verify Combinational logic circuit LU-3: Construct and Verify function of Flip Flops LU-4: Use 555 IC as Multi vibrator | 30 | 120 | 150 |
| Module M: Industrial Electronics Aim: The aim of this module is to develop knowledge, skills and understanding to carryout industrial electronic devices. | LU-1: Implement Thyristor in power control application. LU-2: Implement single phase and Three phase Inverter LU-3: Operate Digital Sensor Switches LU-4: Control speed of DC/AC Motor | 35 | 130 | 165 |
| Module N: Electrical instrumentation and Calibration Aim: The aim of this module is to develop knowledge, skills and understanding to carryout calibration of Electrical process control instrumentation. | LU-1: Perform Test / Calibrate Flow Sensor LU-2: Perform Test/Calibrate Level Sensor LU-3: Perform Test / Calibrate Pressure Sensor LU-4: Perform Test / Calibrate Temperature Sensor | 35 | 120 | 155 |
| Module O: Electrical Machines Aim: The aim of this module is to develop knowledge, skills and understanding to perform test and analyze on DC generators & operate and test of stepper & servo motors. | LU-1: Verify Basic Laws of Electrical Machines LU-2: Analyze Dc Generators LU-3: Perform Tests On Dc Generators LU-4: Analyze Dc Motors LU-5: Perform Tests On Dc Motors LU-6: Repair/ Maintenance and Service of Dc Motors and Dc Generators. LU-7: Operate Single Phase Motors. LU-8: Operate Special Purpose Motors LU-9: Analyze Three Phase Motors | 50 | 200 | 250 |
| Module P: Soft Skills Aim: The aim of this module is to develop knowledge, skills and understanding to manage work planning and development of soft skills. | LU-1: Develop Workplace Policy and Procedures for Sustainability LU-2: Maintain Professionalism in the Workplace LU-3: Manage Personal Work Priorities and Professional Development LU-4: Manage Workforce Planning LU-5: Undertake Project Work LU-6: Prepare and Implement Negotiation LU-7: Manage Meetings LU-8: Organize Schedules LU-9: Identify and Communicate Trends in Career Development LU-10: Apply Specialist Interpersonal and Counseling Interview Skills | 30 | 120 | 150 |
| Module Q: Pneumatics & Hydraulics Aim: The aim of this module is to develop knowledge, skills and understanding to Install / Service of pneumatic & hydraulic units | LU-1: Install / Service Compressed Air Generating Units LU-2: Install Pneumatic Circuit Elements LU-3: Install / Service Hydraulic Power Pack | 20 | 40 | 60 |
| Module R: Programming Aim: The aim of this module is to develop knowledge, skills and understanding to carryout programming. | LU-1: Programming-I LU-2: Programming-II LU-3: Programming-III | 40 | 65 | 105 |
| Module S: PLC Supervisor Aim: The aim of this module is to develop knowledge, skills and understanding to manage PLC system. | LU-1: Install PLC software and Simulator LU-2: Interface PLC with system-I LU-3: Program PLC using Ladder Logic LU-4: Commissioning and Testing of PLC LU-5: Install Relays and Switches in circuits LU-6: Carry out Industrial Automation on PLC LU-7: Interface PLC with system-II | 100 | 180 | 280 |
| Module T: Industrial Instrumentation & Control Aim: The aim of this module is to develop knowledge, skills and understanding to perform to install and setup of various Industrial Instrumentation. | LU-1: Install Transducer & Transmitter in Industrial Application LU-2: Install the process Regulators LU-3: Install the Variable Frequency Drive ( VFD ) LU-4: Install Pneumatic & Hydraulic systems in industry LU-5: Installation and setup procedure for Digital Pressure, Temperature, Level and Flow Controllers | 45 | 75 | 120 |
| Module U: Repair & Maintenance of Automation Equipment Aim: The aim of this module is to develop knowledge; skills and understanding to carryout Repair & Maintenance of Automation Equipment. | LU-1: Identify Fault in Automation/ Process Equipment Installation LU-2: Perform Troubleshooting LU-3: Perform Preventive maintenance | 30 | 50 | 80 |
| Module V: Boiler Instrumentation Aim: The aim of this module is to develop knowledge, skills and understanding to Operate and Install a Boiler Control System. | LU-1: Operate a Boiler Control System LU-2: Install the Boiler Control System | 30 | 50 | 80 |
| Module W: Application of Automation in daily life Aim: The aim of this module is to develop knowledge, skills and understanding Application of Automation in daily life. | LU-1: Operate Product Counter LU-2: Operate ON / OFF / Delay Timers LU-3: Operate Speed Controller LU-4: Operate Level Detector LU-5: Operate Digital Weighing Scale LU-6: Operate Temperature Controller LU-7: Operate Pressure Controller | 40 | 60 | 100 |
| Module X: Building Automation System Supervisor Aim: The aim of this module is to develop knowledge, skills and understanding to carryout Building Automation System. | LU-1: Designing of Building Automation System LU-2: Perform Security Automation LU-3: Perform Energy management and Monitoring LU-4: Perform HVAC inspection & Maintenance LU-5: Perform Elevator Maintenance | 50 | 75 | 125 |
| Module Y: Develop Entrepreneur Skills Aim: The aim of this module is to develop knowledge, skills and understanding to perform entrepreneur ship. | LU-1: Investigate Microbusiness Opportunities LU-2: Develop A Micro Business Proposal LU-3: Develop A marketing Plan LU-4: Develop And Review A Business Plan LU-5: Organize Finances For The Micro Business LU-6: Manage Human Resources LU-7: Market Products And Services LU-8: Monitor And Review Business Performance LU-9: Negotiate For Resolving Business Issues LU-10: Manage Personal Finances LU-11: Coordinate A Work Team LU-12: Lead Small Teams | 100 | 150 | 250 |
| TOTAL |  | 955 | 2645 | 3600 |

# Q- Pneumatics & Hydraulics

## 0714E&A100: Install / service Compressed Air Generating Units

## Objective: This Module covers the knowledge and skills required to install/operate and service compressed air generating units.

Duration:18 Hours				Theory:06 Hours						Practical:12Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1: Install compressed air generating units. | Trainee will be able to: - Demonstrate Safety procedures on compressed air systems - Prepare a strong foundation as required - Execute the installation as per layout plan - Install leak free pipe joints & exhaust ducts - Connect specified safety / Indicative instruments - Operate compressed air unit as per user’s manual - Generate an output report as per SOPs. | - Describe Safety Protocols at workstation. - Describe Air compressor working principle - Describe types of Air compressor - Explain Leveling of Air compressor during installation - Explain safety steps during installation of compressor - Explain air pressure setting - Describe Safety regulation standards on compressed air systems - Describe the execution of installation as per layout plan. - Describe the layout plan of foundation works. - Explain leak free pipe joints and exhaust duct. - Describe connections of specified safety and indicative instrumentation. - Explain commissioning of compressed air unit as per user’s manual. - Explain generation of output report as per SOPs Practical Activity: Demonstrate and Install provided safety / Indicative instruments on air compressor unit. | Total- 09 Hrs Theory- 03Hrs Practical- 06Hrs | - Air compressor - Air receiver tanks - Valves - pressure regulators - safety valves and shut off valves - Oil filters and oil separators - Air filters - Pressure gauges - Temperature gauges - Automatic drain valves - Water separator - Fix Spanner Set - Ring Spanner Set - Plier Set - Screw Driver Set Phillips - Screw Drive Set Flat - Grip Plier - C Clamps - Bench Wise - Special types of tools (specified by the manufacturer, If) - Coolants & Lubricants - Cleaning liquids - Testing instruments - Safety gears - PPE’s | - Class Room - Workshop |
| LU-2: Service the compressed air generating units | Trainee will be able to: - Set optimum and maximum pressure - Check and maintain level of Lubricating Oil - Replace filters | - Describe Safety Protocols at workstation. - Explain optimum and maximum setting of pressure. - Describe checking & maintaining of oil level. - Describe recommended oil for air compressor. - Describe Oil filter. - Describe Oil Separator - Describe Air Filter - Explain compressed air filters and its replacement SOP. - Explain moisture traps. Practical Activity: Demonstrate/Checked and replace the filters of Air Compressor. | Total- 09 Hrs Theory- 03Hrs Practical- 06Hrs | - Air compressor - Oil filters and oil separators - Air filters - Automatic drain valves - Water separator - Fix Spanner Set - Ring Spanner Set - Plier Set - Screw Driver Set Phillips - Screw Drive Set Flat - Grip Plier - C Clamps - Bench Wise - Special types of tools (specified by the manufacturer, If) - Coolants & Lubricants - Cleaning liquids - Safety gears - PPE’s | - Class Room - Workshop |

## 0714E&A101:  Install Pneumatic Circuit Elements.

Objective: This Module covers the knowledge and skills required to identify, select and install pneumatic   components and assemble / dismantle pneumatic circuits diagnose circuit faults.

Duration: 20 Hours				Theory: 05 Hours						Practical: 15 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU-1: Install Working Elements pneumatic | Trainee will be able to: - Select required Pneumatic Working Elements - Check the working element’s functionality - Install Working Elements according to Circuit diagram - Perform post procedural tests - Diagnose and fix the fault if applicable | - Describe Safety Protocols at Workstation. - Describe Pneumatic working Elements - Describe the Symbols& Functions of pneumatic working elements. - Describe working element installation as per circuit diagram. - Describe the Interpretation of circuit diagrams - Describe post procedural test. - Describe the procedure to Diagnose and fix the fault of pneumatic working elements. Practical Activity: Demonstrate and Install the provided pneumatic working elements and make test report. | Total- 08 Hrs Theory- 02 Hrs Practical- 06Hrs | - Pneumatic Cylinders - Pneumatic Rotary Actuators - Pneumatic Semi Rotary Actuators - Spanner set - Teflon tape - Pneumatic pipes and fittings - Fix Spanner Set - PU tubes - PU Tube cutter - PU tube fittings - Leak tester - PPE’s | - Class Room - Workshop |
| LU-2: Install directional Control Valve | Trainee will be able to: - Select required directional control valve - Check the directional control valve’s functionality - Install directional control valve according to Circuit diagram - Perform post procedural tests - Diagnose and fix the fault if applicable | - Describe Safety Protocols at Workstation. - Describe the Symbols of Directional Control Valve - Describe Nomenclature of Directional Control - Describe the types of directional control valves. - Describe the function of directional control valves. - Explain pneumatic circuit diagram - Identify direction control valve - Explain post procedural test Practical Activity: Demonstrate and install the directional control valves according to the circuit diagram. | Total- 07 Hrs Theory- 01 Hrs Practical- 06 Hrs | - Pneumatic Directional ControlValves 2/2,3/2,4/2,4/3,5/2 & 5/3. - Fix Spanner set - Ring Spanner set - Teflon tape - Pneumatic pipes. - Fix Spanner Set - PU Tube cutter - PU tube fittings - Leak Tester - PPE’s | - Class Room - Workshop |
| LU-3: Install Special Purpose valves | Trainee will be able to: - Select required special purpose valves - Check the special purpose valve’s functionality - Install special purpose valves according to Circuit diagram - Perform post procedural tests - Diagnose and fix the fault if applicable | - Describe Safety Protocols at Workstation. - Explain Special purpose valves - Describe Nomenclature of Special purpose valve. - Describe symbols of Special Purpose Valve (SPV) - Describe Function / working of SPV - Identify Special purpose valve - Explain Pneumatic circuit diagram - Explain installation procedure of SPV in pneumatic circuit. - Perform post procedural test - Describe Diagnostic procedure of SPV and fixing the fault. Practical Activity: Demonstrate and install the SPV according to the supplied circuit diagram. | Total- 05Hrs Theory- 02Hrs Practical- 03 Hrs | - Pneumatic Special purpose valves. - Fix Spanner set - Ring Spanner set - Plier set - Screw driver set - L-key Set - Teflon tape - PU tubes - PU Tube cutter - PU tube fittings - Leak tester - PPE’s | - Class Room - Workshop |

## 0714E&A102:  Install / Service Hydraulic Power Pack

Objective: This Module covers the knowledge and skills required to install/operate and service Hydraulic Power Pack

Duration: 20 Hours						Theory: 05 Hours						Practical: 15 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU-1: Install Hydraulic Power Pack. | Trainee will be able to: - Demonstrate the Safety procedures on hydraulic systems - Prepare a strong foundation as required - Execute the installation as per layout plan - Install leak free pipe / hose joints - Connect specified safety / Indicative instruments - Operate hydraulic power pack as per user’s manual - Generate an output report as per SOPs. | - Describe safety Protocols at workstation. - Define Color coding standards - Describe Safety regulation standards fluid power systems - Describe the hydraulic fluids and their applications - Explain foundation layout and types required for hydraulic system installation. - Explain Leveling of hydraulic power pack during installation - Describe safety steps during installation of hydraulic power pack - Explain circuit diagram of hydraulic power pack - Describe operating procedure for hydraulic power pack as per user’s manual. - Explain commissioning report for hydraulic power pack. Practical Activity: Demonstrate &Operate hydraulic power pack unit as per instructions of operating manual. | Total- 04Hrs Theory- 01Hrs Practical- 03Hrs | - Hydraulic pump - Reservoir - Pressure Relief Valve - pressure regulators - safety valves and shut off valves - Heat exchangers - Electric drill - Oil filters - Pressure gauges - Temperature gauges - Fix Spanner Set - Ring Spanner Set - Plier Set - Screw Driver Set Phillips - Screw Drive Set Flat - Grip Plier - C Clamps - Bench Wise - Special types of tools (specified by the manufacturer, If) - Coolants & Lubricants - Cleaning liquids - Testing instruments - Safety gears - Stationary - PPE’s - Projector - Desktop Computer - Computer table - White Board - Board Marker | - Class Room - Workshop |
| LU-2: Service the hydraulic power pack | Trainee will be able to: - Set optimum and maximum pressure - Check and maintain level oil level. - Replace faulty components / seals - Replace filters | - Describe safety Protocols at workstation. - Define Lube Color coding system. - Describe Safety regulation standards fluid power systems - Describe the hydraulic fluids and their applications - Describe the types and applications of filters - Describe types & application of Seals - Describe Hydraulic Components - Explain Hydraulic Pump types - Describe types of hydraulic filters - Explain hydraulic oil grades. - Explain circuit diagram of hydraulic power pack - Explain hydraulic pressure operating and maximum. - Describe oil level checking and replenishing. - Explain trouble shooting of faulty components and its replacement procedure. Practical Activity: Demonstrate and install the filters of hydraulic power pack. | Total- 04Hrs Theory- 01Hrs Practical- 03Hrs | - Hydraulic pump - Reservoir - Pressure Relief Valve - pressure regulators - safety valves and shut off valves - Heat exchangers - Electric drill - Oil filters - Pressure gauges - Temperature gauges - Fix Spanner Set - Ring Spanner Set - Plier Set - Screw Driver Set Phillips - Screw Drive Set Flat - Grip Plier - C Clamps - Bench Wise - Special types of tools (specified by the manufacturer, If) - Coolants & Lubricants - Cleaning liquids - Testing instruments - Safety gears - Stationary - PPE’s - Projector - Desktop Computer - Computer table - White Board - Board Marker | - Class Room - Workshop |
| LU-3: Install Working Elements hydraulic | Trainee will be able to: - Select required Working Elements - Check the working element’s functionality - Install Working Elements according to Circuit diagram - Perform post procedural tests - Diagnose and fix the fault if | - Describe safety Protocols at workstation. - Describe Hydraulic working elements and their functionality. - Explain installation of working elements in hydraulic system. - Describe function of hydraulic working element. - Explain post procedural test - Explain trouble shooting and rectification of faults in working elements Practical Activity: Demonstrate and install the provided working element and prepare report. | Total- 04 Hrs Theory- 01 Hrs Practical- 03 Hrs | - Hydraulic Power pack - Hydraulic cylinder. - Hydraulic motor - Hydraulic directional control valve - Fix Spanner Set - Ring Spanner Set - Plier Set - Screw Driver Set Phillips - Screw Drive Set Flat - Grip Plier - C Clamps - Bench Wise - Special types of tools (specified by the manufacturer, If) - Coolants & Lubricants - Cleaning liquids - Testing instruments - Stationary - PPE’s - Projector - Desktop Computer - Computer table - White Board - Board Marker | - Class Room - Workshop |
| LU-4: Install directional Control Valve | Trainee will be able to: - Select required directional control valve - Check the directional control valve’s functionality - Install directional control valve according to Circuit diagram - Perform post procedural tests - Diagnose and fix the fault if applicable | - Describe safety Protocols at workstation. - Describe Hydraulic Components - Define the Interpretation of circuit diagrams - Describe the Symbols of Directional Control Valve - Describe Nomenclature of Directional Control - Define direction control valve - Describe the function of direction control valve. - Describe the identification and placements of direction control valve in hydraulic circuit diagram. - Describe the installation procedure of direction control valve. - Explain post procedural test - Describe troubleshooting and rectification of faults procedure in direction control valves. Practical Activity: Demonstrate and install the directional control valves according to the circuit diagram. | Total- 04Hrs Theory- 01Hrs Practical- 03Hrs | - Hydraulic Power Pack unit - Hydraulic cylinder - Hydraulic Directional control valves 2/2,3/2,4/2 & 4/3 - Pressure gauges - Cleaning liquids - Testing instruments - Safety gears - Stationary - PPE’s - Projector - Desktop Computer - Computer table - White Board - Board Marker | - Class Room - Workshop |
| LU-5: Install Special Purpose valves | Trainee will be able to: - Select required special purpose valves - Check the special purpose valve’s functionality - Install special purpose valves according to Circuit diagram - Perform post procedural tests - Diagnose and fix the fault if applicable | - Describe safety Protocols at workstation. - Define the Interpretation of circuit diagrams - Define the symbols of SPV - Describe Function / working of SPV - Identification of Special purpose valve - Describe installation of special purpose valve as per hydraulic circuit diagram. - Explain post procedural test - Describe troubleshooting and rectification of faults procedure of Special purpose valves. Practical Activity: Demonstrate and install the SPV according to the Hydraulic circuit diagram. | Total- 04Hrs Theory- 01Hrs Practical- 03Hrs | - Hydraulic power pack unit - Hydraulic Cylinder - Directional control valve - Hydraulic special purpose valves relief valve, pressure regulators, distribution valves, servo valves, proportional valve. - Pressure gauges - Coolants & Lubricants - Cleaning liquids - Testing instruments - Safety gears - Stationary - PPE’s - Projector - Desktop Computer - Computer table - White Board - Board Marker | - Class Room - Workshop |

# R-Programming

## 0714E&A103:  Programming- I

Objective: This module covers the skills and knowledge required to protect from all security threats by ensuring personal safety, work place safety Machines/tools and equipment safety, interpret environmental regulation preparation and safety of all tools and equipment.

Duration:  33 Hours							Theory: 12Hours						Practical: 21 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Develop a computer program (simple) | - Analyze a given problem - Open the IDE for coding - Code a simple program - Compile a code - Debug the code (in case of error) - Run a code | - Describe the basic programming concept - Define basics of C language Practical Activity. Make a simple program to perform basic arithmetic operations. | Theory- 3Hrs Practical-06Hrs Total-09Hrs | - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker | Classroom / Workshop /Computer lab |
| - Develop a program based on control structures | - Identify the keywords and identifiers - Perform comments, indentation and statements - Recognize variables and data types in Python - Check standard Input and Output - Use Operators - Use of IF statement - Use of IF ELSE statement - Use of SWITCH statement | - Define IF Else statement. - Demonstrate the SWITCH statement. Practical Activity. Perform to make a simple program by using IF ELSE statement to print a number from 0 to 100 | Theory- 3Hrs Practical-06Hrs Total-09Hrs | - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker | Classroom / Workshop /Computer lab |
| - Develop program using loop structuresctures | - Use of FOR loop - Use of WHILE loop - Use of DO-WHILE loop - Use of nested loop - Use Break and Continue | - Define FOR Lop. - Demonstrate WHILE Loop. - Explain DO-WHILE Loop. - Demonstrate Nested Loop. Practical Activity. Perform to make a simple program by using DO-WHILE statement to calculate the factorial of any number enters by user. | Theory- 3Hrs Practical-06Hrs Total-09Hrs | - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker papers | Classroom / Workshop /Computer lab |
| - Develop a program using Arrays | - Use of Arrays - Use of one-dimension array declaration. - Use of Array declaration. - Use of Array initialization. - Use of Array elements accessing. - Use of Two-dimension array declaration. | - Define Array. - Demonstrate two-dimension arrays. Practical Activity. Perform to make a simple program by using Nested loop to define two dimensional arrays. | Theory- 3Hrs Practical-03Hrs Total-06Hrs | - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker | Classroom / Workshop /Computer lab |

## 0714E&A104: Programming- II

Objective: This module covers the skills and knowledge on Java Virtual Machine (JVM), Classes, Object, Inheritance, Polymorphism and Encapsulation .It also deals with the functionalities of interface generics and exceptional handling techniques.

Duration:  33 Hours							Theory: 12Hours						Practical: 21 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Install Net Beans | - Locate the Java Language Software Package. - Install Java Development Kit - Start the setup of the Net Beans and follow the installation instruction - Set the Environment Variable and Class path | - Define object oriented programming (OOP). - Explain the characteristics of OOP - Differentiate between object and class Practical Activity. Perform to make a simple program to print the sentence in your screen. | Theory- 2Hrs Practical-0Hrs Total-02Hrs | - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker | Classroom / Workshop /Computer lab |
| - Developing object oriented programs (OOP) | - Open the IDE for coding - Code a simple program - Compile a code - Debug the code (in case of error) - Run a code | - Define IDE. - Explain the characteristics of OOP. Practical Activity. Perform to make a simple OOP based program to print a prime numbers from 0-50. | Theory- 02Hrs Practical-03Hrs Total-05Hrs | - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker | Classroom / Workshop /Computer lab |
| - Develop OOP based program by using control structures | - Use of IF statement - Use of IF ELSE statement - Use of SWITCH statement | - Define IF statement. - Demonstrate IF ELSE statement. Practical Activity. Perform to make a simple OOP based program to sort an entered number by user in ascending / descending order. | Theory- 02Hrs Practical-03Hrs Total-05Hrs | - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker | Classroom / Workshop /Computer lab |
| - Develop program using loop structuers | - Use of FOR loop - Use of WHILE loop - Use of DO-WHILE loop | - Define FOR Loop. - Explain DO-WHILE loop. Practical Activity. Perform to make a simple OOP based program to print an ASCII code of any number as entered by user. | Theory- 02Hrs Practical-03Hrs Total-05Hrs | - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker | Classroom / Workshop /Computer lab |
| CU5. Develop Class in OOPs | - Use of Class in a program - Create Objects in classes in heap area - Use of Constructors and Destructor | - Define object oriented programming (OOP). - Explain IDE. - Demonstrate the characteristics of OOP. Practical Activity. Perform to make a simple OOP based program to perform arithmetic calculations. | Theory- 02Hrs Practical-03Hrs Total-05Hrs | - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker | Classroom / Workshop /Computer lab |
| CU6. Develop Interface | - Create the interface unit - Declare the reference variable of the object class - Make the methods for child object using encapsulation | - Define object oriented programming (OOP). - Demonstrate encapsulation. Practical Activity. Perform to make a simple program of encapsulation. | Theory- 02Hrs Practical-03Hrs Total-05Hrs | - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker | Classroom / Workshop /Computer lab |
| CU7. Develop a program using pointers | - Declare the pointer variable - Assign the value to the pointer variable - Access value of pointer variable by address operator | - Demonstrate Pointer - Explain address operator. - Explain polymorphism. Practical Activity. Perform to make a simple program of polymorphism. | Theory- 01Hrs Practical-03Hrs Total-04Hrs | - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker | Classroom / Workshop /Computer lab |
| CU8. Develop a computer program using structures | - Declare the structure - Declare the elements of the structures - Assign value to structure variables | - Demonstrate structure. - Explain variables. Practical Activity. Perform to make a simple program of pointer and structure. | Theory- 01Hrs Practical-03Hrs Total-04Hrs | - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker | Classroom / Workshop /Computer lab |

## 0714E&A105: Programming- III

Objective: This module covers the skills and knowledge required to develop how to write a computer program. It will create the knowledge to write lists of instructions for a computer to follow and to develop the software programs, the scripts, or other sets of instructions for the computers to execute. This unit will cover the knowledge of programming language C which has variety of data types and powerful operators. Due to this, students will be able to write computer programs efficiently and easily.

Duration:  40 Hours					Theory: 10Hours						Practical: 30 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Python Setup on Windows | - Download the Python 3 Installer - Run the installer - Download the python IDE - Identify Interpreter vs Script Mode | - Define Python - Demonstrate Python commands. Practical Activity. Perform to make a simple program of python to print name. | Theory- 1Hrs Practical-03Hrs Total-04Hrs | - IDE - Raspberry Pi Kit - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker - Tool kit - Wires 0.5 mm - Wire Plier - Wire stipper - Breadboard | Classroom / Workshop /Computer lab |
| - Remote Connection to RPi with VNC | - Enabling VNC Server - Enabling VNC Server graphically - Enabling VNC Server at the command line - Connecting to your Raspberry Pi with VNC Viewer - Establishing a direct connection - Establishing a cloud connection - Authenticating to VNC Server - Creating a virtual desktop | - Define Python - Define Python commands. - Define VNC Server. Practical Activity. Connect your Raspberry Pi with VNC Viewer and operate this on your desktop computer. | Theory- 1Hrs Practical-03Hrs Total-04Hrs | - IDE - Raspberry Pi Kit - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker - Tool kit - Wires 0.5 mm - Wire Plier - Wire stipper - Breadboard | Classroom / Workshop /Computer lab |
| - Raspberry Pi Raspbian OS Setup | - Download and Install aspbian and image writer - Setup the SD card formatter on windows - Write the image - Write the OS on the SD card - Setting up the pi - Run the Setup - Reboot the Raspberry pi - Update the firmware - Identify the Rpi Models and GPIO - Python package installation using pip | - Define the installation procedure of aspbian boot. - Explain python software. Practical Activity. Completely install the python software on Raspberry Pi and SD card. | Theory- 1Hrs Practical-03Hrs Total-04Hrs | - IDE - Raspberry Pi Kit - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker - Tool kit - Wires 0.5 mm - Wire Plier - Wire stipper - Breadboard | Classroom / Workshop /Computer lab |
| - Introduction to LINUX commands | - Opening Linux Terminal - Perform Basics of Linux Terminal - Use Commands to display directory - Create file on the directory - Use Commands to run the file on LINUX. | - Explain Linux - Define the applications of Python. Practical Activity. Perform to make a simple program of python to print Even numbers only from 0-100 | Theory- 1Hrs Practical-03Hrs Total-04Hrs | - IDE - Raspberry Pi Kit - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker - Tool kit - Wires 0.5 mm - Wire Plier - Wire stipper - Breadboard | Classroom / Workshop /Computer lab |
| - Develop a program based on control structures | - Identify Basic Data Types - Use Assignment Operators - Use print() function - Use Comments in Python - Use input() functions - Identify Code Blocks and Indentation - Identify Reserved words in Python - Use Assignment Operators and Expressions - Use Arithmetic Operations - Identify Precedence and Associativity - Identify Docstring | - Demonstrate all the functions of python. Practical Activity. Perform to make a simple program of python to print ODD numbers only between 0-100. | Theory- 1Hrs Practical-03Hrs Total-04Hrs | - IDE - Raspberry Pi Kit - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker - Tool kit - Wires 0.5 mm - Wire Plier - Wire stipper - Breadboard | Classroom / Workshop /Computer lab |
| - Develop program Using Conditional Structuers and Operators | - Use Boolean Expressions - Use If Statement - Use If-Else - Use Nested-If - Use If-Elif-Else - Identify Membership Operators - Identify Logical Operators - Use Bitwise Operators - Identify Simple Recursion - Use Factorial with Recursion - Program to display Fibonacci sequence using recursion - Use Indirect Recursion | - Define Boolean expression in Python - Demonstrate loops in python. Practical Activity. Perform to make a simple program of python to display Fibonacci sequence using recursion. | Theory- 1Hrs Practical-03Hrs Total-04Hrs | - IDE - Raspberry Pi Kit - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker - Tool kit - Wires 0.5 mm - Wire Plier - Wire stipper - Breadboard | Classroom / Workshop /Computer lab |
| - Develop program using loop | - Use While Loop - Use While-break - Use While-Continue - Use for-list - Use for-range - Use for-continue-break - Program to display prime numbers in an interval - Calculate factorial - Compute Fibonacci Series | - Define all type of loops in python. - Demonstrate continue – break statements. Practical Activity. Perform to make a simple program of python to print a numbers in descending order from 0-100. | Theory- 1Hrs Practical-03Hrs Total-04Hrs | - IDE - Raspberry Pi Kit - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker - Tool kit - Wires 0.5 mm - Wire Plier - Wire stipper - Breadboard | Classroom / Workshop /Computer lab |
| - Develop a program using Functions | - Use of simple FUNCTIONS. - Use of Function Declaration. - Use of Function Prototype. - Use of Function Arguments - Use of Function definition. - Use of Function Call. - Use of passing parameters to Function. - Use of Function Arbitrary Arguments | - Define Function declarations. - Define simple FUNCTIONS. - Explain Function Prototype. Practical Activity. Perform to make a simple program of python to calculate factorial of a given numbers. | Theory- 1Hrs Practical-03Hrs Total-04Hrs | - IDE - Raspberry Pi Kit - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker - Tool kit - Wires 0.5 mm - Wire Plier - Wire stipper - Breadboard | Classroom / Workshop /Computer lab |
| - Python file handling | - Create a Text File - Append Data to a File - Read a File - Read a File line by line - Identify File Modes in Python - Handling of CSV file - Handling of Excel File | - Explain CSV files. - Demonstrate Append data. Practical Activity. Perform to make a simple program of python to open file from your desktop. | Theory- 1Hrs Practical-03Hrs Total-04Hrs | - IDE - Raspberry Pi Kit - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker - Tool kit - Wires 0.5 mm - Wire Plier - Wire stipper - Breadboard | Classroom / Workshop /Computer lab |
| - Develop a program using Python Data Structrre | - Declare Strings - Create Lists in python - Apply Lists methods - Constructing Tuples in python - Apply Tuples methods - Create Sets - Use Operators on Sets - Create Dictionary - Methods to query information from dictionaries - Create Strings - Formatters and Operator on String - Methods on String | - Explain Strings - Define Lists in python - Demonstrate Tuples in python Practical Activity. - Perform to make a simple program in python by using LIST. | Theory- 1Hrs Practical-03Hrs Total-04Hrs | - IDE - Raspberry Pi Kit - Desktop - JAVA Language Package - Net beans / Eclipse IDE - Desktop computer - IDE Software - Instruction manual - Computer Table and chairs - Stationaries - Notebook - Printer - A4 papers - Projector - White board - Board marker - Tool kit - Wires 0.5 mm - Wire Plier - Wire stipper - Breadboard | Classroom / Workshop /Computer lab |

# S-PLC Supervisor

## 0714E&A106:  Install PLC software and Simulator

Objective: The module covers the knowledge and skill required to Install PLC software and Simulator, Program a PLC using simulator, Analyze user requirements and specifications, Identify error codes and functionality testing, Identify HMI Software and programming, Identification and configuration of SCADA Systems.

Duration: 30 Hours						Theory: 12 Hours						Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Install PLC software and Simulator | Trainee will be able to: - Install the PLC Programming - Software as per PLC manufacturer such as RS Logic 5000 and RS links classic etc. - Select the best and most frequently used Simulator for programming - Select the module - Input the generic value as per universal settings (check from internet/helped) - Start The Simulator. - Open PLC programming software. - Install the HMI software as per manufacturer such as WinCCflexible and EasyBuilder etc. | - Define simulator. - Differentiate between simulator and emulator. - Define HMI working. - Define communication Protocol Practical Activity Install PLC programming software along with HMI editor | Theory- 02Hrs Practical- 03Hrs Total- 05Hrs | - PLC CPU - PLC Software and hardware - Helping Manual - User guide - Simulator - HMI software and hardware - Communication modules - PC - PLC programming cable. | Classroom / Workshop /Computer lab |
| LU2. Program a PLC using simulator | Trainee will be able to: - Open the programming software as per PLC manufacturer - Ensure that the Simulator is connected and is in ON condition - Create a basic ladder logic program for ON/OFF of a bulb using Examine ON and Examine OFF switch - Create a basic ladder logic program for Simple Start/Stop Ladder Logic Relay - Create a basic ladder logic program for Single Push Button On/Off Ladder Logic - Create a basic ladder logic program for with On Delay Timer - Create a basic ladder logic program for with Off Delay Timer - Create a basic ladder logic program for Up Counter - Create a basic ladder logic program for Down Counter - Create a basic ladder logic program for Motor Control - Create a basic ladder logic program for Traffic signal lights - Create a basic ladder logic program for Elevator Control. | - Define NO and NC in Ladder logic. - Define relay operation in PLC. - Differentiate between momentary switch and toggle switch. - Define different types of timer and its operation. - Define different types of counter operation. Practical Activity Develop PLC logic for Motor Direction and jog control circuit. | Theory- 02Hrs Practical- 03Hrs Total- 05Hrs | - PLC CPU - PLC Software and hardware - Helping Manual - User guide - Simulator - HMI software and hardware - Communication modules - PC - PLC programming cable. | Classroom / Workshop /Computer lab |
| LU3. Analyze user requirements and specifications | Trainee will be able to: - Draw the general value chain of the end user industry - Highlight the set of activities that a firm operating in a specific industry performs in the value chain drawing - Enlist the equipment / gauges / sensors / actuators / transducers used in different stages of the process - Identify critical stages in the process - Identify the safety aspect required in the critical stages of the process - Analyze the possible automation in the existing processes and global trends in automation - Analyze the client requirement at broad level from the proposal - Generate a report of various industrial processes involved in industry. - Collect the required specification of the equipment (if already prepared by the user) and clarify the technical specification | - Define the method of analyzing the customer requirements. Practical Activity Develop and report for analyzing the user requirements for acquiring PLC based automation system. | Theory- 02Hrs Practical- 03Hrs Total- 05Hrs |  | Classroom / Workshop /Computer lab |
| LU4. Identify error codes and functionality testing | Trainee will be able to: - Use error codes to identify programming errors - Determine program scan time in milliseconds - Use a force function to verify an input - Use a force function to verify an output - Perform measurement of status/values at IOs and variables used for logical operation using programming software | - Define various types of error codes used in programming. - Define force function and its effectiveness. Practical Activity Test the hardware for the unusual operation using force function to test the system robustness. | Theory- 02Hrs Practical- 03Hrs Total- 05Hrs | - PLC CPU - PLC Software and hardware - Helping Manual - User guide - Simulator - HMI software and hardware - Communication modules - PC - PLC programming cable. | Classroom / Workshop /Computer lab |
| LU5. Identify HMI Software and programming. | Trainee will be able to: - Open software. - Make a program of graphical representation of tasks on CU2 (P3 – P12). - Program of HMI software to communicate with PLC. - Download the software on HMI and Run. - Create the connection between two units of PLCs. - Identify the communications between two units. - Convey the data of both units on HMI. | - Define the difference between upload and download of PLC program on HMI. - How to select the appropriate PLC from the software? - Define PLC networking. - Define HMI OFF line simulation. - Define HMI ON line simulation. Practical Activity - Design an HMI interface of Motor control. - Integrate the HMI with PLC for ON Line HMI operation of Motor. | Theory- 02Hrs Practical- 03Hrs Total- 05Hrs |  | Classroom / Workshop /Computer lab |
| LU6. Identification and configuration of SCADA Systems | Trainee will be able to: - Create the connection between two units of PLCs. - Define the programming. - Identify the communications between two units. - Convey the data of both units on HMI. | - Define the types of PLC Network connections. - Define Network Protocols. - Define key features of SCADA System. - Define the process of PLC and HMI configuration on SCADA. | Theory- 02Hrs Practical- 03Hrs Total- 05Hrs | - PLC CPU. - HMI software and hardware - SCADA software - Communication modules - Communication Cable. | Classroom / Workshop /Computer lab |

## 0714E&A107: Interface PLC with system - I

Objective: The module covers the knowledge and skill required to: Differentiate Modules of control systems, Install / Modify PLC and its components, Install field instruments

Duration: 30 Hours						Theory: 12 Hours						Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Differentiate Modules of control systems | Trainee will be able to: - Identify the standalone/ module - Demonstrate its functions & capabilities - Extract information from device part number | - Define the basic control system components. - Define the specifications of modules. - Name different types of modules used with the system. - Explain the various module operations w.r.t. applications. - Demonstrate the datasheet reading methods Practical Activity Select and demonstrate the module as per the required parameters and specification mentioned in the user guide. | Theory- 4 Hrs Practical-06 Hrs Total-10 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - PLC editing software. - Personal Computer. - Power source. - Test bench - Connection cords. - Hand tools. - Din rail. - Screwdriver set. - Cutter. - Player | Classroom / Workshop /Computer lab |
| LU2. Install / Modify PLC and its components | Trainee will be able to: - Implement hardware configuration as per given design - Disassemble the hardware in accordance user’s manual | - Define PLC hardware and its associated module. - Define the dissembling process of the PLC modules and associated hardware. Practical Activity Demonstrate the process of assembling and dissembling of modules. | Theory- 4 Hrs Practical-06 Hrs Total-10 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - PLC editing software. - Personal Computer. - Power source. - Test bench - Connection cords. - Hand tools. - Din rail. - Screwdriver set. - Cutter. - Player | Classroom / Workshop /Computer lab |
| LU3. Install field instruments | Trainee will be able to: - Identify field instruments - Install the wiring from Module to instrument location - Install the instrument - Perform field testing and calibration (if required) - Generate the field-testing reports | - Explain the process of field instrument installation. - Explain the Instrument parameter under consideration operation. Practical Activity Install the provided instrument as per the SO.P. | Theory- 4 Hrs Practical-06 Hrs Total-10 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - PLC editing software. - Personal Computer. - Power source. - Test bench - Connection cords. - Hand tools. - Screw driver set. - Cutter. - Player | Classroom / Workshop /Computer lab |

## 0714E&A108: Program PLC using Ladder Logic

Objective: The module covers the knowledge and skill required to: Installation of PLC programming software, Design Basic logic program on Ladder logic, Apply timers on Ladder logic program, Apply counters on Ladder logic program

Duration: 36 Hours						Theory: 12 Hours						Practical: 24 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Installation of PLC programming software . | Trainee will be able to: - Identify PLC languages a) Instructions List (IL) a1) Structured Text (ST) b) Graphical language b1) Ladder Diagrams (LD) b2) Function Block Diagram (FBD) b3) Sequential Function Chart (SFC) - Download and open setup file for software installation on windows PC. - Configure installation setup. - Install all parts of software. - Complete installation and restart the PC. | - Explain the various programming languages of PLC. - Explain various PLC software’s from different brands. - Explain the procedure of software installation with port setup. - Configure the data rate for PLC to PC communication. Practical Activity - Perform the installation procedure for PLC programming software on personal computers. - Establish communication between PLC and Program editor. | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - PLC Communication cable. - PLC editing software. - Push buttons. - Light Indicators. - Personal Computer. - Power source. - Test bench. - Table chair. - Stationary. | Classroom / Workshop /Computer lab |
| LU2. Design Basic logic program on Ladder logic | Trainee will be able to: - Open software GUI. - Design basic logical ON/OFF operation in Ladder logic programming. - Run simulator software to verify program. - Upload that program on PLC hardware | - Define PLC Programming interface with its various tabs. - Explain the process of using Simulator for testing the logic. - Define the PLC addressing for handling the PLC I/O modules. - Demonstrate the PLC uploading and downloading process. Practical Activity - Develop a PLC ON/OFF logic for digital Ii/O (using any language) on PLC editing software. - Simulate the program on PLC editor for error testing and debugging. . | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - PLC communication cable. - PLC editing software. - Personal Computer - Power supply. - Test bench - Table. - Chair - Stationary. | Classroom / Workshop /Computer lab |
| LU3. Apply timers on Ladder logic program . | Trainee will be able to: - Open software GUI. - Design program and insert timers. - Configure timer block according to requirement. - Run simulator software to verify this program. - Upload this program and run on PLC. | - Define timers and their function. - Explain different types of timer application. - Explain ON Delay and OFF Delay timers functions. - Explain time retention function in PLC. - Explain various modes and timer resolution. Practical Activity Develop timer logic to operate motor Stat Delta control system using timer. | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - PLC Communication cable. - PLC editing software. - Personal Computer - Power supply. - Test bench - Table. - Chair. - Stationary. | Classroom / Workshop /Computer lab |
| LU4. Apply counters on Ladder logic program | Trainee will be able to: - Open software GUI. - Design program and insert counters. - Configure counter block according to requirement. - Run simulator software to verify this program. - Upload this program and run on PLC | - Define counters and their function. - Explain UP/ Down counter function. - Explain different types of counter application. Practical Activity Develop logic to operate a car parking management system having capacity of 100 cars using counter function. | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - PLC Communication cable. - PLC editing software. - Personal Computer - Power supply. - Test bench - Table chair. - Stationary. | Classroom / Workshop /Computer lab |

## 0714E&A109: Commissioning and Testing of PLC

Objective: The module covers the knowledge and skill required to: Prepare work plan, Design and program PLC, Installation and Commissioning, Test the PLC.

Duration: 36 Hours						Theory: 12 Hours						Practical: 24 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare work plan | Trainee will be able to: - Suggest globally practiced and accepted automation systems if the user is not aware of the technical specifications - List down the sub systems that are involved in the process - List down sensors and actuators requirement. - Collect information on process logic - Collect information for operator station screens - Decide on whether the system can be developed as per the user requirement - Support the project manager in calculating the time required for each stage to ensure completion of project - Assist in preparing the work plan with deliverables and timelines - Explain the expected output to the user - Calculate the number of days needed for commissioning of the panel at site - Summarize the user requirement | - Define the sub systems that are involved in the process. - Define sensors and actuators requirement. - Define the process and its flow. - Define customer requirement and customization in work plan. - Define system Imperilment and planning implications. - Explain time estimation in project planning. - Explain how to ensure customer satisfaction. - Explain the methods to meet deadlines. - Explain the time line estimation for process control. Practical Activity - Design the work plan sheet for project implementation. - Develop a generic work sheet for implementing the work plan as plan | Theory- 3 Hrs Practical-6Hrs Total- 09 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - PLC Communication cable. - PLC editing software. - Relays. - Push buttons. - Light Indicators. - Personal Computer. - Pen - Pencil - Eraser - Marker - Power source. - Test bench | Classroom / Workshop /Computer lab |
| LU2. Design and program PLC. | Trainee will be able to: - Develop PLC application as per user requirement by following the standard operating procedure (SOP) of the organization - Apply approved engineering concepts, processes and principles in developing the PLC application - Install organization approved software (system and application software) to develop the system - Identify the requirement of indications, switchgears and accessories - Develop the control circuit drawing - Prepare wiring plans - Integrate the main process system with the sub-systems as per the user requirement (e.g., using communication protocol) - Ensure that safety aspect of the process is captured in the design plan - Program PLC as per FDF - Program SCADA Application - PLC-SCADA Communication - Create backup copies of all designs developed for control panel and store in a secure location - Prepare a product manual and store them for future references. | - Define Programming. - Define program standardization - Explain PLC programming for customized control system. - Explain key features of standard programming in any PLC language. - Describe essential of system design. - Describe hardware design for any control system for PLC. Practical Activity - Develop a folio for hardware required for PLC based control system. - Design a PLC program to automate the system as per requirement. | Theory- 3 Hrs Practical-6Hrs Total- 09 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - PLC Communication cable. - PLC editing software. - Associated hardware (limit switch, actuators) hardware. - Push buttons. - Light Indicators. - Personal Computer - Power supply. - Hand tools. - Screwdrivers. - Tape. - Player. - Test bench | Classroom / Workshop /Computer lab |
| LU3 Installation and Commissioning | Trainee will be able to: - Check availability of panel and tools required for installation - Check the internal panel wiring and ensure that it is in accordance with the design drawing - Carry out insulation check of internal panel wiring and devices within the panel - Check if batteries and chargers have been assembled in accordance with the manufacturers recommended procedures - Identify the conductors size and capacity for installation - Ensure that the panel is positioned as prescribed, following safety norms - Make connections to socket outlets, switches and protective conductors - Perform settings as per customer requirements on the equipment in each of the panels - Test all control system interlocks - Check each digital control point by comparing the command at the control panel and status of the device that it controls - Ensure that fuses, switches and other protective devices are labeled correctly - Follow the grounding and earthling procedures while commissioning - Put danger and warning notices, (if necessary) - Test continuity, insulation resistance, functions of all devices, etc., after completion of installation | - Define personal safety standards during work. - Define the term Installation. - Define the term commissioning. - Differentiate between installation and commissioning. - Explain the working of necessary tools needed for the job. - Explain electrical drawing reading and editing process for the assigned task. - Describe the necessity of Pannel insulation. - Explain the importance of insulation safety. - Explain safety standards adopted during installation and commissioning process. - Describe the backup power and its essentials. - Describe the checking procedures to ensure smooth operation. - Define wiring standards and its selection criteria. - Define panel standards and essentials. - Explain the importance of interlocking in an electrical system. - Describe cable tagging/ labeling and its importance in fault detection. - Explain the participation of earthling in plant protection. - Explain the pre and post installation test for leakage current. - Explain the importance of hazard sign during plant erection Practical Activity Install and commission the given electrical and PLC panels as per instruction. Keeping the safety standard in line with the process till smooth operating conditions achieved. | Theory- 3 Hrs Practical-6Hrs Total- 09 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - PLC Communication cable. - PLC editing software. - Associated hardware (limit switch, actuators ) hardware. - Push buttons. - Light Indicators. - Personal Computer - Power supply. - Hand tools. - Screwdrivers. - Dinrail - Pannel - Wires - Cables - Connectors - Player. - Test bench | Classroom / Workshop /Computer lab |
| LU4. Test the PLC | Trainee will be able to: - Locate field devices and their interface to PLC - Test the system in off line mode using simulator - Test the gauges independently for integration of main system with the sub-systems (if applicable) - Verify that the system conforms with all the user specifications during testing - Rework if there are any issues found and fix them - Send the test report for review to the customer - Perform Factory Acceptance Test (FAT) - Perform site acceptance test plan | - Describe the pre start procedures of PLC testing. - Describe PLC static (before operation) Input and output wiring check. - Describer the control program review. - Explain the Dynamic system checkout (Program logic review). - Explain Factory Acceptance Test (FAT) and Site Acceptance Test (SAT) for PLC. Practical Activity Perform the Factory Acceptance Test (FAT) of a PLC. Adopt necessary procedure to test the PLC operation. | Theory- 3 Hrs Practical-6Hrs Total- 09 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - PLC Communication cable. - PLC editing software. - Associated hardware (limit switch, actuators) hardware. - Push buttons. - Light Indicators. - Personal Computer - Power supply. - Hand tools. - Screwdriver - Test bench | Classroom / Workshop /Computer lab |

## 0714E&A110: Install Relays and Switches in circuits

Objective: The module covers the knowledge and skill required to: Implement Relays in circuits, Implement switches, Implement Proximity/Limit Switches

Duration: 30 Hours						Theory: 12 Hours						Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Implement Relays in circuits. | Trainee will be able to: - Identify different types of relay - Identify different terminals of relay - Install relay in circuit. | - Explain the function of Relay. - Differentiate between EMR and SSR relay. - Explain switches and their working w.r.t application. - Explain the different ways to install relays(EMR,SSR, Read, e.t.c…) in panels and circuits. Practical Activity - Develop a control circuit to operate 220 VAC motor using Electro mechanical relay. - Design a flickering flash light indicator circuit using Solid State relay. | Theory- 04 Hrs Practical-06 Hrs Total- 10 Hrs | - General tool kit - Electrical / Electronic Test equipment - Temperature gun. - PPE’s - Soldering gun - Operation manual. - Multimeter - Desktop computer and table. - White board with markers. - Projector - 24VDC Power Supply - Wire 1mm - 24 VDC Relay with base. - PLC - PLC cable | Classroom / Workshop /Computer lab |
| LU2. Implement switches | Trainee will be able to: - Develop PLC application as per user requirement by following the standard operating procedure (SOP) of the organization - Apply approved engineering concepts, processes and principles in developing the PLC application - Install organization approved software (system and application software) to develop the system | - Explain the electrical wiring drawing. - Define switches and their various application w.r.t. their types. - Explain the functions of switches in association with PLC. - Explain various connection techniques to integrate switches with PLC. Practical Activity Develop a latch circuit using push buttons with relays. | Theory- 04 Hrs Practical-06 Hrs Total- 10 Hrs | - General tool kit - Electrical / Electronic Test equipment - Temperature gun. - PPE’s - Soldering gun - Operation manual. - Multimeter - Desktop computer and table. - White board with markers. - Projector - 24VDC Power Supply - Wire 1mm - 24 VDC relay with base. | Classroom / Workshop /Computer lab |
| LU3. Implement Proximity /Limit Switches | Trainee will be able to: - Identify the Proximity switches. - Identify the Limit switches. - Identify the requirement of indications (LED) for ON/OFF states switches. - Draw layout on paper of circuit. - Connect circuit components as per layout. | - Explain various types of limit switches. - Explain the electrical symbols in drawing. - Explain various types of proximity switches. - Explain the various types of switches connections (wring). Practical Activity - Connect the Eye mark(sensor) controller with the packaging machine to count the packets. - Connect the limit switch with a motorized door operation. | Theory- 04 Hrs Practical-06 Hrs Total- 10 Hrs | - General tool kit - Electrical / Electronic Test equipment - Temperature gun. - PPE’s - Soldering gun - Operation manual. - Multimeter - Desktop computer and table. - White board with markers. - Projector - 24VDC Power Supply - Wire 1mm - 24 VDC relay with base. | Classroom / Workshop /Computer lab |

## 0714E&A111: Carry out Industrial Automation on PLC

Objective: The module covers the knowledge and skill required to: Implement industrial application using instruments and communication system, Analyze user requirements and specifications, Implement DC Motor control with PLC,  Proximity and Limit Switches, Maintenance and Troubleshooting.

Duration: 36 Hours						Theory: 12 Hours						Practical: 24 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Implement industrial application using instruments and communication system | Trainee will be able to: - Sketch the process of application (Flowchart, Pseudo code) - Identify process data and communication protocols and their specification - Implement open/close loop motor control - Implement a communication BUS system to monitor remote data | - Explain the use of Flow chart for process elaboration/demonstration. - Explain the difference between Pseudo code and flowchart. - Describe various communication protocols (Modbus, CNET, PPI, MPI….) used in PLC for industrial communication. - Describe DCS and SCADA communication protocol. - Explain Remote Terminal Unit RTU uses and application. - Describe the Industrial Ethernet communication. Practical Activity - Establish a communication between PC and PLC using MPI communication cable with desired parameters. - Establish a communication between PC and HMI using RS232 communication cable with desired parameters. - Establish a communication between PLC and HMI using communication cable with desired parameters | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - PLC Software - Communication Module - Simulator - Helping Manual - User guide - Communication driver. | Classroom / Workshop /Computer lab |
| LU2. Analyze user requirements and specifications | Trainee will be able to: - Draw the general value chain of the end user industry - Highlight the set of activities that a firm operating in a specific industry performs in the value chain drawing - Enlist the equipment / gauges / sensors / actuators / transducers used in different stages of the process - Identify critical stages in the process - Identify the safety aspect required in the critical stages of the process - Analyze the possible automation in the existing processes and global trends in automation - Analyze the client requirement at broad level from the proposal - Generate a report of various industrial processes involved in industry - Collect the required specification of the equipment (if already prepared by the user) and clarify the technical specification. | - Describe the general requirements of a project. - Describe the frequently required parameters considered by the user in PLC based system. - Explain the critical stages of a project for quick response. - Describe the methods for selecting the appropriate hardware or software as per user need. - Describe the basic project management skill needed to complete the project without omitting the necessary needs. - Describe the importance of supportive (exemplary) documents for justifying the selection of components and software. Practical Activity - Implement the PLC based project from user requirement till finalization stage with fulfilling all necessary user and technical needs | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - Stationary. - Need Assessment Form. - Hardware manuals. - Manufacturer list. - Cost analysis tool. - Varinty analysis. - MTBF evaluation. - Project management software. | Classroom / Workshop /Computer lab |
| LU3. Implement DC Motor control with PLC, Proximity and Limit Switches. | Trainee will be able to: - Enlist the required hardware and tool used in different stages of the process. - Draw a circuit connection diagram - Draw control strategy of system - Make physical connection of PLC, DC motor, Proximity switch and limit switch as per drawing. - Power up the circuit. - Write and upload the code - Write report | - Explain the method to generate requirement list (hardware / software). - Explain the circuit connection diagram for elaboration. - Explain the flow control of the operating logic of PLC. - Describe the wiring connection layout of loads and control circuit associated with PLC system. - Describe the operation of sensor and transducers associated with the PLC system. - Describe the control logic of the system systematic operation. - Explain the report generation methods for given tasks. Practical Activity A part is places on the conveyer at S1. A start push button is pressed which moves the part on the conveyer to the spray painting booth. As the part enter the booth sensor SN1 Enable paint sprayer. As the conveyer moves on senxor SN2 sense the part and stop the spray motor. When the part reaches at location S2 the conveyer stops automatically. The system may be stop at any time by pressing stop button. | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - PLC Software - DC Motor - Proximity Switches - Limit Switches - Screw drivers - Simulator - Helping Manual - User guide - Wiring and Connectors - Power supply. - PPE | Classroom / Workshop /Computer lab |
| LU4. Maintenance and Troubleshooting | Trainee will be able to: - Identify status of LEDs on Power Supply, CPU, I/O Cards - Match status LEDs within troubleshooting tables defined in manufacturer manual - Monitoring of Input and Output status using Programming interface - Carry out replacement of faulty cards as per manufacturer instructions - Perform replacement of faulty back up battery on PLC - Identify problems in control circuit for I/O by loop testing, contact resistance, signal electrical parameters | - Describe Error codes w.r.t manufactures specification. - Explain the uses of troubling table - Explain the hardware troubleshooting methods for associated components (Diode, transistor, LED, CPU, Modules). - Explain basic troubleshooting technique may incuse short circuit test, continuity test, power break up test. Practical Activity Troubleshoot the power supply of the PLC for fault detection and elimination. | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - PLC . - Power Supply. - Power Source. - Test and measuring equipment. - Troubleshooting manual. - PPE | Classroom / Workshop /Computer lab |

## 0714E&A112:  Interface PLC with system-II

Objective: The module covers the knowledge and skill required to: Interface Relay/Push button with PLC for Start/Stop Relay Logic, Single Push Button On/Off Logic, Interface Pneumatic linear Actuator and Pressure Sensor with PLC to Apply pressure on a body and o measure the linear distance covered by actuator, . Interface Servo motor with PLC to Control rpm, Rotary Position, Interface Stepper motor with PLC to control rotary Position.

Duration: 36 Hours						Theory: 12 Hours						Practical: 24 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Interface Relay/Push button with PLC for I) Start/Stop Relay Logic ii) Single Push Button On/Off Logic. | Trainee will be able to: - Draw connection layout of all hardware. - Connect the components (Relay, Push Button) as per layout. - Make and test ladder logic code PLC - Upload code to PLC - Run PLC and perform task - Get the results BUS system to monitor remote data | - Define the importance of layout design. - Define the importance of right symbol used in the layout. - Define various types of relays and switches as per their uses. - Define the program uploading/downloading process. Practical Activity - Install PLC programming software. - Install HMI Software. - Establish communication between PLC and Program editor. | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - PLC Communication cable. - PLC editing software. - Relays. - Push buttons. - Light Indicators. - Personal Computer. - Power source. - Test bench | Classroom / Workshop /Computer lab |
| LU2. Interface Pneumatic linear Actuator and Pressure Sensor with PLC to - Apply pressure on a body ii) To measure the linear distance covered by actuator. | Trainee will be able to: - Identify and enlist the components and sensors as per requirement. - Draw connection layout of all hardware. - Connect the components (pneumatic linear actuator) as per layout. - Make and test ladder logic code PLC - Upload code to PLC - Run PLC and perform task - Get the results (Pressure and Distance) | - Define Pneumatic Linear Actuator. - Define various types of Pressure sensors. - Explain the connection types of pressure sensors and linear actuator. Practical Activity - Develop PLC logic for testing and operation of Pressure sensor. - Develop PLC logic for testing and operation of linear actuator. | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - PLC Communication cable. - PLC editing software. - Relays. - Push buttons. - Light Indicators. - Personal Computer - Power supply. - Pressure sensor - Linear actuator. - Hand tools. - Tape. - Player. Test bench | Classroom / Workshop /Computer lab |
| LU3. Interface Servo motor with PLC to - Control rpm ii) Rotary Position. | Trainee will be able to: - Identify and enlist the components and sensors as per requirement. - Draw connection layout of all hardware. - Connect the components (pneumatic linear actuator) as per layout. - Make and test ladder logic code PLC - Upload code to PLC - Run PLC and perform task - Get the results (RPM and Position) | - Define the servo motor operation. - Explain the servo motor control system. - Explain the rotary operation of servo motor control. - Define the connection of servo motor with PLC module. - Explain the servo motor configuration and integration with PLC (software/ hardware) Practical Activity Connect and configure the PLC to operate with servo motor on defined parameters. | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - Servo Motor. - PLC Communication cable. - PLC editing software. - Relays. - Push buttons. - Light Indicators. - Personal Computer - Power supply. - Pressure sensor - Linear actuator. - Hand tools. - Tape. - Player. - Test bench | Classroom / Workshop /Computer lab |
| LU4. Interface Stepper motor with PLC to control rotary Position | Trainee will be able to: - Identify and enlist the components and sensors as per requirement. - Draw connection layout of all hardware. - Connect the components (pneumatic linear actuator) as per layout. - Make and test ladder logic code PLC - Upload code to PLC - Run PLC and perform task - Get the results (Position) | - Define the stepper motor operation. - Explain the stepper motor control system. - Explain the rotary operation of stepper motor control. - Define the connection of stepper motor with PLC module. - Explain the stepper motor configuration and integration with PLC (software/ hardware) Practical Activity Connect and configure the PLC to operate with stepper motor on defined parameters. | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - PLC Power supply. - PLC CPU. - PLC Interfacing module. - Servo Motor. - PLC Communication cable. - PLC editing software. - Relays. - Push buttons. - Light Indicators. - Personal Computer - Power supply. - Pressure sensor - Linear actuator. - Hand tools. - Tape. - Player. - Test bench | Classroom / Workshop /Computer lab |

# T-Industrial Instrumentation & Control

## 0714E&A113:  Install Transducers & Transmitters in Industrial Application

Objective: This module covers the knowledge and skills required to grasp the uses, basic concepts, installation, and maintenance of transducers and industrial transmitters.

Duration: 36 Hours				Theory: 12 Hours						Practical: 24 Hours

| Learning Unit | Learning Outcomes |  | Learning Elements |  | Duration |  | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| LU1: Install Flow Transmitter | Trainee will be able to: - Analyze the Flow transducer/transmitter to be installed. - Install the Flow transducer/transmitter as per the installation’s manual. - Perform the post installation measures. - Generate an output report for the transducer/transmitter. |  | - Describe Safety Protocol at Workstation - Describe types of Flow Transmitter - Define working principle of Flow Transmitter Practical Activity: Select the type of flow Transmitter to be installed as per drawing. Install the flow Transmitter in the system and check the output as per standard. |  | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs |  | - Flow Transmitter - Multi meter - Connecting tube - Connecting Cables - Spanner set - Screw driver set - Watch maker - Screw driver Set - Stationary - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Safety Shoes - Safety Helmet - Allen Key set - Wire Cutter - Wire Stripper - Calibrator for Flow - Flow channel | Classroom / Workshop /Computer lab |
| LU2: Install Level Transmitter |  | Trainee will be able to: - Analyze the Level transducer/transmitter to be installed. - Install the Level transducer/transmitter as per the installations manual.. - Perform the post installation measures. - Generate an output report for the transducer/transmitter |  | - Describe Safety Protocol at Workstation - Describe types of Level Transmitter - Define working principle of Level Transmitter Practical Activity: Select the type of Level Transmitter to be installed as per drawing. Install the Level Transmitter in the system and check the output as per standard. |  | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - Level Transmitter - Multi meter - Connecting tube - Connecting Cables - Spanner set - Screw driver set - Watch maker - Screw driver Set - Stationary - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Safety Shoes - Safety Helmet - Allen Key set - Wire Cutter - Wire Stripper - Calibrator for Level | Classroom / Workshop /Computer lab |
| LU3: Install Pressure Transmitter |  | Trainee will be able to: - Analyze Pressure transducer/transmitter to be installed. - Install the Pressure transducer/transmitter as per the installations manual.. - Perform the post installation measures. - Generate an output report for the transducer/transmitter. |  | - Describe Safety Protocol at Workstation - Describe types of Pressure Transmitter - Define working principle of Pressure Transmitter Practical Activity: Select the type of Pressure Transmitter to be installed as per drawing. Install the Pressure Transmitter in the system and check the output as per standard. |  | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - Pressure Transmitter - Multi meter - Connecting tube - Connecting Cables - Spanner set - Screw driver set - Watch maker - Screw driver Set - Stationary - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Safety Shoes - Safety Helmet - Allen Key set - Wire Cutter - Wire Stripper - Calibrator for Pressure - Air Compressor | Classroom / Workshop /Computer lab |
| LU4: Install Temperature Transmitter |  | Trainee will be able to: - Analyze the type of transducer/transmitter to be installed. - Install the desired type of transducer/transmitter as per the installations manual.. - Perform the post installation measures. - Generate an output report for the transducer/transmitter. |  | - Describe Safety Protocol at Workstation - Describe types of Temperature Transmitter - Define working principle of Temperature Transmitter Practical Activity: Select the type of Temperature Transmitter to be installed as per drawing. Install the Temperature Transmitter in the system and check the output as per standard. |  | Theory- 3 Hrs Practical-6 Hrs Total- 09 Hrs | - Temperature Transmitter - Multi meter - Connecting tube - Connecting Cables - Spanner set - Screw driver set - Watch maker - Screw driver Set - Stationary - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Temperature Bath - Safety Shoes - Safety Helmet - Allen Key set - Wire Cutter - Wire Stripper - Calibrator for Temerature | Classroom / Workshop /Computer lab |

## 0714E&A114:  Install the Process regulators

Objective: This module covers the knowledge and skills required to grasp the uses, basic concepts and installation and maintenance of Process Regulators.

Duration: 24 Hours				Theory: 06 Hours						Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1: Install Flow regulator | Trainee will be able to: - Analyze the type of Flow Regulators to be installed. - Locate the point of installation for Flow Regulators. - Install the Flow Regulator as per the instructions in manual. - Perform Post Installation measures. | - Describe safety protocol at Workstation - Describe types of Flow Regulator - Define working principle of Flow regulator Practical Activity: Identify and install the Flow regulator in the system as per sop. Apply input to the Flow regulator and verify the output. | Total- 08Hrs Theory- 02Hrs Practical- 06Hrs | - Flow Regulators - Differential Pressure Flow meter - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Safety Shoes - Safety Helmet - Allen Key set - Connecting tube - Connecting Cables - Wire Cutter - Wire Stripper - Calibrator for Flow - Shut-Off Valves | Classroom / Workshop /Computer lab |
| LU2: Install Pressure Regulator | Trainee will be able to: - Analyze the type of Pressure Regulators to be installed. - Locate the point of installation for Pressure Regulators. - Install the Pressure Regulator as per the instructions in manual. - Perform post Installation measures. | - Describe safety protocol at Workstation - Describe types of Pressure Regulator - Define working principle of Pressure regulator Practical Activity: Identify and install the Pressure regulator in the system as per sop. Apply input to the Pressure regulator and verify the output. | Total- 08Hrs Theory- 02Hrs Practical- 06Hrs | - Pressure Regulators - Differential Pressure Flow meter - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Safety Shoes - Safety Helmet - Allen Key set - Connecting tube - Connecting Cables - Wire Cutter - Wire Stripper - Calibrator for Pressure - Shut-Off Valves - Air Compressor | Classroom / Workshop /Computer lab |
| LU3: Install Temperature Regulator / Controller | Trainee will be able to: - Analyze the type of Temperature Regulators to be installed. - Locate the point of installation for temperature Regulators/Controller - Install the Flow Regulator as per the instructions in manual. - Perform Post Installation measures. | - Describe safety protocol at Workstation - Describe types of Temperature Regulator - Define working principle of Temperature regulator Practical Activity: Identify and install the Temperature regulator in the system as per sop. Apply input to the Temperature regulator and verify the output. | Total- 08Hrs Theory- 02Hrs Practical- 06Hrs | - Temperature Regulators - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Safety Shoes - Safety Helmet - Allen Key set - Connecting Cables - Wire Cutter - Wire Stripper - Calibrator for Temperature - Shut-Off Valves - TRIAC Module - DIAC Module - VFD | Classroom / Workshop /Computer lab |

## 0714E&A115:  Install the Variable Frequency Drive

Objective: This module covers the knowledge and skills required to grasp the uses, basic concepts and installation and maintenance of variable frequency drives.

Duration:  18 Hours				Theory: 06 Hours						Practical: 12 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1: Install and Set parameters of Variable Frequency Drive | Trainee will be able to: - Analyze the type of VFD to be installed. - Select the appropriate type of VFD. - Install the desired VFD type as per the installation instructions. - Perform a test run on the VFD - Analyze the required parameter. - Select the appropriate parameter - Perform Parameter downloading - Perform a test run with parameter - Generate the Output report | - Describe safety protocol at Workstation - Describe types of VFD - Define working principle of VFD Practical Activity: Construct a Start/Stop three phase motor circuit through Variable Frequency Drive (VFD). | Total- 18Hrs Theory- 06Hrs Practical- 12Hrs | - 3-phase Motor - Multi-meter - Oscilloscope - Signal Generator - Product manual - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Safety Shoes - Safety Helmet - Allen Key set - Screw Driver Set - Spanner Set - Connecting tube - Connecting Cables - Wire Cutter - Wire Stripper | Classroom / Workshop /Computer lab |

## 0714E&A116:  Install Pneumatic & Hydraulic system in the Industry

Objective This module covers the knowledge and skills required to grasp the uses, basic concepts and installation and maintenance of Pneumatic & Hydraulic System in industry.

Duration: 27 Hours				Theory: 09 Hours						Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1: Install Pneumatic actuators | Trainee will be able to: - Analyze the type of Pneumatic actuators to be installed. - Locate the point of installation for Pneumatic actuator. - Install the Pneumatic actuator as per the installations manual. - Perform Post Installation measures - Generate an output report for the actuator. | - Describe safety protocol at Workstation - Describe types of Pneumatic Actuators - Define working principle of Pneumatic Actuators Practical Activity: Identify and install the Pneumatic Actuator in the system as per sop. Operate the Pneumatic Actuator and verify the output. | Total- 09Hrs Theory- 03Hrs Practical- 06Hrs | - Pneumatic Actuators - Pneumatic DCV - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Safety Shoes - Safety Helmet - Allen Key set - Connecting tube - Connecting Cables - Wire Cutter - Wire Stripper - Shut-Off Valves | Classroom / Workshop /Computer lab |
| LU2: Install Pneumatic transmitters | Trainee will be able to: - Analyze the type of Pneumatic transmitters to be installed. - Locate the point of installation for Pneumatic transmitter. - Install the Pneumatic Transmitter as per the installations manual. - Perform Post Installation measures - Generate an output report for the transmitter. | - Describe safety protocol at Workstation - Describe types of Pneumatic Transmitter - Define working principle of Pneumatic Transmitter Practical Activity: Identify and install the Pneumatic Transmitter in the system as per sop. Apply input to the Pneumatic Transmitter and verify the output. | Total- 09Hrs Theory- 03Hrs Practical- 06Hrs | - Pneumatic Transmitter - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Safety Shoes - Safety Helmet - Allen Key set - Connecting tube - Connecting Cables - Wire Cutter - Wire Stripper - Shut-Off Valves - 4-20 mA source - 3-15 psi compressed air source | Classroom / Workshop /Computer lab |
| LU3: Install Pneumatic directional control Valves | Trainee will be able to: - Analyze the type of Pneumatic Directional Control Valve to be installed. - Locate the point of installation for Pneumatic Directional Control Valve - Install the Pneumatic Directional Control Valve as per the installations manual. - Perform Post Installation measures - Generate an output report for the transmitter. | - Describe safety protocol at Workstation - Describe types of Pneumatic Directional Control Valves - Define working principle of Directional Control Valves Practical Activity: Identify and install the Pneumatic Directional Control Valves in the system as per sop. Operate the Pneumatic Directional Control Valve and verify the output. | Total- 09Hrs Theory- 03Hrs Practical- 06Hrs | - Pneumatic Directional control valve - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Safety Shoes - Safety Helmet - Allen Key set - Connecting tube - Connecting Cables - Wire Cutter - Wire Stripper - Shut-Off Valves - Air Compressor | Classroom / Workshop /Computer lab |

## 0714E&A117:  Installation & Setup Procedure for Digital Pressure, Temperature, Level & Flow Controllers

Objective: This module covers the knowledge and skills required to standard Installation procedure and setup of Pressure, Temperature, Level and Flow, Controllers.

Duration: 36 Hours						Theory: 12 Hours						Practical: 24 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1: Installation and setup of Digital Pressure Controllers. | Trainee will be able to: - Analyse the requirement of Digital Pressure Controllers. - Analyse the Digital Pressure controller datasheet according to the application and measurement required. - Select the Digital Pressure Controller as per requirement with the help of pressure range and its mounting. - Draw Sketch diagram as per required application - Install the Digital pressure Controller as per installation guidelines. - Test and calibrate the Digital Pressure Controller as per SOP. - Prepare Installation reports of Digital Pressure Controller. | - Describe Safety Protocol at Workstation - Describe types of Digital Pressure Controllers - Define working principle of Digital Pressure Controllers Practical Activity: Select the type of Digital Pressure Controller to be installed as per drawing. Install the Digital Pressure Controller in the system and check the output as per standard. | Total- 09Hrs Theory- 3Hrs Practical- 06Hrs | - Digital Pressure Controller - Multi meter - Connecting tube - Connecting Cables - Differential pressure flow meter - Spanner set - Screw driver set - Watch maker Screw driver Set - Stationary - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Safety Shoes - Safety Helmet - Allen Key set - Wire Cutter - Wire Stripper - Calibrator for Pressure - Air Compressor | Class Room and Workshop / Field Visit |
| LU2: Installation and setup of Digital Temperature Controllers. | Trainee will be able to: - Analyse the requirement of Digital Temperature Controllers. - Analyse the Digital Temperature controller datasheet according to the application and measurement required. - Select the Digital Temperature Controller as per requirement with the help of pressure range and its mounting. - Draw Sketch diagram for as per required application - Install the Digital Temperature Controller as per installation guidelines. - Test and calibrate the Digital Temperature Controller as per SOP. - Prepare Installation reports Digital Temperature Controller. | - Describe Safety Protocol at Workstation - Describe types of Digital Temperature Controllers - Define working principle of Digital Temperature Controllers Practical Activity: Select the type of Digital Temperature Controller to be installed as per drawing. Install the Digital Temperature Controller in the system and check the output as per standard. | Total- 09Hrs Theory- 3Hrs Practical- 06Hrs | - Digital Temperature Controller - Multi meter - Connecting tube - Connecting Cables - Spanner set - Screw driver set - Watch maker - Screw driver Set - Stationary - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Safety Shoes - Safety Helmet - Allen Key set - Wire Cutter - Wire Stripper - Calibrator for Temperature - Assorted Temperature Sensor | Class Room and Workshop / Field Visit |
| LU3: Installation and setup of Digital Level Controllers. | Trainee will be able to: - Analyse the requirement of Digital Level Controllers. - Analyse the Digital Level controller datasheet according to the application and measurement required. - Select the Digital Level Controller as per requirement with the help of pressure range and its mounting. - Draw Sketch diagram for as per required application - Install the Digital Level Controller as per installation guidelines. - Test and calibrate the Digital Level Controller as per SOP. - Prepare Installation reports Digital Level Controller. | - Describe Safety Protocol at Workstation - Describe types of Digital Level Controllers - Define working principle of Digital Level Controllers Practical Activity: Select the type of Digital Level Controller to be installed as per drawing. Install the Digital Level Controller in the system and check the output as per standard. | Total- 09Hrs Theory- 3Hrs Practical- 06Hrs | - Digital Level Controller - Multi meter - Connecting tube - Connecting Cables - Spanner set - Screw driver set - Watch maker - Screw driver Set - Stationary - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Safety Shoes - Safety Helmet - Allen Key set - Wire Cutter - Wire Stripper - Digital Calibrator for Level | Class Room and Workshop / Field Visit |
| LU4: .Installation and setup of Digital Flow Controllers | Trainee will be able to: - Analyse the requirement of Digital Flow Controllers. - Analyse the Digital Flow controller datasheet according to the application and measurement required. - Select the Digital Flow Controller as per requirement with the help of pressure range and its mounting. - Draw Sketch diagram for as per required application - Install the Digital Flow Controller as per installation guidelines. - Test and calibrate the Digital Flow Controller as per SOP. - Prepare Installation reports Digital Flow Controller. | - Describe Safety Protocol at Workstation - Describe types of Digital Flow Controller - Define working principle of Digital Flow Controller Practical Activity: Select the type of Digital Flow Controller to be installed as per drawing. Install the Digital Flow Controller in the system and check the output as per standard. | Total- 09Hrs Theory- 3Hrs Practical- 06Hrs | - Digital Flow Controller - Multi meter - Connecting tube - Connecting Cables - Spanner set - Screw driver set - Watch maker - Screw driver Set - Stationary - White board with marker - Multimedia projector - Desktop Computer - Computer Table with chair - Cotton Gloves - Safety Glasses - Safety Shoes - Safety Helmet - Allen Key set - Wire Cutter - Wire Stripper - Calibrator for Flow | Class Room and Workshop / Field Visit |

# U-Repair & Maintenance of Automation Equipment

## 0714E&A118:  Identify Fault in Automation/ Process Equipment Installation.

Objective: This module identifies the competencies required to perform trouble shooting at workplace in accordance with the manufacturer’s instructions and organizational requirements.

Duration:  24 Hours							Theory: 06Hours						Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |  |
| --- | --- | --- | --- | --- | --- | --- |
| - Prepare a list of items/material(s) required for repair/replacement as per specifications | - Identify the required items for repair & replacement - List down the items as per specification. | - Explain the preparation procedure for list for items required for repairing and replacement - Define the listed items needed for replacement. Practical Activity. Prepare the list of items/material(s) required for repair/replacement. | Theory- 02Hrs Practical-06Hrs Total-08Hrs | - Multimeter - Spanner set - Allen key set - Combinational Plier - Cable cutter - Pipe wrench set - Hacksaw - Toolkit - Hand drill machine - Measuring tape - Desktop computer with table - White board with marker. - Workbench with wise. - Projector. |  | Classroom and Workshop |
| - Make necessary troubleshooting according to the standards | - Study the log sheet/history card thoroughly before trouble shooting. - Identify the reported problem with the help of service manual and test run standards (if required). - Identify the root cause. | - Explain the troubleshooting procedure as per equipment SOP. - Explain the procedure/ method of log sheet / history card development. Practical Activity. Perform to make necessary troubleshooting according to the standards. | Theory- 02Hrs Practical-06Hrs Total-08Hrs | - Multimeter - Spanner set - Allen key set - Combinational Plier - Cable cutter - Pipe wrench set - Hacksaw - Toolkit - Hand drill machine - Measuring tape - Desktop computer with table - White board with marker. - Workbench with wise. - Projector. |  | Classroom and Workshop |
| - Corrective action and record keeping. | - Take the corrective action to resolve the problem. - Verify the corrective action and lock the parameter. - Record this problem and corrective action in to History card and save this for future troubleshooting. | - Explain the importance of record keeping and utilization for future needs - Explain the corrective action needed for record keeping. - Explain the reference data importance in taking corrective measures from record. Practical Activity. - Implement the necessary procedure for record keeping. - Utilize the recorded data (history card) for upcoming error elimination/ corrections. | Theory- 02Hrs Practical-06Hrs Total-08Hrs | - Multimeter - Spanner set - Allen key set - Combinational Plier - Cable cutter - Pipe wrench set - Hacksaw - Toolkit - Hand drill machine - Measuring tape - Multimeter |  | Classroom and Workshop |

## 0714E&A119:  Perform Troubleshooting of equipment.

Objective: This module identifies the competencies required to perform trouble shooting at workplace in accordance with the manufacturer’s instructions and organizational requirements.

Duration:  24 Hours							Theory: 6Hours						Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |  |
| --- | --- | --- | --- | --- | --- | --- |
| - Prepare a list of items/material(s) required for repair/replacement as per specifications | - Identify the required items for repair & replacement - List down the items as per specification. | - Explain the preparation procedure for list for items required for repairing and replacement - Define the listed items needed for replacement. Practical Activity. Prepare the list of items/material(s) required for repair/replacement. | Theory- 2Hrs Practical-06Hrs Total-08Hrs | - Multimeter - Spanner set - Allen key set - Combinational Plier - Cable cutter - Pipe wrench set - Hacksaw - Toolkit - Hand drill machine - Measuring tape - Desktop computer with table - White board with marker. - Workbench with wise. - Projector. |  | Classroom and Workshop |
| - Make necessary troubleshooting according to the standards | - Study the log sheet/history card thoroughly before trouble shooting. - Identify the reported problem with the help of service manual and test run standards (if required). - Identify the root cause. | - Explain the troubleshooting procedure as per equipment SOP. - Explain the procedure/ method of log sheet / history card development. Practical Activity. Perform to make necessary troubleshooting according to the standards. | Theory- 2Hrs Practical-06Hrs Total-08Hrs | - Multimeter - Spanner set - Allen key set - Combinational Plier - Cable cutter - Pipe wrench set - Hacksaw - Toolkit - Hand drill machine - Measuring tape - Desktop computer with table - White board with marker. - Workbench with wise. - Projector. |  | Classroom and Workshop |
| - Corrective action and record keeping. | - Take the corrective action to resolve the problem. - Verify the corrective action and lock the parameter. - Record this problem and corrective action in to History card and save this for future troubleshooting. | - Explain the importance of record keeping and utilization for future needs - Explain the corrective action needed for record keeping. - Explain the reference data importance in taking corrective measures from record. Practical Activity. - Implement the necessary procedure for record keeping. - Utilize the recorded data (history card) for upcoming error elimination/ corrections. | Theory- 2Hrs Practical-06Hrs Total-08Hrs | - Multimeter - Spanner set - Allen key set - Combinational Plier - Cable cutter - Pipe wrench set - Hacksaw - Toolkit - Hand drill machine - Measuring tape - Multimeter |  | Classroom and Workshop |

## 0714E&A120:  Perform Preventive Maintenance of Equipment.

Objective: This module identifies the competencies required to carry out repair and maintenance of Automation/ Process Equipment installations at workplace in accordance with the manufacturer’s instructions and organizational requirements. The underpinning knowledge regarding carrying out repair and maintenance of Automation/ Process Equipment installations will be sufficient to provide the basis for your work.

Duration:  28 Hours							Theory: 10Hours						Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Carry out Preventive maintenance as specified by the manufacturers | - Identify unsafe conditions & take actions / steps - Prepare inspection plan for preventive maintenance as per service manual. - Apply preventive maintenance to ensure production or industrial process run smoothly. - Perform test run. | - Explain the importance of preventive maintenance. - Explain the procedure of preventive maintenance and its significance on the plant. Practical Activity. Perform preventive maintenance and to ensure industrial process run smoothly as defined by user manual. | Theory- 05Hrs Practical-09Hrs Total-14Hrs | - Multimeter - Toolset - Desktop - Projector - White board - Board marker. - Desktop computer. - Computer table. | Classroom and Workshop |
| - Update Maintenance/service records as per requirement | - Maintain equipment log book - Prepare maintenance report of performed job | - Explain the uses and importance of equipment logbook. - Explain the method of maintaining the equipment logbook. - Explain theentries of equipment logbook. - Define the procedure of equipment logbook. Practical Activity. Perform to make a detailed equipment logbook and record its data and make an history card. | Theory- 05Hrs Practical-09Hrs Total-14Hrs | - Multimeter - Toolset - Desktop - Projector - White board - Board marker. - Desktop computer - Computer table. | Classroom and Workshop |

# V-Boiler Instrumentation

## 0714E&A121:  Operate Boiler Control system

Objective: After the following competency standard, the student will be able to operate, perform operational shutdowns, monitor, analyze and record boiler data in various industries.

Duration: 24 Hours	                                       			Theory: 06 Hours	                                                Practical:  18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1: Prepare the boiler for operation | Trainee will be able to: - Identify Health and safety hazards & report to responsible personnel. - Purge the boiler according to workplace procedure - Perform pre-operational checks & confirm operational status of boiler and related equipment | - Describe the Boiler operation checks - Describe Health & safety hazards Practical Activity Design hardware of boiler for operation | Theory- 1 Hrs Practical- 3Hrs Total- 04Hrs | - Datasheets - Digital pressure gauge - Digital thermometer - Electrical Tester - Electrical Tool Box - Function generator - Jumper wire set - Mili-Amp Source - Multi-Meter | Class Room and Workshop |
| LU2: Start and monitor boiler operation | - Start the boiler safely as per manufacturer’s specifications - Operate the plant within limits of manufacturer’s specifications - Monitor the Equipment to confirm operating condition - Test the water quality and adjust as required - Ensure that the workplace meets housekeeping standards | - Describe the services associated with boilers - Explain the boiler system layout and steam/oil cycle - Explain the importance and procedure of ash removal - Explain the limitation of a boiler and the process data which need to be monitored Practical Activity Start the boiler and monitor parameters of boiler operation | Theory- 1 Hrs Practical- 3Hrs Total- 04Hrs | - Datasheets - Digital pressure gauge - Digital thermometer - Electrical Tester - Electrical Tool Box - Function generator - Jumper wire set - Mili-Amp Source - Multi-Meter | Class Room and Workshop |
| LU3: Analyze and respond to abnormal performance | - Analyze operating data and plant operating conditions to identify causes of abnormal performance - Take corrective action in response to Hazards - Implement emergency procedures as required | - Explain the parameter which impacts the shutdown. - Explain the pre-handover procedures/checklist and their impact on overall operation. - Explain the relationships of process variables and data curves - Explain the basic working principles of combustion operation - Explain the cleaning/purging procedure (internal/external) during shutdown - Define the data and their operating ranges. Practical Activity Analyze and respond to abnormal performance in boiler operation | Theory- 1 Hrs Practical- 3Hrs Total- 04Hrs | - Datasheets - Digital pressure gauge - Digital thermometer - Electrical Tester - Electrical Tool Box - Function generator - Jumper wire set - Mili-Amp Source - Multi-Meter | Class Room and Workshop |
| LU4: Handover the boiler operations | - Maintain the workplace in accordance with statutory requirements and workplace procedures - Carry out Handing over according to workplace procedure | - Define the importance of PPEs and safe working procedures - Explain the procedure of Handover the boiler operation Practical Activity Handover the shift responsibility of boiler operations | Theory- 1 Hrs Practical- 3Hrs Total- 04Hrs | - Datasheets - Digital pressure gauge - Digital thermometer - Electrical Tester - Electrical Tool Box - Function generator - Jumper wire set - Mili-Amp Source - Multi-Meter | Class Room and Workshop |
| LU5: Carry out an operational shutdown | - Shut down the boiler according to workplace procedures - Identify the maintenance requirements & report according to workplace reporting procedure | - Explain the purpose of purging, efficiency of fuel, tagout/lockout. - Explain the operational and emergency shutdown procedure. - Define the operational data and its importance - Explain the procedures for responding to emergency situations including safe shutdown procedure Practical Activity - Perform operational shutdown of boiler | Theory- 1 Hrs Practical- 3Hrs Total- 04Hrs | - Datasheets - Digital pressure gauge - Digital thermometer - Electrical Tester - Electrical Tool Box - Function generator - Jumper wire set - Mili-Amp Source - Multi-Meter | Class Room and Workshop |
| LU6: Prepare the boiler for an internal inspection | - Shut down the boiler according to workplace procedures - Clean the boiler is internally and externally according to workplace procedures - Remove the valves and fittings - Place the boiler in the appropriate storage mode according to manufacturer’s recommendations - Generate a record report | - Understand the inspection procedure as per SOP | Theory- 1 Hrs Practical- 3Hrs Total- 04Hrs | - Datasheets - Digital pressure gauge - Digital thermometer - Electrical Tester - Electrical Tool Box - Function generator - Jumper wire set - Mili-Amp Source - Multi-Meter | Class Room and Workshop |

## 0714E&A122:  Install the Boiler Control system

Objective: After this competency standard the student will be able to implement, troubleshoot and perform maintenance and diagnostics of boiler instruments and its control system in various industries.

Duration: 42 Hours	                                           			Theory: 06 Hours	                                                Practical:  36 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Install feed water control | Trainee will be able to: - Select tools and raw material as per drawing standards - Select appropriate feed water control system components as per drawing or process sheet. - Test feed water control - Assemble and install feed water control system | - Describe the Working principle and method of boiler. • Describe the installation and calibration method of Current to Pneumatic (I/P) and Pneumatic to Current (P/I) converters • Explain the types of mounting fittings and their working principles. • Define instruments as per need and environment. • Explain applications of Bernoulli’s Theorem. • Describe the heating system and its effectiveness. • Explain the importance and procedure of flow, pressure and temperature compensation. Practical Activity Select given fittings & Instruments according to the required specification. | Theory- 1Hrs Practical-09Hrs Total- 10Hrs | - Datasheets - Digital pressure gauge - Digital thermometer - Electrical Tester - Electrical Tool Box - Function generator - Jumper wire set - Mili-Amp Source - Multi-Meter | Class Room and Workshop |
| - Install Drum level Control | Trainee will be able to: - Select tools and raw material as per drawing standards for drum level control - Select appropriate drum level control system components as per drawing or process sheet. - Test Drum level Control - Assemble and install drum level control | - Explain the installation and calibration method of Pressure, flow and differential Pressure transmitter (ΔP). O - Calculation for conversion of ΔP to flow measurement. - Explain the installation of Level and density transmitters/controllers. - Define the mounting and understanding of pressure and flow gauges with pig-tail siphon. - Explain the selection of digital and analog actuators. - Define ventilation system and its importance - Explain the working principles of motor operated valves. (MOV), regulators, air blower, ignition transformers knowledge of their impact on overall operation of a boiler. - Explain the use of Orifice plate for fluid and gas. Practical Activity Install given Instruments according to the SOP | Theory- 1Hrs Practical-09Hrs Total- 10Hrs | - Datasheets - Digital pressure gauge - Digital thermometer - Electrical Tester - Electrical Tool Box - Function generator - Jumper wire set - Mili-Amp Source - Multi-Meter - O&M Manuals - Part Manuals - Power supply - Spanner Set - Special Tools - Tagout/lockout tools - trainer | Class Room and Workshop |
| - Install Boiler Combustion Control | - Select tools and raw material as per drawing standards for Boiler Combustion Control system - Select appropriate Boiler Combustion Control system components as per drawing or process sheet. - Test Boiler Combustion Control system - Assemble and install Boiler Combustion Control system. - Perform fuel adjustment as per requirement | - Explain Boiler Combustion control - Describe the parts of Boiler Combustion control - Describe safety regulations for process. - Define Process Control Loop. - Define Tagging techniques of connections. - Define assembling & dismantling techniques. - Define testing techniques of connections· | Theory- 2Hrs Practical-09Hrs Total- 11Hrs | - Datasheets - Digital pressure gauge - Digital thermometer - Electrical Tester - Electrical Tool Box - Function generator - Jumper wire set - Mili-Amp Source - Multi-Meter | Class Room and Workshop |
| - Install Gas air ratio control system | - Select tools and raw material as per drawing standards for Gas air ratio control system - Select appropriate Gas air ratio control system components as per drawing or process sheet. - Test Gas air ratio control system - Assemble and install Gas air ratio Control system - Perform gas air ratio as per fuel supply | - Explain gas air ratio - Describe the parts of Gas air ratio control system - Define Operating principle of Sensors & Transducers - Define indicating, integrating and recording instruments. - Define Electrical/ - Describe the functional parameters of Sensors - Define the functional range of instruments - Define electronic fault diagnosis. - Define the component parameter, ratings and application of Instruments. | Theory- 2Hrs Practical-09Hrs Total- 11Hrs | - Datasheets - Digital pressure gauge - Digital thermometer - Electrical Tester - Electrical Tool Box - Function generator - Jumper wire set - Mili-Amp Source - Multi-Meter - O&M Manuals - Part Manuals - Power supply - Spanner Set - Special Tools - Tagout/lockout tools trainer | Class Room and Workshop |

# W-Application of Automation in daily life

## 0714E&A123:  Operate Product Counter

Objective: This module covers the specific skills and knowledge related to various types of product counter operation.

Duration: 24 Hours						Theory: 06 Hours					Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Setup and procedure before starting the operation | Trainee will be able to - Follow the handling precaution as per provided specification of counter. - Read the required parameters | - Describe PNP/NPN sensors. - Explain Pin diagram of Counter - Define Data sheet of counter PRACTICAL ACTIVITY: Set the set point of counter. | Total – 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Counter - LED Display - DC power supply - Multimeter - Tool set | Laboratory/ Workshop/ Classroom |
| - Introduction of Counters | Trainee will be able to - Demonstrate the various types of Counters. - Differentiate between UP & Down Counters. - Identify the Input / Output power of Counter meter. - Differentiate between NPN and PNP Signals. - Identify the pin of Input signals. | - Define Counters. - Identify different types of counters. - Explain the function of UP & Down Counters. PRACTICAL ACTIVITY: Perform calculations or scaling the values on counter. | Total – 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Counter - LED Display - DC power supply - Multimeter - Tool set | Laboratory/ Workshop/ Classroom |
| - Installation of Counters. | Trainee will be able to - Read the pin diagram of power, input and output signals. - Provide connection of Input power. - Connect any digital sensors wire in input of counter. - Verify the connections with multimeter. - Power On the supply. - Check the response by passing any obstacle in front of sensor. | - Define Counters. - Explain the operational procedure of different counters. - Function of UP & Down Counters. PRACTICAL ACTIVITY: Count the pulses by using up counter and display the result. | Total – 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Counter - LED Display - DC power supply - Multimeter - Tool set | Laboratory/ Workshop/ Classroom |

## 0714E&A124:  Operate ON / OFF / Delay Timers

Objective: This module covers the specific skills and knowledge related to operate on/off/delay timer various automation applications in our surrounding which is used and see every time in our daily life.

Duration: 24 Hours						Theory: 6 Hours					Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Setup Timer | Trainee will be able to: - Follow the handling precaution as per provided specification of timer - Input the required parameters. - Setup the timer. | - Explain the pin diagram of timer - Read the data sheet of given timer PRACTICAL ACTIVITY: Perform calculations or scaling the values on timer. | Total – 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Timer - LED Display - DC power supply - Multimeter - Tool set | Laboratory/ Workshop/ Classroom |
| - Introduction of Timer | Trainee will be able to: - Demonstrate the various types of Timers. - Differentiate between ON Delay Timer / OFF Delay Timer. - Identify the Input / Output power of Timer. - Differentiate between NPN and PNP Signals. - Identify the pin of Input signals / Output Signals. | - Explain the function of timer - Explain different types of timers. PRACTICAL ACTIVITY: Perform test on different types of timers. | Total – 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Timer - LED Display - DC power supply - Multimeter - Tool set | Laboratory/ Workshop/ Classroom |
| - Setup Delay Timer | Trainee will be able to: - Read the pin diagram of input and output power for signal. - Provide connection of Input power. - Connect the digital sensors / switch wire in Pulse input of Timer. - Verify the connections with multimeter. - Power On the supply. - Check the response of timer by providing any signal to timer. | - Define timers. - Function of On and Off delay timer. PRACTICAL ACTIVITY: Switch on the load for 5 seconds by using on delay timer | Total – 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Timer - LED Display - DC power supply - Multimeter - Tool set | Laboratory/ Workshop/ Classroom |

## 0714E&A125:  Operate speed controller

Objective: This module covers the specific skills and knowledge related to operate speed controller in various automation applications in our surrounding which is used and see every time in our daily life.

Duration: 24 Hours						Theory: 6 Hours					Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |  |
| --- | --- | --- | --- | --- | --- | --- |
| - Setup and procedure before starting the operation | Trainee will be able to - Follow the handling precaution as per provided specification of speed controller. - Read the required parameters. - Read the method of passing analog & digital signals. | - Describe main components used in speed controller. - Read the data sheet of given speed controller PRACTICAL ACTIVITY: Identify type of speed controllers. Check its various functions | Total – 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Speed Controller - Relay - DC power supply - Multimeter - Tool set - Tachometer |  | Laboratory/ Workshop/ Classroom |
| - Introduction of speed Controller. | Trainee will be able to - Demonstrate the various types of speed controllers. - Differentiate between analog & digital controller. - Identify the operational parameters of controllers. - Demonstrate Pulse Width Modulation. - Identify the pin of Input signals / Output Signals. | - Explain the pin diagram of speed controller. PRACTICAL ACTIVITY: Set the speed parameter and power up the speed controller. | Total – 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Speed Controller - Relay - DC power supply - Multimeter - Tool set - Tachometer |  | Laboratory/ Workshop/ Classroom |
| - Setup speed Controller | Trainee will be able to - Read the pin diagram of input and output power for signal of speed controllers. - Provide connection of Input power. - Verify the connections with multimeter. - Power On the supply. - Check the response of speed controller by varying potentiometer in clockwise / anticlockwise directions. | - Describe the function of speed controller PRACTICAL ACTIVITY: - Turn on the DC motor and run at speed of 100 rpm using counter. - Run the motor at full speed in anti-clock direction using speed controller. | Total – 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Speed Controller - Relay - DC power supply - Multimeter - Tool set - Tachometer |  | Laboratory/ Workshop/ Classroom |

## 0714E&A126:  Operate Level Detector

Objective: This module covers the specific skills and knowledge related to operate level detector controller in various automation applications in our surrounding which is used and see every time in our daily life.

Duration: 24 Hours						Theory: 6 Hours						Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Setup Level detector | Trainee will be able to - Follow the handling precaution as per provided specification of Level Detector - Input the required parameters. - Demonstrate the operating Procedure of Level Detector. | - Describe Industrial control circuits. - Define Level Detectors. - Read the data sheet of given level detector PRACTICAL ACTIVITY: Install the level detector and power up the detector. | Total – 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Water tank - Relay - DC power supply - Multimeter - Tool set | Laboratory/ Workshop/ Classroom |
| - Introduction of level detector | Trainee will be able to - Demonstrate the various types of Analog / Digital Level Detector. - Identify the Input / Output power of Level Detector. - Differentiate between Analog / Digital Signals of Level Detectors. - Identify the I/O Signal Pins. | - Explain various types of level detector with pin configuration. PRACTICAL ACTIVITY: Use digital level detector to detect the higher level of water tank. | Total – 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Water tank - Relay - DC power supply - Multimeter - Tool set | Laboratory/ Workshop/ Classroom |
| - Installation of Level Detector | Trainee will be able to - Provide connection of Input / Output power. - Provide the connections of Motor. - Connect the level detector with relay. - Verify the connections with multimeter. - Power On the supply. - Check the response of Level Detector by On / Off motor. | - Explain installation of various types of level detector. - Describe the function of level detector. PRACTICAL ACTIVITY: Use digital level detector to detect the water level in the tank | Total – 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Water tank - Relay - DC power supply - Multimeter - Tool set | Laboratory/ Workshop/ Classroom |

## @@0714E&A127:  Operate Digital Weighing Scale

Objective: This module covers the specific skills and knowledge related to operate Digital controller in various automation applications in our surrounding which is used and see every time in our daily life.

Duration: 24 Hours							Theory: 06 Hours					Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Setup weighing scale | Trainee will be able to - Follow the handling precaution as per provided specification of Weighing Scale. - Input the required parameters. - Demonstrate the operating Procedure of Weighing Scale. | - Define the data sheet of given Digital Weighing Scale - Explain the connection diagram of Digital Weighing Scale PRACTICAL ACTIVITY: Install the setup and power up the Digital Weighing Scale. | 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Digital Weighing Scale - DC power supply - Multimeter - Tool set | Laboratory/ Workshop/ Classroom |
| - Introduction of weighing scale | Trainee will be able to - Demonstrate the various types of Analog / Digital Weighing Scale. - Identify the Input / Output power of Weighing Scale. - Differentiate between Analog / Digital Signals of Weighing Scale. - Identify the I/O Signal Pins of Weighing Scale. | - Describe main components used in Digital Weighing Scale - Describe Load Cells. - Define Analog / Digital measurements. PRACTICAL ACTIVITY: Set the desired weight settings according to weighting the product. | 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Digital Weighing Scale - DC power supply - Multimeter - Tool set | Laboratory/ Workshop/ Classroom |
| - Installation of Load cell | Trainee will be able to - Provide connection of Input / Output power. - Provide the connections of Load Cell. - Connect Amplifier with Load cell. - Connect the Load Cell output with relay. - Verify the connections with multimeter. - Power On the supply. - Check the response of Weighing Scale by applying load in top of weighing scale. | - Describe the function of Digital Weighing Scale - Describe the function of Load Cell. PRACTICAL ACTIVITY: Place the sample product in the Digital Weighing Scale and show the results. | Total – 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Digital Weighing Scale - DC power supply - Multimeter - Tool set | Laboratory/ Workshop/ Classroom |

## 0714E&A128:  Operate Temperature Controller

Objective: This module covers the specific skills and knowledge related to operate temperature controller in various automation applications in our surrounding which is used and see every time in our daily life.

Duration: 24 Hours							Theory: 6 Hours						Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Introduction of Temperature Controller | Trainee will be able to - Follow the handling precaution as per provided specification of Temperature Controller. - Input the required parameters. - Setup the Temperature Controller. - Identify the Output controlling Method through SSR or Relays. - Demonstrate the PID and Hysterisis methods of Controller. | - Describe main components used in Temperature controller. - Read the data sheet of given Temperature controller PRACTICAL ACTIVITY: Identify given type of temperature controller | Total – 06 Hrs Theory – 02 Hrs Practical – 04 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Temperature Controller - DC power supply - Multimeter - Tool set - Lamp - Fan | Laboratory/ Workshop/ Classroom |
| - Setup the Temperature Controller. | Trainee will be able to. - Demonstrate the various types of Temperature Controller - Identify the Input / Output power of Temperature Controller - Differentiate between Analog/Digital Signals Temperature Controller - Identify the I/O Signal Pins of Temperature Controller. - Setup the Parameters of Temperature Controller for PID and Hysterisis. - Provide Connections of Temperature Controller with SSR and Relay separately. - Verify the connections with multimeter. | - Define Analog / Digital Signals. - Describe the function of Temperature Controller. - Explain the connection diagram of Temperature controller PRACTICAL ACTIVITY: Control the temperature of the desired portion by using temperature controller | Total – 08 Hrs Theory – 02 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Temperature Controller - DC power supply - Multimeter - Tool set - Lamp - Fan | Laboratory/ Workshop/ Classroom |

## 0714E&A129:  Operate Pressure Controller

Objective: This module covers the specific skills and knowledge related to operate pressure controller in various automation applications in our surrounding which is used and see every time in our daily life.

Duration: 24 Hours						Theory: 06 Hours					Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Setup pressure Controllers. | Trainee will be able to - Follow the handling precaution as per provided specification of pressure controller. - Input the required parameters. - Setup the Pressure Controller. - Install Digital / Analog Pressure Controller. | - Describe main components used in pressure controller. - Read the data sheet of given pressure controller PRACTICAL ACTIVITY: - Perform the setup value on Pressure Controller. - Identify different types of Pressure Controller. - Perform calculations or scaling the values on Pressure Controller. | Total – 12 Hrs Theory – 03 Hrs Practical – 09 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Pressure Controller - DC power supply - Multimeter - Tool set - Pump - Valve | Laboratory/ Workshop/ Classroom |
| - Connections of Pressure controllers. | Trainee will be able to - Provide connection of Input / Output power. - Provide the connections of Air / Oil Pressure - Connect Amplifier with Pressure Controller. - Connect the Pressure Controller output with relay. - Verify the connections with multimeter. - Power On the supply. - Check the response of Pressure Controller.by applying pressure. | - Define Pressure controllers. - Define type of Pressure Transmitter and Pressure Controller. - Explain the connection diagram of pressure controller PRACTICAL ACTIVITY: Control the pressure of the cylinder by using pressure controller | Total – 12 Hrs Theory – 03 Hrs Practical – 09 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Pressure Controller - DC power supply - Multimeter - Tool set - Pump - Valve | Laboratory/ Workshop/ Classroom |

# X-Building Automation System Supervisor

## 0714E&A130:  Designing of Building Automation System

Objective: This competency standard covers the skills and knowledge related to design & automates building management system used to control buildings heating, ventilation and air conditioning (HVAC) system, control indoor and outdoor lighting, security system, plumbing and fire alarms.

Duration: 33 Hours						Theory: 06 Hours					Practical: 27 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Requirement of Building automation System (BAS) | Trainee will be able to - Assess requirements of building system. - Identify building automation system available in market (e.g. Johnson Control, Honeywell and Schneider) - Identify sensors and actuators. - List down the integration requirement of building system among each other. - Collect information for operator station screen (HMI) | - Define Building Automation System - Describe operation of sensor - Describe operation of actuators PRACTICAL ACTIVITY: - Identify the requirements of I/O’s - Identify the power requirements | Total – 11 Hrs Theory – 02 Hrs Practical – 09 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Sensors - Actuators - Building automation System (BAS) - AC Supply - DC power supply - Multimeter - Tool set | Laboratory/ Workshop/ Classroom |
| - Designing of BAS | Trainee will be able to - Identify Inputs (Digital & Analog) and Outputs (Digital & Analog). - Identify processing data, communication protocols and their requirement. - Quantify the requirement of Controllers, Input and Output Modules - Develop control circuit drawing and layout. | - Define function of Controllers - Define Communication protocols - Define Human Machine Interface (HMI) PRACTICAL ACTIVITY: Perform, Installation of sensors and actuators | Total – 11 Hrs Theory – 02 Hrs Practical – 09 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Sensors - Actuators - Building automation System (BAS) - AC Supply - DC power supply - Multimeter - Tool set - Wire | Laboratory/ Workshop/ Classroom |
| - Installation and Configuration of BAS components | Trainee will be able to - Mounting and connection of all sensors and actuators - Calibration of sensors and actuators - Installation of Controllers and I/O Modules - Downloading of Program in Controllers. - Addressing of Input and Output Modules - Functional testing of connected sensors and actuators | - Describe calibration of sensors and actuators PRACTICAL ACTIVITY: Make the code according to requirements and download in the controller | Total – 11 Hrs Theory – 02 Hrs Practical – 09 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Sensors - Actuators - Building automation System (BAS) - AC Supply - DC power supply - Multimeter - Tool set - Wire | Laboratory/ Workshop/ Classroom |

## @@0714E&A131:  Perform Security Automation

Objective: This competency standard covers the skills and knowledge related to install & maintain security system such as fire alarms, CCTV Cameras and Access Control.

Duration: 27 Hours						Theory: 9 Hours					Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Installation of Fire Alarms | Trainee will be able to - Design layout for alarm zones - Select the sensing devices (Smoke, Heat Detectors, Manual Pull Station) as per requirement - Select fire notifying appliances (Buzzers, Bells, Horn, Strobes) as per requirement - Install sensing and alarm notifying devices - Connect fire alarm control with sensing devices and notifying devices - Check performance of sensing and notifying devices - Perform maintenance of faulty components of fire alarm system | - Describe different types of fire sensing device and alarms - Describe Function of Smoke detector - Describe Function of heat detector - Describe Function of Buzzer PRACTICAL ACTIVITY: Perform, Installation/replacement of fire alarms and its components | Total – 09 Hrs Theory – 03 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Fire Alarm - Smoke detector - Buzzer - AC Supply - DC power supply - Multimeter - Tool set - Wire | Laboratory/ Workshop/ Classroom |
| - Installation of Closed-circuit television (CCTV) Camera | Trainee will be able to - Selection of CCTV camera - Mount camera as per surveillance requirement - Set up Digital Video Recorder (DVR) and monitor - Connect cable from camera to DVR unit - Power up the system and set user interface - Test the performance of camera - Perform Maintenance of faulty components | - Describe working of CCTV camera - Describe components of CCTV camera - Describe types of CCTV camera PRACTICAL ACTIVITY: Perform Installation of CCTV cameras and record the video. | Total – 09 Hrs Theory – 03 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - CCTV Camera - DC power supply - Multimeter - Tool set - Wire | Laboratory/ Workshop/ Classroom |
| - Install Access Control System | Trainee will be able to - Install fingerprint reader - Plug your fingerprint scanner into your machine - Install fingerprint reader software. - Register a fingerprint with the software by pressing your finger against the scanner. - Test the fingerprint scanner. | - Describe building evacuation process - Describe working of Biometric system PRACTICAL ACTIVITY: Save 3 samples of fingerprint with the software by placing your finger against the scanner. | Total – 09 Hrs Theory – 03 Hrs Practical – 06 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Fingerprint scanner - AC Supply - DC power supply - Multimeter - Tool set - Wire | Laboratory/ Workshop/ Classroom |

## 0714E&A132:  Perform Energy management and Monitoring

Objective: This competency standard covers the skills and knowledge related to install monitor and maintain building power and lighting systems.

Duration: 28 Hours						Theory: 10 Hours					Practical: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Electrical Power Monitoring | Trainee will be able to - Operation of standby generator, in case of malfunction in main supply - Check load distribution of stand by generators - Inspect stand-by battery supply and operation - Monitoring of power consumption and backup power - Monitor power factor correction capacitor bank - Check operation of Main switch/switchboard and outgoing circuits with sub-main switches. - Check operations of C.T (current transformer) - Inspect performance of Automatic Changeover Switch - Check all protective devices are functioned properly. - Ensure Protective relays have been correctly set and overcurrent protective devices suitably set for all circuits. - Ensure Distribution boards securely mounted on suitable supports. - Check indicator and alarm functions. - Check wiring for emergency lightings - Ensure fire services installation segregated from other wirings. | - Define types and function of protective devices - Describe working of CT - Describe operation of switchboard - Define working Automatic Changeover Switch - Define general guidelines of generators - Define power factor PRACTICAL ACTIVITY: Perform, Check/replace electrical protective equipment | Total – 14 Hrs Theory – 05 Hrs Practical – 09Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - DC power supply - Multimeter - Tool set - Battery 30A/50A - Current Transformer - Circuit Breaker - Fuses - Switch board - Power Meter - Relays - Contactor - DB - Alarm - Wire - UPS Min 1kva - Generator Min 1 kva - Automatic Changeover Switch - Tester | Laboratory/ Workshop/ Classroom |
| - Light Control System | Trainee will be able to - Design floor wise layout of lighting system - Perform Load Calculation of all facilities. - Selection of wire/ cable according to calculated load. - Selection of protection components (Breaker, fuse) according to calculated load. - Selecting Appropriate Lighting Controls according to designated area - Installation of lighting equipment - Perform maintenance of faulty components. - Ensure proper wiring routes in DBs (Distribution Board) - Ensure Timer switch operated lighting control system can properly installed and operate as commissioned. - Ensure motion sensors are properly installed and operate as commissioned. - Ensure All lamps are the correct wattage and voltage ratings - Interface lighting system with building management system (BMS), or central control and monitoring system (CCMS) - Monitor lighting system through central control system - Evaluate and maintain Lux | - Describe working Timer switch operated lighting - Define working smart sensors. - Describe operation of motion sensor - Describe operation of Timer switch sensor - Explain operation of proximity sensor PRACTICAL ACTIVITY: Perform, troubleshoot fault in wiring and lighting system | Total – 14 Hrs Theory – 05 Hrs Practical – 09Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - DC power supply - Multimeter - Tool set - Circuit Breaker - Fuses - Switch board - Power Meter - Relays - Contactor - DBS - Alarm - Wire - Automatic Changeover Switch - Tester - Motion sensor - Proximity sensor - Building Management System (BMS) | Laboratory/ Workshop/ Classroom |

## 0714E&A133:  Perform HVAC inspection & Maintenance

Objective: This competency standard covers the skills and knowledge related to Inspection and Maintenance of HVAC Systems for Energy Efficiency operation. The competency is relevant to typical Heating Ventilation and Air Conditioning (HVAC) Systems that are installed in commercial office type buildings.

Duration: 36 Hours						Theory: 09 Hours					Practical: 27 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Air Conditioning Inspection | Trainee will be able to - Check the refrigerant charge including suction line pressure and liquid Line pressure - Check refrigerant leakages - Inspect the suction line insulation - Check electrical wiring, line voltages and components (Motor, breakers, contactors, capacitors, relays and switches) - Test the pressure switches - Blow out the drain line - Remove leaves and debris - Rinse the condenser coils - Check the drain for proper fall - Proper float switch operation - Check the secondary drain pan - Inspect the evaporator coil - Look at the return air filter - Check function of thermostat - Inspect the duct system | - Define Building Management System - Describe function of components used in HVAC - Describe working of HVAC (Heating, ventilation, and air conditioning) - Describe working of Air condition - Describe types of Pump PRACTICAL ACTIVITY: - Perform, Inspect/replace thermostat in HVAC - Perform, Inspect/replace evaporator coil - Perform, Inspect/replace air filter | Total – 12 Hrs Theory – 03 Hrs Practical – 09 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - HVAC Trainer - AC Supply - DC power supply - Multimeter - Tool set - Wire - Blower - Relay - Contactor - Pressure Switch - Capacitors - condenser coils - air filter - thermostat - Pumps - Valves | Laboratory/ Workshop/ Classroom |
| - Gas burner Inspection | Trainee will be able to - Clean / check the gas burners - Check / clean the pilot tube - Check the igniter for proper resistance and function - Clean the flame sensor - Check the blower motor amps and speed - Evaluate the temperature rise - Inspect the heat exchangers - Check for proper combustion - Clean out and inspect the pressure switch tubing - Evaluate the pressure switch operations - Test all of the limit and roll out switches - Inspect the gas pipe plumbing - Set manifold gas pressures - Check the gas input rate - Light the pilot and check the thermocouple - Check the pilot safety thermocouple (electronic ignition) - Check all of the electrical wiring and components - Set the heat anticipator on the thermostat - Make sure that there are no code violations - Check the safety interlock switch - Test the combustion fan motor and check amps - Make sure that there is proper combustion air - Inspect the duct system - Perform a carbon monoxide test | - Describe function of components used in HVAC - Describe working of HVAC (Heating, ventilation, and air conditioning) - Describe types of Gas burner - Describe different types of fire sensing device and alarms PRACTICAL ACTIVITY: - Perform, Inspect/replace thermostat in HVAC - Perform, Inspect/replace pressure switch - Perform, Inspect/replace combustion fan motor | Total – 12 Hrs Theory – 03 Hrs Practical – 09 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - HVAC Trainer - AC Supply - DC power supply - Multimeter - Tool set - Wire - Blower - Relay - Contactor - Pressure Switch - Thermocouple - air filter - thermostat - Pumps - Valves - Safety interlock switch | Laboratory/ Workshop/ Classroom |
| - Heating Coil Inspection | Trainee will be able to - Check the temperature rise across the coil - Inspect the coils for cleanliness, leaks, or deficiencies - Test the defrost cycle - Make sure the reversing valve is working properly - Test the auxiliary heat staging - Check the emergency heat operation - Test and inspect the thermostat operation - Check electrical wiring, line voltages and components (Motor, breakers, contactors, capacitors, relays and switches) - Perform a visual check for refrigerant leaks - Analyze the air flow and make adjustments - Check the filtration system - Insure proper return air sizing - Insure proper insulation on the refrigeration lines - Set the proper defrost timer cycle - Test the pressure switches - Check the duct system | - Describe working of HVAC (Heating, ventilation, and air conditioning) - Explain Heating circuit PRACTICAL ACTIVITY: - Perform; inspect the components of heating section - Perform; inspect the air flow - Perform; inspect the thermostat | Total – 12 Hrs Theory – 03 Hrs Practical – 09 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - HVAC Trainer - AC Supply - DC power supply - Multimeter - Tool set - Wire - Blower - Relay - Contactor - Breaker - Pressure Switch - Thermocouple - air filter - thermostat - Pumps - Valves | Laboratory/ Workshop/ Classroom |

## 0714E&A134:  Perform Elevator Maintenance

Objective: This competency standard covers the skills and knowledge related to inspect and perform maintenance of elevator and lift systems.

Duration: 28 Hours						Theory: 09 Hours					Practical: 27 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Elevator Car | Trainee will be able to - Check power supply, electric wiring, electric /electronic components using Multimeter. - Check the interior of the car for damage, including ceiling, handrails and walls. - Replace any burned out bulbs, from the position indicator lights to ceiling lighting. - Check the acceleration, deceleration and leveling accuracy of the car as it travels up and down. - Confirm the doors move smoothly without slamming or bouncing when they are fully open and closed. - Ensure door restrictor operates correctly. - Check the exterior of the car and replace any burned out bulbs - Examine the door clearances and panel. - Test the smoke alarm and fire service system. | - Define acceleration, deceleration and leveling accuracy of the car - Describe Mechanical structure of Car - Define types of elevators. PRACTICAL ACTIVITY: Perform; inspect the electrical and electronic components in the elevator system. | Total – 12 Hrs Theory – 03 Hrs Practical – 09 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Relay - Contactor - DC power supply - Multimeter - Tool set - Lamps - Wire - Clamp meter - Fire alarm - Smoke Alarm - Door Sensor - Elevator Door motor - Drill Machine - Screwdriver set - LN keys - Drill Machine - Ring Spanner set - Fixed spanner set - Plier set - Long handle - Short handle | Laboratory/ Workshop/ Classroom |
| - Perform Elevator Cabling System | Trainee will be able to - Ensure the stop switch and inspection station at the top of the car work properly. - Examine guide rails, leveling mechanisms and rollers. - Check the cables for signs of wear. - Inspect the hoist way for signs of fire safety issues, rodents or vandalism. - Ensure sump pump is working correctly. - Check & replace noisy bearings or bearing malfunction - Inspect & repair Misaligned motor drive - Inspect & repair Worn Sheaves | - Describe Mechanical structure of Cabling system of elevator - Describe function of rollers - Describe function of Bearings related to elevator car - Describe function of Sheaves PRACTICAL ACTIVITY: Perform; inspect the mechanical parts in the elevator system. | Total – 12 Hrs Theory – 03 Hrs Practical – 09 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Relay - Contactor - DC power supply - Multimeter - Tool set - Elevator Motor Drives Trainer - Lamps - Shieling Wire - guide rails - leveling mechanisms for Elevator car - rollers - Switch button - Bearings related to elevator car - Sheaves - Screwdriver set - LN keys - Drill Machine - Ring Spanner set - Fixed spanner set - Plier set - Long handle - Short handle | Laboratory/ Workshop/ Classroom |
| - Perform Elevator Machine Room | Trainee will be able to - Remove any items that are unrelated to the upkeep and maintenance of the elevator system. - Check oil levels. - Examine electrical components for indications of failure. - Lubricate appropriate components. - Schedule a service appointment if needed. - Check and calibrate braking system - Check sling wire of the elevator | - Describe Elevator Motors. - Describe Elevator Motor Drivers. - Define Motor Gear Systems - Define Sling wire standards PRACTICAL ACTIVITY: Perform; inspect the electrical and electronic components in the elevator system. | Total – 12 Hrs Theory – 03 Hrs Practical – 09 Hrs | - Stationaries - PPE - Projector - White Board - Board Marker - Desktop Computer - Computer Table - Workbench - Machine oil - DC power supply - Multimeter - Tool set - Screwdriver set - LN keys - Drill Machine - Ring Spanner set - Fixed spanner set - Plier set - Long handle - Short handle - Elevator Motor drives trainer | Laboratory/ Workshop/ Classroom |

# Entrepreneurship

## Module: Develop Entrepreneurial Skills

Objective:

After the completion of this competency standard, the Trainee will be expected to develop a business plan, collect information regarding funding sources, develop a marketing plan and develop basic business communication skills. Trainee’ss underpinning knowledge regarding entrepreneurial skills will be sufficient to provide you the basis for your work.

Duration:  30 Hours			Theory:  12 Hours			Practice:  18 Hours          	        Credit Hours:

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Develop a business plan | Trainee will be able to: - Conduct a market survey to collect following information: - Customer /demand - Tools, equipment, machinery and furniture with rates - Raw material - Supplier - Credit / funding sources - Marketing strategy - Market trends - Overall expenses - Profit margin - Select the best option in terms of cost, service, quality, sales, profit margin, overall expenses - Compile the information collected through the market survey, in the business plan format | - Main elements of business plan - Filling the business plan format - Enlist specific business terms used in the industry - Describe 7Cs of business communication | Theory- 03 Hr Practical- 03Hrs Total- 06 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Collect information regarding funding sources | Trainee will be able to: - Identify the available funding sources based on their terms and conditions, maximum loan limit, payback time, interest rate - Choose the best available option according to investment requirement - Prepare documents according to the loan agreement requirement - Include the information of funding sources in the business plan | - Enlist the available funding sources - Explain how to get loan to start a new business - Explain market survey and its tools e.g.: questionnaire, interview, observation etc | Theory Theory- 03 Hr Practical- 03Hrs Total- 06 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Develop a marketing plan | Trainee will be able to: - Make a marketing plan for the business including product, price, placement, promotion, people, packaging and positioning - Include the information of marketing plan in the business plan | - 7ps of marketing including product, price, placement, promotion, people, packaging and positioning | Theory- 03 Hr Practical- 03Hrs Total- 06 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Develop basic business communication skills | Trainee will be able to: - Communicate with internal customers e.g.: labor, partners and external customers e.g.: suppliers, customers etc., using effective communication skills - Use different modes of communication to communicate internally and externally e.g.: presentation, speaking, writing, listening, visual representation, reading etc. - Use specific business terms used in the market | - Description of the market trends for specific product offering - Different modes of communication and their application in the industry | Theory- 03 Hr Practical- 09Hrs Total- 12 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Module: Apply management and communications techniques

Objective:

After the completion of this competency standard, the Trainee will be able to contribute to communications planning, Conduct information management activities, Communicate project information, Contribute to assessing effectiveness of communication.

Duration:  30 Hours		Theory:  12Hours			Practice:  18 Hours          	        Credit Hours:

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Contribute to communications planning | Trainee will be able to: - Identify, source and contribute relevant information requirements to initial project documentation. - Contribute to developing and implementing the project communications plan and communications networks. | - Outline methods of reviewing communication outcomes | Theory- 03 Hr Practical- 03Hrs Total- 06 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Conduct information management activities | Trainee will be able to: - Act on and process project information according to agreed procedures as directed, to aid decision-making processes throughout project life cycle. - Maintain information to ensure data is secure and auditable. | - Summarize models and methods of communications management in context of project life cycle and other project management functions | Theory- 03 Hr Practical- 03Hrs Total- 06 Hr Min | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Communicate project information | Trainee will be able to: - Communicate with clients and other stakeholders during project using agreed networks, processes and procedures to ensure flow of necessary information. - Ensure reports are prepared and released according to authorization, or produced for release by others. - Seek information and advice from appropriate project authorities as required. | - Identification of Project Information, policies and procedures relevant - Summarize models and methods of communications management in context of project life cycle and other project management functions | Theory- 03 Hr Practical- 03Hrs Total- 06 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Contribute to assessing effectiveness of communication | Trainee will be able to: - Assist in ongoing review of project outcomes to determine effectiveness of communications-management activities. - Report communications-management issues and responses to higher project authorities for application of lessons learned to future projects. | - Assessment of effectiveness of project communication | Theory- 03 Hr Practical- 09Hrs Total- 12 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Module: Create Human Resources Management Plan

Objective:

After the completion of this competency standard, the Trainee will be able to develop a plan for a telecommunications project, including assessing project requirements and planning for all stages to completion and final documentation. It applies to individuals who are likely to have responsibility for the provision of installations, maintenance, upgrades and new services.

Duration:  30 Hours		Theory:  12 Hours			Practice:  18 Hours          	        Credit Hours:

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare project management plan | Trainee will be able to: - Evaluate and assess project brief and related documents. - Produce document on project tasks and associated timelines, including installation processes and test requirements. - Assess and produce document on resource requirements to assist allocation of appropriate resources. - Produce training plan assessing training needs and associated timelines for efficient project implementation. - Determine and document budgetary requirements. - Discuss roles of all identified parties associated with project to ensure their involvement. - Produce project verification document, including monitoring and control processes, and review processes such as quality audits. - Consult with all relevant parties prior to finalizing draft plan and make changes as appropriate. | - Preparation of Project Plans and their management - Evaluation and assessment of project related documentation and tasks - Project Budget preparation | Theory- 03 Hr Practical- 03Hrs Total- 06 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Develop and evaluate management plan | Trainee will be able to: - Produce preliminary plan for consultation, including identified factors that may impact on realization of project and observance of relevant legislation, codes, regulation and standards. - Consult with client and clarify any amendments. - Develop final plan with recommendations. | - Development and evaluation of project management plans - Client dealing for clarification and amendments in project plans - Finalization of plans | Theory- 03 Hr Practical- 03Hrs Total- 06 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Communicate project information | Trainee will be able to: - Produce and document final plan to include implementation details and training needs. - Present plan to client and obtain sign off. | - Presentation of Project plan to client | Theory- 03 Hr Practical- 03Hrs Total- 06 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Contribute to assessing effectiveness of communication | Trainee will be able to: - Assist in ongoing review of project outcomes to determine effectiveness of communications-management activities. - Report communications-management issues and responses to higher project authorities for application of lessons learned to future projects. | - Review of project outcomes and asses effectiveness of business communication | Theory- 03 Hr Practical- 09Hrs Total- 12 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Module: Plan And Implement Business-To-Business Marketing

Objective:

After the completion of this competency standard, the Trainee will be able to plan and implement business-to-business (B2B)
marketing. It applies to individuals who work in a supervisory capacity in a team environment, who possess a sound theoretical knowledge base and demonstrate a range of managerial skills to ensure business activities are conducted effectively. In this role, individuals may work in small, medium or large enterprises across a variety of industries.

Duration:  30 Hours		Theory:  12 Hours			Practice:  18 Hours          	        Credit Hours:

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify and evaluate business -to-business marketing strategies | Trainee will be able to: - Identify B2B markets in an industry context - Research characteristics of business markets in an industry context - Identify and analyze factors influencing business buyers in an industry context - Analyze the business buying process and its implications in the industry context - Research and analyze a range of B2B marketing strategies appropriate for the organization - Identify key personnel in buying decision process in the organization s business markets | - Identification of Business to Business markets | Theory- 03 Hr Practical- 03Hrs Total- 06 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Select business-to business marketing strategies | Trainee will be able to: - Analyze trends within business markets and identify B2B marketing opportunities for the organization - Identify and analyze success of the organization s previous B2B marketing strategies - Select most appropriate B2B marketing strategies and activities that fit with organization s strategic & marketing plans | - Preparation of business to business strategies | Theory- 03 Hr Practical- 03Hrs Total- 06 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Plan and develop business-to-business marketing activities | Trainee will be able to: - Record B2B marketing objectives and purpose - Calculate costs of B2B marketing activities with assistance of appropriate personnel - Select methods to report and measure effectiveness of B2B marketing activities - Assign responsibilities to team members for B2B marketing activities - Record B2B marketing plan and present to relevant stakeholders - Assemble required resources to implement B2B marketing plan | - Plan the business to business strategies | Theory- 03 Hr Practical- 03Hrs Total- 06 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Implement and monitor business-to business marketing plan | Trainee will be able to: - Schedule work on each B2B marketing campaign element, according to lead times required and marketing plan - Brief staff and suppliers on their budgets, timelines, roles and responsibilities, and legal and ethical requirements - Plan implementation of B2B marketing activities according to marketing plan - Identify & use evaluation criteria and evaluation methods to determine effectiveness of marketing plan - Analyze success indictors of B2B marketing plan and record performance according to organizational reporting requirements | - Trends in B2B marketing, corporate sector and business sector and preparation of plans | Theory- 03 Hrs Practical- 09Hrs Total- 12 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Module: Manage  Finances

Objective:

After the completion of this competency standard, the Trainee will be able to develop, implement and monitor a personal
budget in order to plan regular savings and manage debt effectively.

Duration:  30 Hours		Theory:  12 Hours			Practice:  18 Hours          	        Credit Hours: 0.5

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Develop a personal budget | Trainee will be able to: - Calculate current living expenses using available information to prepare a personal budget. - Keep a record of all income and expenses for a short period of time to help estimate ongoing expenses. - Subtract total expenses from total income to determine a surplus or deficit budget for the specified period. - Find reasons for a deficit budget and ways to reduce expenditure identified. - Identify ways to increase income, if possible | - Preparing cash flow statement - Basic concepts of Time value of money - Understanding of current and fixed assets - Understanding of elements of equity and liabilities (long term and short term) - Identification of available financial resources - Step by step budget plan preparation - Budget review techniques | Theory- 4 Hrs Practical- 06Hrs Total- 10 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Develop longer term personal budget | Trainee will be able to: - Analyze income and expenditure and set longer term personal, work and financial goals. - Develop a longer-term budget based on the outcomes of short-term budgeting, and adjust to meet living, work and future career requirements. - Identify obstacles that might affect finances such as job loss, sickness or unexpected expenses contingency savings - Formulate a regular savings plan based on budget, using secure savings products and services. - Monitor expenditure against budget and identify areas of possible expenditure saving | - Develop a personal budget based on analysis of expenditure and income - Monitor expenditure for a period of up to 2 weeks. | Theory- 4 Hrs Practical- 06Hrs Total- 10 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Identify ways to maximize future finances | Trainee will be able to: - Determine sources and ways to maximize personal income, including from work, investments or available government payments/allowances. - Get further education or training to maintain or improve future income. - Identify the need for debt to finance living and other expenses, and determine the appropriate levels of debt and repayment. - Consolidate existing debt, where possible, to minimize interest costs and fees. - Seek professional money management services, where available, to ensure financial plans are effective and achievable | - Formulate goals and identify financial contingency plans | Theory- 4 Hrs Practical- 06Hrs Total- 10 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Module: Develop A Project Management Plan

Objective:

After the completion of this competency standard, the Trainee will be able to develop a plan for a telecommunications project, including assessing project requirements and planning for all stages to completion and final documentation. It applies to individuals who are likely to have responsibility for the provision of installations, maintenance, upgrades and new services.

Duration:  41 Hours		Theory:  20 Hours			Practice:  21 Hours          	        Credit Hours: 4.1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare project management plan | Trainee will be able to: - Evaluate and assess project brief and related documents. - Produce document on project tasks and associated timelines, including installation processes and test requirements. - Assess and produce document on resource requirements to assist allocation of appropriate resources. - Produce training plan assessing training needs and associated timelines for efficient project implementation. - Determine and document budgetary requirements. - Discuss roles of all identified parties associated with project to ensure their involvement. - Produce project verification document, including monitoring and control processes, and review processes such as quality audits. - Consult with all relevant parties prior to finalizing draft plan and make changes as appropriate. | - Preparation of Project Plans and their management - Evaluation and assessment of project related documentation and tasks - Project Budget preparation | Theory- 05 Hrs Practical- 06Hrs Total- 11 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Develop and evaluate management plan | Trainee will be able to: - Produce preliminary plan for consultation, including identified factors that may impact on realization of project and observance of relevant legislation, codes, regulation and standards. - Consult with client and clarify any amendments. - Develop final plan with recommendations. | - Development and evaluation of project management plans - Client dealing for clarification and amendments in project plans - Finalization of plans | Theory- 05 Hrs Practical- 06Hrs Total- 11 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Communicate project information | Trainee will be able to: - Produce and document final plan to include implementation details and training needs. - Present plan to client and obtain sign off. | - Presentation of Project plan to client | Theory- 05 Hrs Practical- 06Hrs Total- 11 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Contribute to assessing effectiveness of communication | Trainee will be able to: - Assist in ongoing review of project outcomes to determine effectiveness of communications-management activities. - Report communications-management issues and responses to higher project authorities for application of lessons learned to future projects. | - Review of project outcomes and asses effectiveness of business communication | Theory- 05 Hrs Practical- 03Hrs Total- 08 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Module: Develop A Sales Plan

Objective:

After the completion of this competency standard, the Trainee will be able to develop a sales plan for a product or service for a team covering a specified sales territory based on strategic objectives and in accordance with established performance targets. It applies to individuals working in a supervisory or managerial sales role who develop a sales plan for a product or service.

Duration:  30 Hours		Theory:  12 Hours			Practice: 18 Hours          	        Credit Hours:

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify organizational strategic direction | Trainee will be able to: - Obtain and analyze assessment of market needs and strategic planning documents - Review previous sales performance and successful approaches to identify factors affecting performance - Analyze information on market needs, new opportunities, customer profiles and requirements as a basis for decision making | - Assessment of market needs and strategic planning documents preparation - Knowledge of business opportunities, customer profiles and decision making | Theory- 02 Hrs Practical- 3Hrs Total- 05 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Establish performance targets | Trainee will be able to: - Determine practical and achievable sales targets - Establish realistic time lines for achieving targets - Determine measures to allow for monitoring of performance - Ensure objectives of the sales plan and style of the campaign are consistent with organizational strategic objectives and corporate image | - Statistical techniques for analyzing sales and market trends | Theory- 02 Hrs Practical- 3Hrs Total- 05 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Develop a sales plan for a product | Trainee will be able to: - Determine approaches to be used to meet sales objectives - Identify additional expertise requirements and allocate budgetary resources accordingly - Identify risks and develop risk controls - Develop advertising and promotional strategy for product - Identify appropriate distribution channels for product - Prepare a budget for the sales plan - Present documented sales plan to appropriate personnel for approval | - Principles and techniques for selling Sources of internal and external information - Identification of organizational strategic direction and developing a product sales plan - Preparation of sales plan and its approval | Theory- 02 Hrs Practical- 3Hrs Total- 05 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Identify support requirements | Trainee will be able to: - Identify and acquire staff resources to implement sales plan - Develop an appropriate selling approach - Train staff in the selling approach selected - Develop and assess staff knowledge of product to be sold | - Resources requirement for sales plan | Theory- 02 Hrs Practical- 3Hrs Total- 05 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU5. Monitor and review sales plan | Trainee will be able to: - Monitor implementation of the sales plan - Record data measuring performance versus sales targets - Make adjustments to sales plan as required to ensure required results are obtained | - Principles, monitoring and techniques for selling Sources of internal and external information | Theory- 04 Hrs Practical- 06Hrs Total- 10 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Module: Conduct research for Customer Needs & Satisfaction

Objective:

After the completion of this competency standard, the Trainee will be able to manage an ongoing relationship with a customer
over a period of time. This includes helping customers articulate their needs and managing networks to ensure customer needs are addressed. It applies to individuals who are expected to have detailed product knowledge in order to recommend customized solutions. In this role, individuals would be expected to apply organizational procedures and be aware of, and apply as appropriate, broader factors involving ethics, industry practice and relevant government policies and regulations.

Duration:  30 Hours		Theory:  12Hours			Practice:  18Hours          	        Credit Hours:

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Assist customer to articulate needs | Trainee will be able to: - Ensure customer needs are fully explored, understood and agreed - Explain and match available services and products to customer needs - Identify and communicate rights and responsibilities of customers to the customer as appropriate | - Explain organizational procedures and standards for establishing and maintaining customer service relationships. - Explain consumer rights and responsibilities | Theory- 03 Hrs Practical- 03Hrs Total- 06 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Satisfy complex customer needs | Trainee will be able to: - Explain possibilities for meeting customer needs - Assist customers to evaluate service and/or product options to satisfy their needs - Determine and prioritize preferred actions - Identify potential areas of difficulty in customer service delivery and take appropriate actions in a positive manner | - Describe ways to establish effective regular communication with customers - Variations within a limited product and service range. | Theory- 03 Hrs Practical- 03Hrs Total- 06 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Manage networks to ensure customer needs are addressed | Trainee will be able to: - Establish effective regular communication with customers - Establish, maintain and expand relevant networks to ensure appropriate referral of customers to products and services from within and outside the organization - Ensure procedures are in place to ensure that decisions about targeting of customer services are based on up-to-date information about the customer and the products and services available - Ensure procedures are put in place to ensure that referrals are based on the matching of the assessment of customer needs and availability of products and services - Maintain records of customer interaction in accordance with organizational procedures | - Outline details of products or services including with reference to possible alternative products and services | Theory- 03 Hrs Practical- 03Hrs Total- 06 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Convert customer enquiries into sales | Trainee will be able to: - Use information provided by customers or accessed from customer relationship management (CRM) system to identify any need - Identify suitable products /services to meet needs - Make convincing sales pitches to customers following standard scripts - Handle customer queries, objections and rebuttals following standard scripts - Adapt your approach and style to customer preferences, within limits of your competence and authority - Refer issues outside your area of competence and authority to appropriate people, following your organization’s procedures - Identify and act on opportunities to up-sell or cross-sell other products/services to customers - Confirm customer wishes and needs in order to close sales - Obtain required financial information from customers, following your organization’s procedures - Complete your organization’s post-sales procedures in order to complete/fulfill sales - Comply with relevant standards, policies, procedures and guidelines when converting customer enquiries into sales | - Organizational standards for maintaining customer relationships to convert convincing sales pitches to customers need | Theory- 03 Hrs Practical- 09Hrs Total- 12 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Module: Identify & resolve Problems

Objective: After the completion of this competency standard, the Trainee will be able to apply the process of problem solving for problems beyond those associated directly with the process unit.

Duration:  40 Hours		Theory:  19 Hours			Practice:  21 Hours          	        Credit Hours:  4.0

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Analyze the problem | Trainee will be able to: - Evaluate issues/concerns are evaluated based on data gathered. - Identify possible causes of problem are identified within the area of responsibility as based on experience and the use of problem solving tools/analytical techniques. - Develop possible cause statements based on findings. - Use analogies to support reasoning. - Identify cause and effects are identified based on the criteria or information provided to support reasoning. | - Explain Analytical skills and broad knowledge of diagnostic tools - Explain broad knowledge of the client business domain - Elaborate broad understanding of organizational systems and functions Outline communication skills according to the type of audience - Explain the methods of questioning and active listening employed to clarify general information | Theory- 04 Hrs Practical- 03Hrs Total- 07Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Identify possible solutions | Trainee will be able to: - Consider all possible options for solution of the problem in accordance with safety and operating procedures. - Determine strengths and weaknesses of possible options. - Take corrective action to solve the problem and determine its possible future causes. - Analyze past experience - Provide samples to support generalization. - Implement simulations as needed. | - Describe the ways to develop critical thinking - Explain methods and techniques for decision making within a limited range of options - Describe general customer service skills | Theory Theory- 04 Hrs Practical- 03Hrs Total- 07Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Recommend solution to higher management | Trainee will be able to: - Prepare report or documentation. - Present recommendations to appropriate personnel. - Follow up recommendations, if required. | - Explain the ways to improve teamwork in reference to personal responsibility | Theory- 04 Hrs Practical- 03Hrs Total- 07Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Implement solution | Trainee will be able to: - Identify measurable objectives - Identify resource needs - Prepare timelines in accordance with plan. | - Develop teams and individuals and ask for individual feedback | Theory- 04 Hrs Practical- 06Hrs Total- 10Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU5. Evaluate / monitor results and outcome | Trainee will be able to: - Identify processes and improvements based on evaluative assessment of problem. - Prepare recommendations and submit to superiors | - The evidence should integrate employability skills with workplace tasks and job roles and verify competency is able to be transferred to other situations | Theory- 03 Hrs Practical- 06Hrs Total- 09Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

# List of Tools and Equipment:

(FOR A CLASS OF 25 STUDENTS)

| Sr. # | Description | Quantity |
| --- | --- | --- |
| 1 | Steel-toed footwear, | 25 Nos. |
| 2 | hard hat, | 25 Nos. |
| 3 | safety gloves, | 25 Sets |
| 4 | appropriate safety glasses, | 25 Nos. |
| 5 | high visibility vest, | 25 Nos. |
| 6 | hearing protection, | 25 Nos. |
| 7 | respirators, masks, | 25 Nos. |
| 8 | De-electric boots and gloves for protection from electrical shock. | 25 Nos. |
| 9 | First Aid Box (Include all necessary bandages and medicines) | 02 Sets |
| 10 | fire extinguishers, | 04 Nos. |
| 11 | fire blankets, | 04 Nos. |
| 12 | Sand Bucket with stand | 02 Sets |
| 13 | basic tools, such as grease gun, air pump etc | 10 Sets |
| 14 | Allen Key | 10 Sets |
| 15 | Work Bench (able to hold 06 bench wises) | 05 Nos. |
| 16 | Bench Wise | 30 Nos. |
| 17 | hammer, | 05 each size |
| 18 | screwdrivers, | 05 each size |
| 19 | pliers, | 05 each size |
| 20 | self-locking pliers, | 05 each size |
| 21 | adjustable wrench, | 05 each size |
| 22 | Assorted other wrenches, measuring tape(100m) | 05 each size |
| 23 | Basic supplies, such as grease, oil, window cleaner, rags, ice scraper, whisk broom. | 05 each |
| 24 | Color-code cards, utility documentation. Logbooks Service Manuals, OHS Regulation, | 10 sets |
| 25 | Fix Safe guards | 04 Nos |
| 26 | Moveable Safe guards | 04 N0s. |
| 27 | Solder | 04 N0s. |
| 28 | Wire stripper | 04 N0s. |
| 29 | Nose plier | 04 N0s. |
| 30 | Solder wire | 04 N0s. |
| 31 | Insulation remover | 04 N0s. |
| 32 | Flat File | 25 Nos. |
| 33 | Half round file | 10 Nos. |
| 34 | Round File | 10 Nos. |
| 35 | Mild Steel Sheet (4 x 8 ft) | 02 Nos |
| 36 | Mild Steel round work piece (Dia 30) | 10 ft |
| 37 | Mild Steel flat bar (W:50xL:100xT:20mm) | 25 Nos. |
| 38 | GI pipe 1”, 2” | 20 Feet each |
| 39 | Lathe machine (5 ft) | 02 Nos |
| 40 | Revolving center | 02 Nos |
| 41 | Dead center | 02 Nos |
| 42 | Draw bar | 02 Nos |
| 43 | Face plate | 02 Nos |
| 44 | Knurling Tool | 02 Nos |
| 45 | HSS Tool bit | 10 Nos |
| 46 | Pedestal Drill machine | 02 Nos |
| 47 | Hand Grinder | 02 Nos |
| 48 | Drill bits | 02 Set |
| 49 | Drill shank | 02 Set |
| 50 | Drill chuck | 02 Nos |
| 51 | Counter sink tool | 02 Nos |
| 52 | Counter bore tool | 02 Nos |
| 53 | Machine reamer set | 02 Set |
| 54 | Hand Reamer set | 02 Set |
| 55 | Universal Milling machine | 01 Nos. |
| 56 | Machine wise | 01 Nos. |
| 57 | Tail stock with dead center | 01 Set |
| 58 | Portable welding machine 3 Phase 300 Amps. | 02 Nos, |
| 59 | Welding table | 03 Nos, |
| 60 | Toggle | 02 Nos, |
| 61 | Leather gloves | 01 Nos, |
| 62 | Welding apron | 05 Nos, |
| 63 | Oxygen Cylinder with protector cap | 01 Nos, |
| 64 | Acetylene Cylinder with protector cap | 01 Nos. |
| 65 | Welding Torch | 01 Nos. |
| 66 | Welding Tip (Nozzle) | 01 Set |
| 67 | Pressure Regulators | 01 Nos. |
| 68 | Hose & Hose fittings | 30 ft. |
| 69 | Filler Rod | 01 Box |
| 70 | Flux Material | 500 gm. |
| 71 | Surface Table | 01 Nos. |
| 72 | Surface plate. | 02 Nos. |
| 73 | Steps and collars. | 02 Set |
| 74 | Folding rule | 02 Nos. |
| 75 | Combination set. | 02 Nos. |
| 76 | Scriber. | 02 Nos. |
| 77 | Tri square. | 02 Nos. |
| 78 | Divider. | 02 Nos. |
| 79 | Spirit level | 02 Nos. |
| 80 | Radius gauge | 02 Nos. |
| 81 | Filler gauge | 02 Nos. |
| 82 | Plug gauge | 02 Set |
| 83 | Ring gauge | 02 Set |
| 84 | Outside micrometer | 02 Nos. |
| 85 | Inside micrometer | 02 Nos. |
| 86 | Depth micrometer. | 02 Nos. |
| 87 | Bevel protractor. | 02 Nos. |
| 88 | Vernier Bevel protractor. | 02 Nos. |
| 89 | Dial protractor. | 02 Nos. |
| 90 | Sine bar. | 02 Nos. |
| 91 | Sine block | 02 Nos. |
| 92 | Sine plate. | 02 Nos. |
| 93 | Sine table. | 02 Nos. |
| 94 | Sine center. | 02 Nos. |
| 95 | Gear tooth caliper | 02 Nos. |
| 96 | Gear Inspection machine. | 01 Nos. |
| 97 | Gear testing machine. | 01 Nos. |
| 98 | Parkinson Gear Tester. | 01 Nos. |
| 99 | Multi meters | 02 Nos. |
| 100 | Resistors of different values | 04 Nos. (Each) |
| 101 | Small pieces of copper wire | 01 roll |
| 102 | Small pieces of copper wire | 01 roll |
| 103 | Breadboard. | 04 Nos. |
| 104 | Connecting wires | 02 Rolls |
| 105 | Incandescent lamp of different watts. | 04 Nos. |
| 106 | Voltmeter | 04 Nos. |
| 107 | Ampere meter | 04 Nos. |
| 108 | Multimeter | 04 Nos. |
| 109 | Combination plier | 04 Nos. |
| 110 | Phase tester | 04 Nos. |
| 111 | Energy meter | 04 Nos. |
| 112 | Thin coated copper wire. | 02 Rolls |
| 113 | Dry cell battery | 04 Nos. |
| 114 | Horse shoe magnet. | 04 Nos. |
| 115 | Transformer. | 02 Nos. |
| 116 | Compass needle. | 02 Nos. |
| 117 | Bar Magnet. | 04 Nos. |
| 118 | Galvanometer. | 02 Nos. |
| 119 | Capacitors, 4.7 μF | 04 Nos. |
| 120 | Capacitors, 10, 100 & 8.2 μF. | 04 Nos. (each) |
| 121 | Voltmeter. | 04 Nos. |
| 122 | D.C. power supply unit. | 02 Nos. |
| 123 | Bridging plugs. | 04 Nos. |
| 124 | Connecting leads. | 4 |
| 125 | Multimeter. (With option of Capacitance measurement) | 04 Nos. |
| 126 | D.C. power supply unit | 02 Nos. |
| 127 | Variable D.C powers supply 0-30 Voltas | 2 |
| 128 | Capacitor (Sanyo Operated Volts 6.3 V, SE 30) | 02 Nos. (each) |
| 129 | D.C Analog or Preferably Digital voltmeter Range 0-50V. | 02 Nos. (each) |
| 130 | Digital Multimeter | 04 Nos. |
| 131 | Oscilloscope Diode | 04 Nos. |
| 132 | Wire cutter | 04 Nos. |
| 133 | Wire stripper | 04 Nos. |
| 134 | White chart paper | 100 Nos. |
| 135 | Graphics and drawing sheets | 200 Nos. |
| 136 | Pencil | 30 Nos. |
| 137 | Eraser | 30 Nos. |
| 138 | Sharpener | 30 Nos. |
| 139 | Tee | 25 Nos. |
| 140 | Drawing Board | 25 Nos. |
| 141 | Set Square | 25 Nos. |
| 142 | Geometry set | 25 Nos. |
| 143 | French Curve | 25 Nos. |
| 144 | Printer | 01 Nos. |
| 145 | Multimedia projector | 01 Nos. |
| 146 | Computer | 25 Nos. |
| 147 | CAD software (Multi user) | 1 |
| 148 | IDE Software (C Language) | 1 |
| 149 | Digital clock | 04 Nos. |
| 150 | 555 IC | 2 |
| 151 | Connecting leads. | 02 Rolls |
| 152 | Coil | 02 Rolls |
| 153 | Armature | 02 Nos. |
| 154 | Winding machine | 02 Nos. |
| 155 | Insolating paper | 02 Nos. |
| 156 | Carbon brushes | 04 Nos. |
| 157 | Soldering wire | 02 Rolls |
| 158 | Stator frame | 02 Nos. |
| 159 | Spring balance | 02 Nos. |
| 160 | Ohm meter | 02 Nos. |
| 161 | DC compound motor | 02 Nos. |
| 162 | Electro dynamo meter | 02 Nos. |
| 163 | AC series motor | 02 Nos. |
| 164 | Reluctance motor | 02 Nos. |
| 165 | Hysteresis motor | 02 Nos. |
| 166 | Stepper motor | 02 Nos. |
| 167 | Servo motor | 02 Nos. |
| 168 | Control circuit | 02 Nos. |
| 169 | Temperature sensors. | 02 Nos. |
| 170 | IDE Software (C++ Language) | 1 |
| 171 | Nuts | 02 Dozen (each size) |
| 172 | Bolts | 02 Dozen (each size) |
| 173 | Screws | 02 Dozen (each size) |
| 174 | Grippers | 02 Nos. |
| 175 | Conveyor belt | 02 Nos. |
| 176 | Sensor | 02 Nos. |
| 177 | Actuator | 02 Nos. |
| 178 | Jumpers | 02 Nos. |
| 179 | SD card | 02 Nos. |
| 180 | LED | 02 Nos. |
| 181 | Power Adaptor | 02 Nos. |
| 182 | HDMI cable | 02 Rolls |
| 183 | Humidity sensor | 02 Nos. |
| 184 | Calculator | 02 Nos. |
| 185 | calibration standards measuring devices | 01 Nos. |
| 186 | calibration angles measuring devices | 01 Nos. |
| 187 | OHS Standard Manual | 1 |
| 188 | Capacitive pressure sensor | 02 Nos. |
| 189 | Electromagnetic pressure sensor | 02 Nos. |
| 190 | Optical pressure sensor | 02 Nos. |
| 191 | Force balancing | 02 Nos. |
| 192 | Pressure sensor | 02 Nos. |
| 193 | Lm35 ic solid state temperature sensor | 02 Nos. |
| 194 | Negative temperature coefficient (ntc) thermistor | 02 Nos. |
| 195 | Resistance temperature detector (rtd) | 02 Nos. |
| 196 | Thermocouple | 02 Nos. |
| 197 | Semiconductor-based sensors | 02 Nos. |
| 198 | Retro-reflective sensors | 02 Nos. |
| 199 | Diffuse reflection sensors | 02 Nos. |
| 200 | Hydraulic bench | 02 Nos. |
| 201 | Control Valve | 02 Nos. |
| 202 | Centrifugal pump | 02 Nos. |
| 203 | Sump tank | 02 Nos. |
| 204 | Vertical pipe | 02 Nos. |
| 205 | Channel | 02 Nos. |
| 206 | Drain Valve | 02 Nos. |

# 6.	Members of the Curriculum Development Committee

| S# | Name | Designation | Organization |
| --- | --- | --- | --- |
| 1 | Mr. Taufiq Ahmed | Automation Engineer | Dewan Cement |
| 2 | Mr. Aurangzeb Ansari | UIT | Usman Institute of Technology |
| 3 | Mr. Usama Khan | Assistant Manager, Maintenance | PCI, Automotive Pvt. Ltd. |
| 4 | Mr. Baber Sayeed | Chief Instructor. | Pak Swiss Training Center, Karachi |
| 5 | Mr. Tariq Aziz | CEO | Megafactor Engineering, Karachi |
| 6 | Mr. Mustafa Mohiuddin | Lecturer | Dawood University of Engg. & Tech. |
| 7 | Mr. Syed Farhan Hamid Ali | Sr. Instructor. | Pak Swiss Training Center, Karachi |
| 8 | Mr. Safwan | Automation Engineer | Dewan Cement |
| 9 | Mr. Yasir Arafat | Assistant Director | NAVTTC |
| 10 | Mr. Shaikh Asim Qamar | Certified DACUM Expert | iCAT Transmission |

# 7.	Members of the Curriculum Review & Validation Committee

| S# | Name | Designation | Organization |
| --- | --- | --- | --- |
| 1 | Mr. Shaikh Asim Qamar | Certified DACUM Expert | iCAT Transmission |
| 2 | Engr. Rizwan Iqbal | Assistant Professor | Dawood University of Engineering & Technology, Karachi |
| 3 | Mr. Tariq Aziz | CEO | Megafactor Engineering, Karachi |
| 4 | Mr. Mustafa Mohiuddin | Lecturer | Dawood University of Engg. & Tech. |
| 5 | Sohail Gull | Assistant Professor | GCT Peshawar |
| 6 | Mr. Muhammad Yasir | Deputy Director | NAVTTC |

Learning hours in training provider premises,

Training workshop, laboratory and on-the-job workplace