Instruction Sheet for the Candidate

| Qualification | Construction Machinery Level-5 ( Power Generators (GEN-SET)) |
| --- | --- |
| Competency Standard | Carry out Trouble Shooting Guide |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name______________________________________________________ Registration/Roll Number_______________________________________ |
| Guidance for Candidate | To meet this standard, you are required to complete the following within time frame (for practical demonstration & assessment): CU1. Analyze why Engine Fails To Start. CU2. Check Engine stoppage due to high coolant temperature. CU3. Troubleshot fan malfunction. CU4. Analyze auto mode (on, off) of generator. CU5. Check Alarm For Not In Auto Mode (Standby Sets Only). CU6. Check Output Voltage. CU7. Analyze why Output Voltage low. CU8. Analyze Voltage drop when load is imposed. CU9. Check why Voltage Higher than rated Voltage. |
| Time: 05 Hrs. | During a practical assessment, under observation by an assessor, you are required to |
| Minimum Evidence Required | Analyze why Engine Fails To Start. - Check all emergency stop push buttons are released - Check the stop button light is not on - Check there are no shutdown events active - Reset, if required, after remedying the indicated fault Check Engine stoppage due to high coolant temperature. - Check coolant level in the radiator. - Remove radiator cap safely using cloth - Fill water if necessary - Check the radiator - Check Thermostat - Check Water Pump Troubleshot fan malfunction. - Check radiator fan working or not - Check fuse of radiator fan - Check electrical supply of radiator fan Analyze auto mode (on, off) of generator. - Check that the generator set stops - Depress emergency stop push button - Held down the stop key for 5 seconds - Skip cool down time Check Alarm For Not In Auto Mode (Standby Sets Only). - Check the module is in “auto “mode - Check emergency stop push buttons are not pressed Check Output Voltage. - Fuse on AVR broken. - AVR broken. - Rotating rectifier (diode bridge) defect. - Alternator winding burned or broken. - Bad wire connection Analyze why Output Voltage low. - Adjust voltage on AVR. - Check alternator speed. - AVR defect. - Alternator windings damaged Analyze Voltage drop when load is imposed. - Check LED’s on AVR. - Check nominal power with load requirements. - Power problem on engine. - AVR defect. - Alternator windings Check why Voltage Higher than rated Voltage. - Unbalanced load. - Nonlinear load, harmonics. - AVR defect. |

Self-Assessment Checklist

| Candidate Name |  |
| --- | --- |
| Registration No. |  |
| Qualification | Construction Machinery Level-5 (Power Generators (GEN-SET)) |
| Competency Standard | Carry out Trouble Shooting Guide |
| Purpose of Assessment | Formative Assessment |
| Assessment Task | - Analyze why Engine Fails To Start. - Check Engine stoppage due to high coolant temperature. - Troubleshot fan malfunction. - Analyze auto mode(on, off) of generator. - Check Alarm For Not In Auto Mode (Standby Sets Only). - Check Output Voltage. - Analyze why Output Voltage low. - Analyze Voltage drop when load is imposed. - Check why Voltage Higher than rated Voltage. |

I can……………….

| Performance Criteria | Yes | No |
| --- | --- | --- |
| - Check all emergency stop push buttons are released |  |  |
| - Check the stop button light is not on |  |  |
| - Check there are no shutdown events active |  |  |
| - Reset, if required, after remedying the indicated fault |  |  |
| - Check coolant level in the radiator. |  |  |
| - Remove radiator cap safely using cloth |  |  |
| - Fill water if necessary |  |  |
| - Check the radiator |  |  |
| - Check Thermostat |  |  |
| - Check Water Pump |  |  |
| - Check radiator fan working or not |  |  |
| - Check fuse of radiator fan |  |  |
| - Check electrical supply of radiator fan |  |  |
| - Check that the generator set stops |  |  |
| - Depress emergency stop push button |  |  |
| - Held down the stop key for 5 seconds |  |  |
| - Skip cool down time |  |  |
| - Check the module is in “auto“ mode |  |  |
| - Check emergency stop push buttons are not pressed |  |  |
| - Check Fuse on AVR. |  |  |
| - Check AVR. |  |  |
| - Check Rotating rectifier (diode bridge) defect. |  |  |
| - Inspect Alternator winding. |  |  |
| - Bad wire connection |  |  |
| - Adjust voltage on AVR. |  |  |
| - Check alternator speed. |  |  |
| - Check AVR defect. |  |  |
| - Inspect Alternator windings damaged |  |  |
| - Check LED’s on AVR. |  |  |
| - Check nominal power with load requirements. |  |  |
| - Power problem on engine. |  |  |
| - Unbalanced load. |  |  |
| - Nonlinear load, harmonics. |  |  |

Candidate’s Signature__________________ Assessor’s Signature____________________

Date: _______________________________

Assessors Judgment Guide

| Qualification | Construction Machinery Level-5 (Power Generators (GEN-SET)) |
| --- | --- |
| Competency Standard | Carry out Trouble Shooting Guide |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name: ______________________________________________________________ Registration/Roll Number: ______________________Signature: _______________ |
| Assessment Outcome | COMPETENT NOT YET COMPETENT Name of the Assessor________________________________________________ Assessor’s code:____________________________________________________ Signature: ________________________________ |

| Assessment Summary (to be filled by the assessor) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Activity | Method |  |  |  |  | Result |  |
| Nature of Activity | Written | Oral | Observation | Portfolio | Role Play | Competent | Not Yet Competent |
| Practical Skill Demonstration |  |  |  |  |  |  |  |
| Knowledge Assessment |  |  |  |  |  |  |  |
| Other Requirement |  |  |  |  |  |  |  |

Observation Checklist

| Assessment Task |  | - Analyze why Engine Fails To Start. - Check Engine stoppage due to high coolant temperature. - Troubleshot fan malfunction. - Analyze auto mode(on, off) of generator. - Check Alarm For Not In Auto Mode (Standby Sets Only). - Check Output Voltage. - Analyze why Output Voltage low. - Analyze Voltage drop when load is imposed. - Check why Voltage Higher than rated Voltage. |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| During the practical assessment, candidate demonstrated the following: |  |  |  | Yes | No | Remarks |
|  | Check all emergency stop push buttons are released |  |  |  |  |  |
|  | Check the stop button light is not on |  |  |  |  |  |
|  | Check there are no shutdown events active |  |  |  |  |  |
|  | Reset, if required, after remedying the indicated fault |  |  |  |  |  |
|  | Check coolant level in the radiator. |  |  |  |  |  |
|  | Remove radiator cap safely using cloth |  |  |  |  |  |
|  | Fill water if necessary |  |  |  |  |  |
|  | Check the radiator |  |  |  |  |  |
|  | Check Thermostat |  |  |  |  |  |
|  | Check Water Pump |  |  |  |  |  |
|  | Check radiator fan working or not |  |  |  |  |  |
|  | Check fuse of radiator fan |  |  |  |  |  |
|  | Check electrical supply of radiator fan |  |  |  |  |  |
|  | Check that the generator set stops |  |  |  |  |  |
|  | Depress emergency stop push button |  |  |  |  |  |
|  | Held down the stop key for 5 seconds |  |  |  |  |  |
|  | Skip cool down time |  |  |  |  |  |
|  | Check the module is in “auto“ mode |  |  |  |  |  |
|  | Check emergency stop push buttons are not pressed |  |  |  |  |  |
|  | Check Fuse on AVR. |  |  |  |  |  |
|  | Check AVR. |  |  |  |  |  |
|  | Check Rotating rectifier (diode bridge) defect. |  |  |  |  |  |
|  | Inspect Alternator winding. |  |  |  |  |  |
|  | Bad wire connection |  |  |  |  |  |
|  | Adjust voltage on AVR. |  |  |  |  |  |
|  | Check alternator speed. |  |  |  |  |  |
|  | Check AVR defect. |  |  |  |  |  |
|  | Inspect Alternator windings damaged |  |  |  |  |  |
|  | Check LED’s on AVR. |  |  |  |  |  |
|  | Check nominal power with load requirements. |  |  |  |  |  |
|  | Power problem on engine. |  |  |  |  |  |
|  | Unbalanced load. |  |  |  |  |  |
|  | Nonlinear load, harmonics. |  |  |  |  |  |
| Competent |  |  | Not Yet Competent |  |  |  |

Knowledge Assessment

| Qualification | Construction Machinery Level-5 ( Power Generators (GEN-SET)) |
| --- | --- |
| Competency Standard | Carry out Trouble Shooting Guide |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name:______________________________________________________________ Registration/Roll Number: _________________ Candidate Signature:___________ |
| Assessment Outcome | COMPETENT NOT YET COMPETENT Name of the Assessor:________________________________________________ Assessor’s code:____________________________________________________ Signature of the Assessor:_______________________ |

Candidate’s response is not required to be identical, but similar concepts and/or keywords must be used. Oral questioning may be used to clarify candidate understanding of topic and its application.

| Questions (Candidate confidently answered questions correctly and demonstrated understanding of the topics and their application) |  | Satisfactory | Not Satisfactory |
| --- | --- | --- | --- |
|  | Explain emergency signals and signal LED’s |  |  |
|  | What is Thermostat and ATS(auto transfer switch)? |  |  |
|  | Describe water pump and what is cool down time? |  |  |

Feedback to the Candidate

Candidate’s Signature__________________ Assessor’s Signature _________________