National Vocational Certificate Level 4 in Electrical Technology

(Industrial Electrician)

(Curriculum)

National Vocational and Technical Training Commission (NAVTTC)

Government of Pakistan

Table of Contents

1. 	Introduction	5

1.1.	Purpose of the Training Program:	6

1.2.	Overall Objectives of Training Program	7

1.3.	Competencies to be gained after Completion of Course	8

1.4.	Entry Level of Trainees	10

1.5.	Minimum Qualification for Teachers	10

1.6.	Medium of Instruction	10

1.7.	Duration of the Course:	10

1.8.	Description and structure of the course	12

1.9.	Overview of the Curriculum for Electrical Technology (Level 1-5)	16

1.10.	Detail of Modules.	52

Computer Operator (Electrical)	52

1.10.1.	Select Computer Specification and Work with Windows	52

1.10.2.	Process Data with MS Office	55

1.10.3.	Carryout Basic Programming	59

1.10.4.	Perform Internet Browsing	62

1.10.5.	Perform the Different Engineering Curves Used in Various Mechanisms	65

1.10.6.	Perform Multi-View Drawings	73

1.10.7.	Draw Production Drawing	80

1.10.8.	Design and Simulate the Electronic Circuit by Using Computer Aided Design (CAD) Software	84

DC Machine Operator	90

1.10.9.	Verify Basic Laws of Electrical Machines	90

1.10.10.	Analyze DC Generators	95

1.10.11.	Perform Tests on DC Generators	105

1.10.12.	Analyze DC Motor	115

1.10.13.	Perform Tests on DC Motors.	119

1.10.14.	Repair/Maintenance and servicing of DC Motors and DC Generator	129

Transformer Winding Supervisor	134

1.10.15.	Verify Basic Laws of Electrical Machines	135

1.10.16.	Operate Single Phase Transformer	140

1.10.17.	Perform Tests on Single Phase Transformer	145

1.10.18.	Operate Auto Transformer	150

1.10.19.	Perform Tests on Auto Transformer.	152

1.10.20.	Operate Three Phase Transformer	156

1.10.21.	Identify Vector Group of Three Phase Transformer	164

1.10.22.	Repair/ Maintenance and Service of Transformer	167

Industrial Electrician	171

1.10.23.	Maintain Tools & Equipment for Three Phase	171

1.10.24.	Make Cable/Wire Joints for Three Phase	175

1.10.25.	Prepare and Install Distribution Boards for Three Phase	179

1.10.26.	Install Three Phase Electrical Wiring	182

1.10.27.	Install Three Phase Complex Electrical Wiring	188

1.10.28.	Perform Testing of Electrical Wiring	200

1.10.29.	Diagnose Electrical Fault in Generator	211

1.10.30.	Repair/ Maintenance of Electrical Installations for Three Phase	217

1.10.31.	Carry Out Manual Electrical Planning and Estimation	221

List of Personal Protective Equipment	229

Complete List of Tools, Equipment, Machines and Consumables	230

# 1. 	Introduction

The Technical and Vocational is a profession that is increasingly getting attention in Pakistan, not only among the youth seeking to enter the industry but also among adults who wish to polish their skills to develop a career out of it. Scope and demand of Electrical engineers, supervisors, operator, and technician is very high in Pakistan due to fast growing economic zone like CPEC. There are more job opportunities for electrical technician and supervisors in Pakistan than any other field of engineering. Pakistan is still facing energy crises, for need for more power houses, renewable energy sources is being felt which will definitely result in more demand of electrical engineers.

CBT based level 5 course in Electrical Technology with updated concepts, not only allows students to equip with growing Industrial trends but will be beneficial in capturing the job market across the globe. The course is divided into sub fields like electronics, computer engineering, power engineering, telecommunications, control systems, and microelectronics. Many of these sub disciplines overlap with other engineering branches, spanning a huge number of specializations such as hardware engineering, power electronics, avionics, Electrical and nanotechnology.

Pakistan can boost economic growth and job creation by overcoming inefficiencies in its power sector, Reforms that address these distortions can make better use of existing facilities. These need to focus on eliminating waste, promoting the shift towards cleaner energy and attracting private investments.”

“Power sector reform should be a top priority, as few other reforms could yield economic gains of a similar magnitude so quickly, based on findings from this report, and says Fan Zhang, Senior Economist at the World Bank. If well designed, these reforms will directly benefit the poor by increasing access, improving reliability, and reducing cost and pollution.”

## Purpose of the Training Program:

The purpose of the training is to set the high professional standards for the Electrical technological sector. The specific objectives of developing these qualifications are as under:

- Improve the professional competence of the trainees

- Provide opportunities for recognition of the skills attained through formal or informal pathways

- Improve the quality and effectiveness of the training and assessment for Electrical Technological sector

- Enabling / helping / facilitating the existing workforce to indulge themselves in new technologies and methods.

Based upon this demand of industry, these competency‐based qualifications for Electrical Technology are developed under National Vocational Qualification Framework (Level 1 to 5). The qualifications mainly cover competencies along with related knowledge and professional attitude which is essential for getting a job or self-employed.

The qualifications are also in line with the vision of Pakistan’s National Skills Strategy (NSS), National TVET Policy and National Vocational Qualification Framework (NVQF). This provides policy directions, support and an enabling environment to the public and private sectors to impart training for skills development to enhance social and economic profile. The National Vocational & Technical Training Commission (NAVTTC) has approved the Qualification Development Committee (QDC) for Textile Chefs Technology.The QDC consists experts from the relevant industries from different geographical locations across Pakistan and academicians who were consulted during the development process to ensure input and ownership of all the stakeholders. The National Modules could be used as a referral document for the development of curricula to be used by training institutions.

The purpose of the training is to provide skilled manpower to improve the quality of value added products of industrial sector. This training will provide the basic skills to the trainees in the field of Electrical and convert it into value added product which is acceptable by International market reducing the line losses and fit-in a skilled graduate into National Vocational Qualification Framework for his / her vertical career progression and qualification equivalencies at par with acceptable international standards.

## Overall Objectives of Training Program

The Electrical qualifications of level 4 consists of both the theoretical and practical details and having the following Occupations:

- Industrial Electrician

- Computer Operator-Electrical

- DC Machine Operator

- Transformer Winding Supervisor

## Competencies to be gained after Completion of Course

Detail of the modules included in qualification are given below:

Computer Operator-Electrical

- Select Computer Specification and Work with Windows.

- Process Data with MS Office.

- Carryout Basic Programming

- Explore Electrical

- Perform The Different Engineering Curves Used in Various Mechanism.

- Perform Multi-View Drawings.

- Draw Production Drawing.

- Design and Simulate the Electronic Circuit by Using Computer-Aided Design (Cad) Software

DC Machine Operator

- Verify Basic Laws of Electrical Machines

- Analyze Dc Generators

- Perform Tests On Dc Generators

- Analyze Dc Motors

- Perform Tests On Dc Motors

- Repair/ Maintenance and Service of Dc Motors and Dc Generators.

Transformer Winding Supervisor

- Verify Basic Laws of Electrical Machines

- Operate Single Phase Transformer

- Perform Tests On Single Phase Transformer.

- Operate Auto Transformer.

- Perform Tests On Auto Transformer.

- Operate Three Phase Transformer.

- Identify Vector Group of Three Phase Transformer

- Repair/ Maintenance and Service of Transformer

Soft Skills

- Develop Workplace Policy and Procedures for Sustainability

- Maintain Professionalism in the Workplace

- Manage Personal Work Priorities and Professional Development

- Manage Workforce Planning

- Undertake Project Work

- Prepare and Implement Negotiation

- Manage Meetings

- Organize Schedules

- Identify and Communicate Trends in Career Development

- Apply Specialist Interpersonal and Counseling Interview Skills

## Entry Level of Trainees

The entry level for National Vocational Certificate Level 4 in Electrical Technology is:

A person having National Vocational Certificate Level 3 in Electrical Technology

## Minimum Qualification for Teachers

- B.Sc. / B.E. in Electrical Engineering.

- 4 Years B. Tech in Electrical Technology with 3 Years teaching experience.

- D. A. E. in Electrical Technology with 7 Years teaching experience

- Must be able to communicate effectively

## Medium of Instruction

English, and Urdu.

## Duration of the Course:

The proposed curriculum is composed of 39 modules (Technical+Generic) that will be covered in 1200 Contact hours. Duration of the course is proposed to be Three years.

Level- 4 = 12 months.

The distribution of contact hours is given below:

Total.		1200 hours.

Theory: 	240 hours (20%)

Practical.	960 hours (80%)

## Description and structure of the course

Following is the structure of the course:

| Competency Standards | Occupation | NVQF Level | Category | Estimated Contact Hours |  |  | Cr Hr |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Th | Pr | Total |  |
| Level 4 |  |  |  |  |  |  |  |
| Select Computer Specification and Work with Windows. | Computer Operator (Electrical) | Level 4 | Technical | 6 | 21 | 27 | 2.7 |
| Process Data with MS Office. |  | Level 4 | Technical | 6 | 21 | 27 | 2.7 |
| Carryout Basic Programming |  | Level 4 | Technical | 6 | 21 | 27 | 2.7 |
| Perform Internet Browsing |  | Level 4 | Technical | 6 | 18 | 24 | 2.4 |
| Perform The Different Engineering Curves Used in Various Mechanisms. |  | Level 4 | Technical | 6 | 24 | 30 | 3 |
| Perform Multi-View Drawings. |  | Level 4 | Technical | 6 | 24 | 30 | 3 |
| Draw Production Drawing. |  | Level 4 | Technical | 6 | 18 | 24 | 2.4 |
| Design and Simulate the Electronic Circuit by Using Computer-Aided Design (Cad) Software |  | Level 4 | Technical | 3 | 30 | 33 | 3.3 |
| Verify Basic Laws of Electrical Machines | DC Machine Operator | Level 4 | Technical | 6 | 21 | 27 | 2.7 |
| Analyze Dc Generators |  | Level 4 | Technical | 6 | 21 | 27 | 2.7 |
| Perform Tests On Dc Generators |  | Level 4 | Technical | 6 | 24 | 30 | 3 |
| Analyze Dc Motors |  | Level 4 | Technical | 6 | 21 | 27 | 2.7 |
| Perform Tests On Dc Motors |  | Level 4 | Technical | 6 | 24 | 30 | 3 |
| Repair/ Maintenance and Service of Dc Motors and Dc Generators. |  | Level 4 | Technical | 6 | 24 | 30 | 3 |
| Verify Basic Laws of Electrical Machines | Transformer Winding Supervisor | Level 4 | Technical | 6 | 18 | 24 | 2.4 |
| Operate Single Phase Transformer |  | Level 4 | Technical | 6 | 18 | 24 | 2.4 |
| Perform Tests On Single Phase Transformer. |  | Level 4 | Technical | 6 | 24 | 30 | 3 |
| Operate Auto Transformer. |  | Level 4 | Technical | 3 | 24 | 27 | 2.7 |
| Perform Tests On Auto Transformer. |  | Level 4 | Technical | 6 | 30 | 36 | 3.6 |
| Operate Three Phase Transformer. |  | Level 4 | Technical | 6 | 27 | 33 | 3.3 |
| Identify Vector Group of Three Phase Transformer |  | Level 4 | Technical | 6 | 24 | 30 | 3 |
| Repair/ Maintenance and Service of Transformer |  | Level 4 | Technical | 6 | 24 | 30 | 3 |
| Maintain Tools & Equipment. | Industrial Electrician | Level 2 | Technical | 6 | 21 | 27 | 2.7 |
| Make Cable/Wire Joints for three phase |  | Level 2 | Technical | 6 | 24 | 30 | 3 |
| Prepare and Install Distribution Boards for three phase |  | Level 2 | Technical | 6 | 27 | 33 | 3.3 |
| Install Three Phase Electrical Wiring |  | Level 3 | Technical | 6 | 24 | 30 | 3 |
| Install Three Phase Complex Electrical Wiring |  | Level 3 | Technical | 6 | 27 | 33 | 3.3 |
| Perform Testing of Electrical Three Phase Wiring |  | Level 3 | Technical | 6 | 24 | 30 | 3 |
| Diagnose Electrical Fault in Generator |  | Level 3 | Technical | 6 | 24 | 30 | 3 |
| Repair/ Maintenance of Electrical Installations |  | Level 3 | Technical | 3 | 27 | 30 | 3 |
| Carry Out Manual Electrical Planning and Estimation |  | Level 3 | Technical | 9 | 24 | 33 | 3.3 |
| Develop Workplace Policy and Procedures for Sustainability | Soft Skills | Level 4 | Generic | 6 | 27 | 33 | 3.3 |
| Maintain Professionalism in the Workplace |  | Level 4 | Generic | 6 | 24 | 30 | 3 |
| Manage Personal Work Priorities and Professional Development |  | Level 4 | Generic | 6 | 24 | 30 | 3 |
| Manage Workforce Planning |  | Level 4 | Generic | 6 | 27 | 33 | 3.3 |
| Undertake Project Work |  | Level 4 | Generic | 6 | 30 | 36 | 3.6 |
| Prepare and Implement Negotiation |  | Level 4 | Generic | 6 | 24 | 30 | 3 |
| Manage Meetings |  | Level 4 | Generic | 6 | 15 | 21 | 2.1 |
| Organize Schedules |  | Level 4 | Generic | 6 | 15 | 21 | 2.1 |
| Identify and Communicate Trends in Career Development |  | Level 4 | Generic | 6 | 24 | 30 | 3 |
| Apply Specialist Interpersonal and Counseling Interview Skills |  | Level 4 | Generic | 6 | 27 | 33 | 3.3 |
| Total |  |  |  | 240 | 960 | 1200 | 120 |
| Percentage |  |  |  | 20 | 80 |  |  |

## Overview of the Curriculum for Electrical Technology (Level 1-5)

| Module Title and Aim | Learning Units |  | Th Days/hours | Workplace Days/hours | Timeframe of modules |
| --- | --- | --- | --- | --- | --- |
| Module 3.1.1 Maintain Occupational Health and Safety | - Ensure the use of personal protective equipment (PPE). - Maintain First-aid Box - Maintain Fire Extinguisher. - Ensure Safeguard of Machines. - Adopt company policies and procedures. - Attain health & safety training. - Prepare for emergencies. - Respond to emergencies |  |  |  |  |
| Module 3.1.2 Adopt Safety Regulation, Labour Protection Laws, Environmental Protection Laws at Workplace | - Implement International Safety Standards in your work environment. - Implement National Safety Standards in your work environment - Implement International and National Labor Protection Laws - Implement National and International Environmental protection laws. - Prepare for emergencies. - Respond to emergencies. - Adopt company policies and procedures. |  |  |  |  |
| Module 3.2.1 Maintain Tools & Equipment for Single Phase Wiring | - Arrange Tools and Equipment - Maintain Tool Box - Insulate Tools and Equipment - Calibrate measuring tools - Manage Inventory of tools and equipment |  |  |  |  |
| Module 3.2.2 Make Cable/Wire Joints for Single Phase Wiring | - Make Cross/Twist joint - Make Straight/Married joint - Make T-Joint - Make Rat-tail joint - Make Britannia joint |  |  |  |  |
| Module 3.2.3 Prepare and Install Distribution Boards for Single Phase Wiring. | - Prepare estimate for wiring material. - Prepare Distribution Board - Install Distribution Board and wiring |  |  |  |  |
| Module 3.2.4 Carryout Basic Electrical Installation for Single Phase | - Perform Basic Electrical wiring - Conduct wiring Test - Lay Cables - Perform single-phase Connection - Perform three phase Connection |  |  |  |  |
| Module 3.2.5 Install Simple Single Phase Electrical Wiring | - Make single pole switch circuit - Make single pole switch socket circuit. - Make two-way switch circuit - Make series/ test lamp circuit - Make intermediate switch circuit. - Make of Tunnel circuit |  |  |  |  |
| Module 3.2.6 Install Single Phase Complex Electrical Wiring | - Design/Develop and Install Kitchen wiring - Install Drawing room circuit - Install Sleeping room circuit - Install hall wiring. - Install impulse switch - Install Bell indicator circuit. - Install timer/time switch circuit - Make fluorescent tube circuit and install - Perform Domestic Electrical Work |  |  |  |  |
| Module 3.2.7 Perform Testing of Electrical Wiring | - Perform Open Circuit Test - Perform Short Circuit Test - Perform Continuity/Loop Test - Perform Visual Test - Perform Insulation Test - Perform Polarity Test - Perform Earth Resistance Test - Perform Earth leakage Test. |  |  |  |  |
| Module 3.2.8 Repair/ Maintenance of Electrical Installations in Single Phase | - Analyze Fault in Electrical Installations - Troubleshoot electrical equipment’s - Carry out Preventive Maintenance |  |  |  |  |
| Module 3.2.9 Repair/ Maintenance and Service of Home Appliance | - Diagnose fault and repair electric iron - Repair/ maintenance of Pedestal Fan and Ceiling Fan. - Repair/ maintenance of Juicer and grinder - Repair/ maintenance Refrigerator /Air conditioner - Repair/ maintenance of sandwich maker/toaster - Repair/ maintenance of washing machine/dryer |  |  |  |  |
| Module 3.4.1 Operate Measuring Instruments | - Operate Ampere meter. - Operate Volt meter. - Operate Ohm meter |  |  |  |  |
| Module 3.4.2 Verify Ohm’s Law & Kirchhoff’s Law by Implementing Series/Parallel Circuits | - Make series circuit and measure voltage and verify KVL. - Make parallel circuit and measure current and verify KCL - Verify resistance of resistors - Verify Ohm’s Law - Measure resistance of Rheostat - . Measure resistance by using Multimeter - . Measure resistance of incandescent lamp |  |  |  |  |
| Module 3.4.3 Measure Electrical Power, Energy, Power Factor & Determine Phase Sequence |  | - Measure power using Multimeter method - Measure power using Multimeter method - Measure single phase AC Power - Measure three phase AC Power. - Measure consumed energy with Energy meter - Measure power factor with voltmeter, ampere meter and watt meter - Measure power factor with power factor - Improve power factor & measure it with power factor meter - Determine phase sequence with phase sequence meter. |  |  |  |
| Module 3.4.4 Operate Oscilloscope |  | - Measure AC voltage with oscilloscope. - Measure current with oscilloscope - Measure frequency of AC signal with oscilloscope - Measure time period of AC signal with oscilloscope - Measure RMS value of AC signal with oscilloscope - Measure average value of AC signal with oscilloscope |  |  |  |
| Module 3.4.5 Implement Electromagnet to See Various Effects & Verify Faradays Law |  | - Implement Electromagnet - Implement circuit to determine the effect on current carrying conductor in magnetic field - Determine the effect on conductor by varying the current with the help of rheostat. - Plot magnetic lines of forces of bar magnet - Verify Faradays law by moving magnet in side coil. - Verify Faraday’s law by moving coil near the magnet field - Verify EMF through induction. |  |  |  |
| Module 3.4.6 Verify law of Combination of Capacitors & Determine Break Down Voltage of Capacitor |  | - Implement a series circuit of capacitors - Implement a parallel circuit of capacitors - Determine the breakdown voltage of low voltage capacitor |  |  |  |
| Module 3.5.1 Perform Cleaning, Oiling and Centering the Job |  | - Perform Cleaning and Oiling of the Lathe Machine - Perform Centering the Job By Tool Method - Perform Centering The Job Held In a Four Jaw Chuck Of Face Plate |  |  |  |
| Module 3.5.2 Perform Facing, Straight Turning, Center Drilling |  | - Perform Facing - Perform Straight Turning - Perform Center Drilling |  |  |  |
| Module 3.5.3 Perform Drilling, Step Turning, Knurling and Boring a Straight Hole on lathe |  | - Perform Drilling On Lathe - Perform Step Turning - Perform Knurling - Perform Boring a Straight Hole |  |  |  |
| Module 3.5.4 Perform Step or Counter Boring, Reaming, Tool Grinding, Taper Turning and Cutting Metric Threads. |  | - Perform Step Or Counter Boring - Perform Reaming - Perform Tool Grinding - Perform Taper Turning By Compound Rest Method - Perform Cutting Metric Threads On Lathe Machine |  |  |  |
| Module 3.5.5 Perform Basic Metal Work |  | - Develop Name Plate manually - Carryout Sawing - Prepration of Inside Calliper - Prepration of Bottle Opener - Prepration of Dovetail Joint - Prepration of small size Tri Square - Produce internal Threads in Work Piece - Prepration of Funnel - Prepration of Drawer Handle - Produce Pipe Threads - Prepare a spanner of (small size) |  |  |  |
| Module 3.5.6 Perform Wood Work |  | - Planning and Squaring to dimensions - Sawing Exercise - Making Mortise and Tendon Joint - Making Dado Joint - Making Cross-lap Joint - Making holes of different Diameters in Wood - Nailing and Wood Screwing Process - Making Middle Half Cross lap joint - Making Dovetail Joint |  |  |  |
| Module 3.5.7 Perform Oxy Acetylene Welding |  | - Make flame for gas welding carburizing flam, Neutral flam, oxidizing flam - Make Pool - Make Bead - Make Edge Joint - Make Open square butt joint (M.S Flat 3mm OR 5mm Thickness) - Make ‘V’ Groove butt joint ( Flat Position) - Make Corner joint - Make Open square brazing Butt joint(M.S Flat 5mm thick |  |  |  |
| Module 3.5.8 Perform Arc Welding |  | - Make Arc - Make Bead - Make Open Square Butt Joint (MS Flat 5 mm Thick) - Make V Groove Butt Joint - Make Lap Joint - Make Corner Joint Flat Position - Make Corner Joint Vertical Position - Make Spot Welding Practice (0.5 mm MS Sheet) - Make Seam Welding Practice (0.5 mm MS Sheet) |  |  |  |
| Module 3.6.1 Maintain Tools & Equipment for Three Phase |  | - Arrange Tools and Equipment - Maintain Tool Box - Insulate Tools and Equipment - Calibrate measuring tools - Manage Inventory of tools and equipment |  |  |  |
| Module 3.6.2 Make Cable/Wire Joints for Three Phase |  | - Make Cross/Twist joint - Make Straight/Married joint - Make T- Joint - Make Rat tail joint - Make Britannia joint |  |  |  |
| Module 3.6.3 Prepare and Install Distribution Boards for Three Phase |  | - Prepare estimate for wiring material - Prepare Distribution Board - Install Distribution Board and wiring |  |  |  |
| Module 3.6.4 Install Three Phase Electrical Wiring |  | - Make and Install 3 phase motor connection ON/OFF by CAM Switch - Make and Install 3 phase motor connection reversing by CAM Switch - Make and Install 3 phase motor connection ON/OFF by Magnetic Contactor - Perform Electrical Work in Commercial Area. |  |  |  |
| Module 3.6.5 Install Three Phase Complex Electrical Wiring |  | - Make and Install 3 phase motor connection Reverse/ forward by Magnetic contactor. - Make and Install 3 phase motor connection Reverse/ forward by Magnetic contactor with indicator. - Make and Install 3 phase motor connection Star/Delta (Manual) by Magnetic contactor. - Make and Install 3 phase motor connection Star/Delta (Manual) by Magnetic contactor with indicator. - Make and Install 3 phase motor connection Star/Delta (Auto) by Magnetic contactor. - Make and Install 3 phase motor connection Star/Delta (Auto) by Magnetic contactor with indicator - Make and Install 3 phase motor connection 2 speed by Magnetic contactor - Make and Install 3 phase motor connection 2 speed by Magnetic contactor with indicator |  |  |  |
| Module 3.6.6 Perform Testing of Electrical Wiring |  | - Perform Earth leakage Test - Perform Open Circuit Test - Perform Short Circuit Test - Perform Continuity/Loop Test - Perform Visual Test - Perform Insulation Test - Perform Polarity Test - Perform Earth Resistance Test - Perform Murray Loop Test - Perform BLAVIER & Earth Loop Test |  |  |  |
| Module 3.6.7 Diagnose Electrical Fault in Generator |  | - Inspect and service Ignition system. - Inspect and service alternator - Inspect and service display panel - Inspect and service governor /Actuator System - Inspect and service charging system - Inspect and service warning system - Inspect and repair wiring |  |  |  |
| Module 3.6.8 Repair/ Maintenance of Electrical Installations for Three Phase |  | - Analyze Fault in Electrical Installations |  |  |  |
| Module 3.6.9 Carry Out Manual Electrical Planning and Estimation |  | - Analyze customer requirement and specification - Plan and estimate domestic electric work - Plan and estimate commercial electric work. - Plan and estimate industrial electric work. |  |  |  |
| Module 3.6.10 Measure Current, Voltage and Make Multiplier for Galvanometer Range Extension |  | - Measure current with Galvanometer - Measure voltage with Galvanometer - Make multiplier for Galvanometer range extension |  |  |  |
| Module 3.6.11 Measure Temperature, Earth Resistance, Light Intensity |  | - Measure temperature with thermocouple by voltage method - Measure the earth resistance by using earth resistance tester - Measure the light intensity with lux meter |  |  |  |
| Module 3.6.12 Measure the Resistance, Measure High Dc Current by Using Shunt. |  | - Measure the resistance by using wheat stone bridge - Measure the resistance by ohm meter - Measure the resistance by AVO meter - Measure high DC current by using shunt |  |  |  |
| Module 3.6.13 Measure Voltage, Frequency, Capacitance & Inductance by CRO |  | - Measure voltage using CRO - Measure frequency using CRO - Measure capacitance using CRO - Measure inductance using CRO |  |  |  |
| Module 3.6.14 Measure Capacitance and Inductance by RLC Meter, Dismantle and Assemble the Instruments |  | - Measure Capacitance by RCL Meter - Measure Inductance by RCL Meter - Dismantle and assemble the moving iron and permanent magnet type instrument |  |  |  |
| Module 3.6.15 Identify The Parts and Connection of Energy Meter(Single/3-Phase), Factor(Pf) Meter, MDI Meter, Maggar |  | - Identify parts and connection of Energy meter(Single/3-phase) - Identify different types of PF meter, its parts and connect it in circuit. - Identify MDI meter parts and use it on line - Measure insulation resistance by Meager |  |  |  |
| Module 3.6.16 Calibrate Electrical Equipment’s |  | - Perform Pre-Calibration activity - Calibrate Ammeter - Calibrate Voltmeter - Calibrate Ohmmeter - Calibrate multimeter - Calibrate 2-terminal/4-terminal Resistor (Direct method) - Calibrate 2-terminal/4-terminal Resistor (Indirect method) - Calibrate Standard Capacitor - Calibrate Standard Inductor - Prepare calibration report |  |  |  |
| Module 3.7.1 Select Computer Specification and Work with Windows |  | - Identify computer requirements and assemble procedures - Make a set of requirements for a personal computer - Work on windows Environment and Install the required operating System with Device drivers |  |  |  |
| Module 3.7.2 Process Data with MS Office |  | - Use MS OFFICE (MS-WORD) - Use MS OFFICE (MS-EXCEL) - Use MS- OFFICE (MS-POWER POINT) |  |  |  |
| Module 3.7.3 Carryout Basic Programming |  | - Make a program to perform arithmetic operations - Make a program in C++ to preparing logical operation - Make a program to sort a string of numbers. |  |  |  |
| Module 3.7.4 Perform Internet Browsing |  | - Draw pin diagram of electronic IC using of search engine - Browse data sheets and symbols - Browse manuals |  |  |  |
| Module 3.7.5 The Different Engineering Curves Used in Various Mechanisms |  | - Construct inscribe and circumscribe figures. - Construct a pentagon, Hexagon and Octagon by circumscribe method. - Construct a pentagon, Hexagon and Octagon by inscribe method - Construct a Tangents of circles (Inside &Outside) when the centre of the given circle is known and when the circle of centre is not known. - Construct an Ellipse by Concentric Circle Method, Rectangle Method, and Oblong Method, Arcs of Circle Method, Rhombus Method and Basic Locus Method. - Construct a parabola curve by Rectangle Method, Method of Tangents( Triangle Method) and Basic Locus Method - Construct a hyperbola curve. - Construct a Archimedean Spiral curve - Construct a involutes curve of square rectangle hexagon and circle. - Construct of cycloid, epicycloids, and hypocycloid |  |  |  |
| Module 3.7.6 Perform Multi-View Drawings |  | - Sketch Orthographic projection 1st angle - Sketch Orthographic projection 3rd angle. - Sketch Oblique Drawing - Construct multi view drawing of Simple Bearing. - Construct multi view drawing of Open Bearing - Sketch prism - Sketch cone - Draw pyramid |  |  |  |
| Module 3.7.7 Draw Production Drawing |  | - .Draw the assembly drawing of Boiler Stop Valve - Draw the views of Connecting Rod in detail and assembly drawing - Draw the assembly drawing of Screw Jack - Draw the assembly of Tail Stock in full section showing its parts |  |  |  |
| Module 3.7.8 Design and Simulate the Electronic Circuit by Using Computer Aided Design (CAD) Software |  | - Analyze customer requirement and specification - Plan and estimate domestic electric work - Plan and estimate commercial electric work. - Plan and estimate industrial electric work |  |  |  |
| Module 3.8.1 Verify Basic Laws of Electrical Machines |  | - Verify Faraday’s law by moving permanent magnet inside the coil. - Verify Faraday’s law by moving coil near the magnet field - Verify Faraday’s law using relative motion of coil and magnet - Verify Faraday’s Law using simple loop generator - Verify Torque induce in a current carrying loop - Verify Mutual induction |  |  |  |
| Module 3.8.2 Analyze DC Generators |  | - Calculate different terms used in armature winding of DC machines. - Develop Single Layer Lap Winding - Develop Double Layer Wave Winding. - Measure the resistance of field winding, armature winding and terminal polarity - Identify DC shunt generator - Identify DC series generator - Identify DC compound generator |  |  |  |
| Module 3.8.3 Perform Tests on DC Generators |  | - Plot the Open circuit characteristics of a Separately excited D.C generator - . Plot the Open circuit characteristics of a D.C shunt generator - Plot the load characteristics of D.C shunt generator - Plot the load characteristics of D.C series generator. - Plot the load characteristics of D.C compound generator for under, flat and over compounding - Perform parallel operation of two DC shunt generators - . Determine copper, iron & friction losses of shunt generator by actual loading |  |  |  |
| Module 3.8.4 Analyze DC Motor |  | - Identify DC shunt motor - Identify DC series motor - Identify DC compound motor |  |  |  |
| Module 3.8.5 Perform Tests on DC Motors |  | - Plot the load characteristics of D.C shunt motor - Plot the load characteristics of D.C series motor - Plot the load characteristics of D.C compound motor - Control the speed of DC series motor - Control the speed of DC shunt motor - Start DC shunts motor with 3 point starter. - Identify the effect of back EMF in DC motor - Calculate Brake Horse Power (BHP) of motor by Brake test. - Calculate efficiency of the motor by Swinburne Test - Perform Regenerative / Hopkinson/ Back to back Test |  |  |  |
| Module 3.8.6 Repair/Maintenance and servicing of DC Motors and DC Generator |  | - Diagnose Fault in DC Motor - Carry out Service / Repair in Electric Motor - Carry out Preventive Service/ Maintenance of Generators - Diagnose and Repair Electric Generator |  |  |  |
| Module 3.9.1 Verify Basic Laws of Electrical Machines |  | - Verify Faraday’s law by moving permanent magnet inside the coil - Verify Faraday’s law by moving coil near the magnet field. - Verify Faraday’s law using relative motion of coil And magnet. - Verify Faraday’s Law using simple loop generator - Verify Torque induce in a current carrying loop - Verify Mutual induction |  |  |  |
| Module 3.9.2 Operate Single Phase Transformer |  | - Identify types of transformer - Measure transformation ratio of single phase transformer - Make transformer winding - Determine voltage regulation of single phase transformer with different loads. - Perform parallel operation of single phase transformer. |  |  |  |
| Module 3.9.3 Perform Tests on Single Phase Transformer |  | - Perform polarity test of single phase transformer - Perform Open circuit test of transformer - Perform Short circuit Test of Transformer - Calculate efficiency of transformer by direct method - Calculate efficiency of transformer by Back to Back test. |  |  |  |
| Module 3.9.4 Operate Auto Transformer |  | - Identify the connection of auto transformer - Calculate Voltage ratio of Auto Transformer - Calculate Current ratio of Auto Transformer |  |  |  |
| Module 3.9.5 Perform Tests on Auto Transformer |  | - Perform open circuit Test of auto transformer - Perform short circuit test of auto transformer - Calculate efficiency of auto transformer. |  |  |  |
| Module 3.9.6 Operate Three Phase Transformer |  | - Make Three Phase Transformer Winding. - Perform Star to Star Connection Of Three Phase Transformer - Perform Star To Delta Connection Of Three Phase Transformer - Perform Delta to Delta Connection Of Three Phase Transformer - Perform Delta to Star Connection Of Three Phase Transformer - Connect Two Single Phase Transformers In Open Delta. - Perform Parallel operation of 3 phase transformers |  |  |  |
| Module 3.9.7 Identify Vector Group of Three Phase Transformer |  | - Connect 3-phase transformers as per given vector group Yyo and Yy6 - Connect 3-phase transformers as per given vector group Ddo and Dd6 - Connect 3-phase transformers as per given vector group Yd11 and Yd1 |  |  |  |
| Module 3.9.8 Repair/ Maintenance and Service of Transformer |  | - Diagnose Fault in transformer - Carry out Service/Repair of Transformer - Carry out Preventive Service/ Maintenance of transformer |  |  |  |
| Module 3.11.1 Perform Pre-Electroplating Activities. |  | - Perform Disassembly and Stripping - Perform Mechanical Cleaning - Perform Chemical Cleaning |  |  |  |
| Module 3.11.2 Perform Electroplating |  | - Ensure safety at workshop - Select appropriate chemical solution - Prepare chemical solutions - Perform plating of Zinc, Cadmium, Tin, Silver, Gold and Brass |  |  |  |
| Module 3.11.3 Perform Post-Electroplating Activities and Tests. |  | - Carry Out Quenching/ Cooling Of The Metal. - Carry Out Visual Inspection And Physical Examination Of The Electroplated Part. - Perform adhesion tests by various methods - Perform thickness and corrosion resistance test |  |  |  |
| Module 3.11.4 Plan an Electroplating Shop |  | - Prepare a layout for the electroplating workshop - Setup pre-Electroplating workstation - Setup Electroplating workshop - Setup post-Electroplating workstation - Prepare an Estimate for Finance and Budgeting |  |  |  |
| Module 3.12.1 Perform Basic Mathematics Calculations in C++ |  | - Generate Addition Program - Generate Subtraction Program - Generate Multiplication Program - Generate Division Program - Generate Program For Power Calculations - Generate Program For Roots Calculations - Generate Program For Exponential Calculations - Generate Trigonometric Function Program - Generate Inverse Trigonometric Function Program - Generate The Program And Calculate Impedance In Polar - Generate The Program And Calculate Impedance In Rectangular - Generate Rectangular To Polar Form Conversion program - Generate Polar Form To Rectangular Form program |  |  |  |
| Module 3.12.2 Perform Basic Circuit Analysis in C++ |  | - Generate Series Circuit Function Program - Generate Parallel Circuit Function Program |  |  |  |
| Module 3.12.3 Perform Electrical Analysis in C++ |  | - Calculate A.C Powers Solution Program - Solve Active Component Function Program - Solve Reactive Component Of Function Program - Generate Program For Improvement Of Power Factor |  |  |  |
| Module 3.12.4 Develop and Analyze Electrical Circuit with MULTISM |  | - Identify computer software component - Install and operate MULTISM - Idenitify toolbox and libraries - Develop RC circuit - Develop RLC circuit - construct active filter - construct passive filter - Construct Amplifier frequency response - Construct half wave rectifier - Construct full wave rectifier |  |  |  |
| Module 3.12.5 Develop and Analyze Electrical circuit with PSPICE software |  | - Install and operate PSPICE - Develop filters - Develop rectifier - Construct CE Amplifier - construct CS Amplifier - construct CC amplifier - Design WEIN Bridge Oscillator |  |  |  |
| Module 3.12.6 Carry out Electrical Planning and Estimation in Computer |  | - Analyze customer requirement and specification - Plan and estimate domestic electric work - Plan and estimate commercial electric work - Plan and estimate industrial electric work |  |  |  |
| Module 3.12.7 Carry out Industrial Automation and PLC Installation |  | - Install PLC software and Simulator - Program a PLC using simulator - Analyze user requirements and specification |  |  |  |
| Module 3.13.1 Verify Basic Laws of Electrical Machines |  | - Verify Faraday’s law by moving permanent magnet inside the coil. - Verify Faraday’s law by moving coil near the magnet field. - Verify Faraday’s law using relative motion of coil and magnet - Verify Faraday’s Law using simple loop generator. - Verify Torque induce in a current carrying loop - Verify Mutual induction |  |  |  |
| Module 3.13.2 Analyze an Alternator |  | - Measure the stator winding resistance with DC test. - Perform no load test - Perform short circuit test. - Measure the efficiency of an alternator. - Measure the effect of field current on terminal voltage. - Measure the effect of speed changes on alternator frequency and active power. - Perform parallel operation of Alternators. |  |  |  |
| Module 3.13.3 Analyze Single Phase Motors. |  | - Operate split phase single phase AC motor. - Operate capacitor start and Capacitor run single phase AC motor. - Operate shaded pole single phase motor. |  |  |  |
| Module 3.13.4 Analyze Special Purpose Motors. |  | - Operate and speed control of AC series motor. - Operate miniature (reluctance and hysteresis) single phase AC motors. - Construct and operate stepper motor. - Construct, Operate and develop control circuit of servo motor |  |  |  |
| Module 3.13.5 Analyze Three Phase Motors. |  | - Identify and operate 3 phase Squirrel cage motor - Verify rotating magnetic field - Measure the starting and running current of three phase induction motor. - Draw torque slip curve of three phase induction motor - Determine the slip of 3 phase induction motor by stroboscope - Start, 3 phase Induction motor with direct on line. - Start, 3 phase Induction motor with Auto transformer starter. - Start, 3 phase Induction motor with Star Delta starter. - Make connection to reverse the direction of induction motor. - Determine the efficiency of three phase induction motor - Control the speed of three phase induction motor by changing primary voltage - Control the speed of three phase induction motor by rotor resistance control method - Operate two motors in cascade - Start the synchronous motor using external prime mover. - Identify the effect of field current on three phase synchronous motor. |  |  |  |
| Module 3.13.6 Repairs/Maintenance and Service of AC Electric Motors and Generators |  | - Diagnose Fault in Electric Motor - Carry out Service/Repair in Electric Motor - Carry out Preventive Service/ Maintenance of Generators - Diagnose and Repair Electric Generator |  |  |  |
| Module 3.14.1 Identify Basic Electronics Components |  | - Identify Various Diodes - Identify Resistors in circuit - Identify Capacitor in circuit - Identify Inductor in circuit - Identify transistor and its types |  |  |  |
| Module 3.14.2 Design a Rectifier using Diode |  | - Identify The parameter of Diode and Draw the characteristic curve of Diode - Design half wave and Full Wave Rectifier (two diode rectifier - Design Full Wave Bridge rectifier |  |  |  |
| Module 3.14.3 Carry out Diode Application |  | - Make voltage regulator using Zener diode - Make Seven Segment Using Light Emitting Diode |  |  |  |
| Module 3.14.4 Implement Bipolar Junction Transistor (BJT) in Different Applications |  | - Perform the Biasing of Transistors - Implement Transistor as an amplifier using CB configuration - Implement Transistor as an amplifier using CC Configuration - Implement Transistor as an amplifier using CE Configuration. - Implement BJT as a switch. - Design the circuit of Class A Power Amplifier |  |  |  |
| Module 3.14.5 Implement Field Effect Transistor (FET) in Different Applications |  | - Perform the Biasing of FET - Implement MOSFET as a switch. - Draw the VI characteristics curves for FETs - Design the circuit of Common Drain (CD) Amplifier - Design the circuit of Common Gate (CG) amplifier. - Construct a Low voltage transistor based regulated power supply |  |  |  |
| Module 3.14.5 Implement Thyristor Family in Various Application |  | - Implement the SCR in electronic circuits as switch - Implement the UJT in electronic circuits as switch - Construct the dimmer circuit using Diac &Triac |  |  |  |
| Module 3.14.6 Application of Operational Amplifier |  | - Construct a Non-inverting amplifier using operational amplifier - Construct an Inverting amplifier using operational amplifier - Construct a differentiator circuit using operational amplifier - Construct a integrator circuit using operational amplifier - Construct a Comparator circuit using operational amplifier |  |  |  |
| Module 3.14.7 Verify Truth Table of Digital Gates |  | - Verify the truth table of AND gate - Verify the truth table of OR gate - Verify the truth table of NOT gate - Verify the truth table of NAND gate - Verify the truth table of NOR gate - Verify the truth table of XOR gate - Verify the truth table of XNOR gate |  |  |  |
| Module 3.14.8 Construct & Verify Combinational Logic Circuit |  | - Apply Karnaugh mapping & Boolean algebra to simplify logic expressions - Construct & verify the truth table of Half adder - Construct & verify the truth table of Full adder - Construct & verify the truth table of Half Subtraction - Construct & verify the truth table of Full Subtraction - Verify Decoder - Operate seven segment display with seven segment decoder - Verify Encoder - Verify multiplexer and DE- multiplexer |  |  |  |
| Module 3.14.9 Construct and Verify Function of Flip Flops |  | - Construct and verify the truth table of RS latch using NAND gate - Construct and verify the truth table of clocked RS latch using NAND gate - Verify function of D flip flop. - Verify function of JK/T flip flop |  |  |  |
| Module 3.14.10 Use 555 IC as Multivibrator |  | - Construct 555 IC as Astable Multivibrator - Construct 555 IC as Mono-stable Multivibrator - Construct 555 IC as Bi-stable Multivibrator and verify its set and reset conduction |  |  |  |
| Module 3.14.11 Construct Shift Registers and Counters with The Help of Flip Flops |  | - Construct a 4 bit shift register by Using Flip Flops - Construct a4-bit binary counter Using Flip Flops - Construct 4-bitsynchronous Counter with D flip-Flops Troubleshoot - different combinational logic circuits. |  |  |  |
| Module 3.15.1 Implement Diode and Thyristor in Power Control Application |  | - Build forward bias circuit of diode and observe its behavior - Build reverse bias circuit of diode and observe its behavior - Use SCR to build Phase control rectifier - Build force commutated circuit for SCR - Build full wave converter and observe natural commutation |  |  |  |
| Module 3.15.2 Implement Single Phase and Three Phase Inverter |  | - Construct single phase half bridge inverter and observe its output - Construct single phase full bridge inverter and observe its output - Construct three phase bridge inverter and observe its output |  |  |  |
| Module 3.15.3 Control Speed of DC/AC Motors |  | - Implement armature control method to control the speed of DC motor with 3 phase control bridge Rectifier - Implement Field control method to control the speed of DC motor with 3 phase bridge rectifier - Implement Field control method & armature control method to control the speed of DC motor with 3 phase bridge rectifier. - Implement AC to AC converter to control the speed of 3 phase AC motor. - Implement single phase cycle-converter with center tapped transformer and SCR’s and change the frequency of output AC signal. - Implement synchros’s to transmit torque |  |  |  |
| Module 3.15.4 Program PLC using Ladder Logic |  | - Install PLC software and Simulator - Program a PLC using simulator |  |  |  |
| Module 3.15.5 Carry out Industrial Automation and PLC Installation |  | - Analyze user requirements and specifications for PLC installation - Prepare work plan for PLC Installation - Design and program PLC - Test the PLC - Ensure quality and productivity standards - Installation and Commissioning - Carry out maintenance of PLC |  |  |  |
| Module 3.15.6 Install PLC Software and Simulator |  | - Install PLC software and Simulator - Program a PLC using simulator - Analyze user requirements and specifications |  |  |  |
| Module 3.15.7 Design and Test the PLC |  | - Prepare work plan - Design and program PLC - Test the PLC |  |  |  |
| Module 3.15.8 Installation, Commissioning and Maintenance of PLC. |  | - Ensure quality and productivity standards - Installation and Commissioning - Carry out maintenance of PLC |  |  |  |
| Module 3.16.1 Identify the Parts of Analog & Digital Telephone Set & Verify their Function |  | - Dismantle and identify the parts of analog telephone set - Dismantle and identify the parts of digital telephone set - Demonstrate the operation of Telephone buzzer - Perform the operation of Transmitter & receiver - Identify the parts of rotary dial & verify its function - Identify the parts of digital dial& verify its function. |  |  |  |
| Module 3.16.2 Carry Out Modulation, Demodulation, Multiplexing, De Multiplexing of Information Signal |  | - Perform Amplitude Modulation of Information Signal - Perform Demodulation of Modulated AM Signal - Calculate band width and modulation index - Perform Frequency Modulation of Information Signal - Perform Demodulation of Modulated FM Signal - Perform Pulse Code Modulation (PCM) of an analog signal - Perform Time Division Multiplexing (TDM) and De-multiplexing - Perform Frequency Division Multiplexing and De-multiplexing |  |  |  |
| Module 3.16.3 Install Cord Less Telephone, PABX & Satellite Dish System. |  | - Install cord less telephone system - Install and Configure of Private Automatic Branch Exchange(PABX) - Install Home satellite dish system |  |  |  |
| Module 3.16.4 Install Power Supply |  | - Construct full wave rectifier/Bridge Rectifier - Construct filtered power supply - Construct Zener diode regulated power supply - Installation and Commissioning of Telecom Rectifier /UPS system - Installation of Valve Regulated Lead Acid Battery (VRLA) / Sealed Lead Acid Batteries (SLA) for Telecom Equipment - Conduct different Tests of VRLA/SLA Battery - Perform Maintenance Of Valve regulated lead Acid Battery |  |  |  |
| Module 3.16.6 Maintain Lead Acid Batteries and Implement Their Series Parallel Combination |  | - Construct series combination of batteries - Construct Parallel combination of batteries - Prepare Electrolyte for battery - Check specific gravity of Electrolyte - Determine internal resistance of cell - Charge the battery with the help of Charger |  |  |  |
| Module 3.17.1 Operate Hydro Power Plant |  | - Inspect Hydropower Plant equipment - Operate plant equipment. - Respond to equipment emergencies and alarms. - Perform maintenance activities. - Generate Report |  |  |  |
| Module 3.17.2 Operate Thermal Power Plant |  | - Carry out General Inspection of the Thermal power plant - Operate steam power plant - Inspect and Monitor Boiler Operation. - Inspect and Operate Ash handling plant - Inspect and Operate Coal Handling plant - Respond to equipment emergencies and alarms. - Perform maintenance activities. - Generate Report |  |  |  |
| Module 3.17.3 Operate Diesel Power Plant |  | - Inspect plant equipment. - Operate plant equipment. - Respond to equipment emergencies and alarms. - Perform maintenance activities - Generate Report |  |  |  |
| Module 3.17.4 Operate Nuclear Power Plant |  | - Carry out General Inspection of the equipment in Nuclear Power Plant - Operate Nuclear Reactor - Inspect and Monitor Water Cooling System in Nuclear Power Plant - Inspect Emergency power supply - Generate Report. |  |  |  |
| Module 3.17.5 Design a Solar Power Plant |  | - Ensure Personal safety - Calculate load for solar PV system design - Plan for installation of solar panel - Install the solar panel frame - Install the solar panel - Perform testing |  |  |  |
| Module 3.17.6 Operate Solar Power Plant |  | - Carry out General Inspection of the power plant - Operate solar plant equipment. - Respond to equipment - Perform maintenance activities. - Generate Report |  |  |  |
| Module 3.17.7 Operate Wind Power Plant |  | - Inspect plant equipment. - Operate plant equipment. - Respond to equipment emergencies and alarms. - Perform maintenance activities. - Generate Report |  |  |  |
| Module 3.17.8 Utilize Electrical Energy in Building |  | - Specify the requirements and characteristics of electrical heating systems. - Specify the requirements and characteristics of lighting system - Specify the requirements and characteristics of ventilation and air-conditioning systems |  |  |  |
| Module 3.17.9 Utilize Natural Energy in Building |  | - Design Natural lightning system - Design Natural Cooling and ventilation system - Design Natural heating system |  |  |  |
| Module 3.17.10 Calculate Tariffs and Economics |  | - Calculate Tariff for Hydro Power Plant - Calculate Tariff for Solar Power Plant - Calculate Tariff for Thermal Power Plant - Comparative Analysis |  |  |  |
| Module 3.18.1 Carryout Transmission of Electrical Power |  | - Select the Conductor for Transmission line - Sort different effects on transmission lines during conduction. - Select the right insulator from different types according to the requirement - Make Foundation and Erect poles and towers. - Perform stringing work and sag of Transmission lines - Install lightning arrester in a transmission system as per requirement |  |  |  |
| Module 3.18.2 Carryout Distribution of Electrical Power |  | - Select the Conductor for Distribution of power - Improve the Power factor - Select the correct insulator from different types according to the requirement - Make Foundation and Erect poles and structures - Supervise construction of Trenches ,Cable try and select appropriate cable - Perform stringing work and sag of distribution lines - Measure performance of distribution lines and take steps to improve Primary and secondary distribution. - Install the equipment for grounding of Substation/Transmission lines - Select and justify the use of reactor in a system - Install Lightning Arrester in a Distribution system as per requirement |  |  |  |
| Module 3.18.3 Carryout Protection of Distribution and Transmission System |  | - Categorize and rectify the symmetrical and asymmetrical faults - Install Circuit breaker in a distribution system (Substation/Grid station) - Install an isolator at grid station/sub station - Install appropriate relays for the protection of power system - Carry out Bus Bar protection - Carry out time graded protection of feeder - Install a fuse in a circuit (Transformer and Distribution panels) - Supervise Protection of power transformer - Carryout protection arrangement for alternator |  |  |  |

## Detail of Modules.

## Computer Operator (Electrical)

### Select Computer Specification and Work with Windows

Objective: This module covers the knowledge and skills required toidentify computer requirements and assembles procedures, Make a set of requirements for a personal computer, Use DOS to write a script, Work on windows, Environment and Install the required operating System with Device drivers.

Duration: 27	 Hours			Theory: 6 Hours				Practice: 21 Hours			Credit Hours: 2.7

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Identify computer requirements and assemble procedures | Trainee will be able to: - Select the hardware components of Computer. - Install the necessary plug-ins - Install the required computer software’s for operations of peripherals | - Identification of hardware peripheral - Installation techniques of hardware peripheral - Definition of Basic purpose of computer - Description of basic Components of computer. - Description of input and output devices. Practical Activity; Make connections of printer with system. | Total : 9 Hrs. Th. 2 Hrs. Practical: 7 Hrs. | - Keyboard - Printer - CPU - Monitor - DVDs,6,10,etc - Relevant software disks | Class Room and workshop |
| - Make a set of requirements for a personal computer | Trainee will be able to: - Arrange processer, RAM, Hard drive, Graphic card according to the requirement. - Identify requirements for a computer to run windows MS Office and Eclipse IDE | - Explanation of the different parts of a functions on present computer - Explanation of specification of processor RAM, Hard drive and Graphic card Practical Activity: Insert RAM according to system specification | Total. 9 Hrs. Th. 2 Hrs. Practical: 7 Hrs. | - Power cables - Tool kits and windows - Internet | Class Room and workshop |
| - Work on windows Environment and Install the required operating System with Device drivers. | Trainee must be able to: - Install and execute test of required Application Software’s. - Make the Ghost of Hard Disk / Partitions. - Apply the appropriate operation and execution of system as per standard - Perform loading and shutdown of operating system. - Create items (icons, shortcut, folders etc) and modifying taskbar. - Change the wallpaper, screensaver, and resolution. - Check the control panel items (add/remove, time and date, mouse, and create user | - Specification of processor RAM, Hard drive and Graphic cards - Explanation of DOS system - Explanation of the Commands used in Dos system Installation, Testing and inspection of operating system and their applications. Practical Activity: Install window 7 and update driver software. | Total: 9 Hrs. Th. 2 Hrs. Practical: 7 Hrs. | - Presentation manuals ,handout hardware ,equipment - Tool kits and Windows - Relevant Software Disks - Multimedia | Class Room and workshop |

### Process Data with MS Office

Objective: This module covers the  skills and knowledge required to Use MS Office (MS-Word), Use MS Office (MS-Excel), and use MS-Office (MS-Power Point).

Duration:  27 Hours				Theory: 6 Hours			Practice: 21 Hours			Credit Hours: 2.7

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Use MS OFFICE (MS-WORD) | Trainee will be able to: - Open the MS Word Screen and its menu. - Create a new document, save it and re-open it from the location and apply spell check & grammar. - Perform Page Formatting (Borders, Character Spacing, Paragraph, Bullets & Numberings and Fonts). - Apply different tool bars like standard, format& drawing tool bars. - Insert pictures, clipart, and shapes. - Use header and footer. - Insert table and also format of table. - Set the page margins, and printing documents. - Implement a lab report in MS word and insert table for measurement | - Definition of the basic input devices. - Function Of MS office - Description of the advance features. - Understanding of basic issues/problems related to rectification of computer operations Practical activity: - Type a report with heading size 22 font style time new roman ,text size 12,style Arial. - Design a format of daily attendance and set the margin lines and split the page. | Total : 9 Hrs. Th. 2 Hrs. Practical: 7 Hrs. | - MS OFFICE - PC | Class Room and workshop |
| LU2. Use MS OFFICE (MS-EXCEL) | Trainee will be able to: - Open the MS EXCEL Screen and its menu. - Create a new excel sheet, save and re-open it from the location and spell check. - Insert and delete row and columns (format of cell). - Apply Merge cell and wrap text command. - Change text size and formats - Check print previews and page setup - Set the page margins, and printing documents. - Make a lab report in MS word - Enter data and Apply formulas in worksheet(Add, Subtract, Multiplying, and Divide & Average) | - Identification of the basic input and out devices and their use. - Identification of basic hardware configuration required for software. - Understand detail knowledge of MS Excel functions. Practical Activity: Design result sheets of 10 students including Eng, Math, Urdu, science GK and apply formulas. - Find Average - Percentage each students. - Write grade according to percentage. | Total: 9 Hrs. Th. 2 Hrs. Practical: 7 Hrs. | - MS OFFICE - PC | Class Room and workshop |
| LU3. Use MS- OFFICE (MS-POWER POINT) | Trainee must be able to: - Open PPT - Select page theme and style - Make a presentation on Mechanical technology. - Select Edit & format a text box - Insert pictures & colors to a slide - Make slide show - Apply Hide and unhide a slide - Insert and delete new slide - Insert table and video in slide. - Use different style of Writing | - Understanding about the usage of Ready-made templates. - Understanding of advance features Practical Activity: Make a presentation on power point of Lathe machine Insert pictures ,text, and colors to a slide - Make slide show - Edit the slides - Apply hide and unhide formula - Insert table and videos. - Add time delay animation | Total : 9 Hrs. Th. 2 Hrs. Practical: 7 Hrs. | - MS OFFICE - PC | Class Room and workshop |

### Carryout Basic Programming

Objective: This module covers the knowledge and  skills required write a program to perform arithmetic operations, write a program in C++ to preparing logical operation, and write a program to sort a string of numbers.

Duration: 27 Hours				Theory: 6 Hours			Practice: 21 Hours			Credit Hours 2.7

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Make a program to perform arithmetic operations | Trainee will be able to: - Install eclipse or other IDE with C++ - Make a program that can take inputs from users and perform arithmetic operations like a calculator - Run the program and verify the results | - Definition of Arithmetic operations Practical Activity; How Old are you??? Design an age calculator | Total : 9 Hrs. Th. 2 Hrs. Practical: 7 Hrs. | - Keyboard - Printer - CPU - Monitor - DVDs,6,10,etc - Relevant software disks | Class Room and workshop |
| LU2. Make a program in C++ to preparing logical operation | Trainee will be able to: - Make a program that takes two numbers and decides which is bigger and which is smaller - Make a program that takes number of lights, fans in a house and calculate load | - understanding of Arithmetic and logical operations in C++ Practical Activity: Design a copy constructor by using C++. | Total : 9 Hrs. Th. 2 Hrs. Practical: 7 Hrs. | - Power cables - Tool kits and windows - Internet | Class Room and workshop |
| LU3 .Make a program to sort a string of numbers. | Trainee must be able to: - Make a script to take 10 numbers as input and display - Make a program to sort numbers in increasing order - Run the program and verify the results | - Definition of Loop operations in C++ Practical Activity: Calculate average of number using arrays | Total : 9 Hrs. Th. 2 Hrs. Practical: 7 Hrs. | - Presentation manuals, - handout Hardware Equipment - Tool kits and Windows - Relevant Software Disks Multimedia | Class Room and workshop |

### Perform Internet Browsing

Objective: This module covers the knowledge and  skills required todraw pin diagram of electronic IC using of search engine, Browse data sheets and symbols, Browse manuals

Duration: 24 Hours			Theory: 6 Hours				Practice: 18 Hours			Credit Hours: 2.4

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1.Draw pin diagram of electronic IC using of search engine | Trainee will be able to: - Open the Internet browser. - Identify various search engines - Open google.com and carry out searching related to course - Open Yahoo.com and carry out searching related to course - Open Ask.com and carry out searching related to course - Open Wikipedia.com and carry out searching related to course - Identify best search engine | - Understanding of search engine - Description of different types of search engine. - Identification of frequently use search engine. Practical Activity: Search electronic IC of OP-AMP with the help of Google .and draw the pin diagram on paper. | Total : 8 Hrs. Th. 2 Hrs. Practical: 6 Hrs. | - Tools - Computer - Internet connection. | Class Room and workshop |
| LU2 .Browse data sheets and symbols | Trainee will be able to: - Search data sheet of various electronic components from the Internet - Search various symbols of electrical components - Search the Electric design software - Prepare a report for the best software and their application | - Understanding of data sheets. - Understanding of symbols Practical Activity: Search the data sheet of OP-AMP,AND gate ,OR gate, ZENER diode | Total : 8 Hrs. Th. 2 Hrs. Practical: 6 Hrs. | - Tools - Computer - Internet connection | Class Room and workshop |
| LU3. Browse manuals | Trainee must be able to: - Search various manuals available on the internet related to course - Read the key terms - Clear your concepts from the manual. | - Definition of data sheets. Practical Activity Browse manual of Repair/ Maintenance and Service of Home Appliance and highlight the key terms by using appropriate search engine | Total : 8 Hrs. Th. 2 Hrs. Practical: 6 Hrs. | - Tools - Computer - Internet connection | Class Room and workshop |

### Perform the Different Engineering Curves Used in Various Mechanisms

Objective: This module covers the knowledge and  skills required to construct inscribe and circumscribe figures, Construct a pentagon, Hexagon and Octagon by circumscribe method, Construct a pentagon, Hexagon and Octagon by inscribe method, Construct a Tangents of circles (Inside & Outside)When the center of the given circle is known and when the circle of center is not known, Construct an Ellipse by Concentric Circle Method, Rectangle Method, Oblong Method, Arcs of Circle Method, Rhombus Method and Basic Locus Method, Construct a parabola curve by Rectangle Method, Method of Tangents( Triangle Method) and Basic Locus Method, Construct a hyperbola curve, Construct a Archimedean Spiral curve, Construct a involutes curve of square rectangle hexagon and circle and Construct of cycloid, epicycloids, and hypocycloid.

Duration:  30 Hours			Theory: 6 Hours			Practice: 24 Hours                   Credit Hours: 3.0

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Construct inscribe and circumscribe figures. | Trainee will be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in different equal parts. - Draw square, triangle and hexagon according to dimension. | Inscribe and circumscribe figures.. Practical Activity Construct inscribe and circumscribe figures. | Total 04 Hrs. Theory: 01Hrs. Practical: 03 Hrs | - Graph and drawing sheet - Drawing Board/Table - Tea-Square - Set Square - Temple - Geometry Box | Class Room and workshop |
| - Construct a pentagon, Hexagon and Octagon by circumscribe method. | Trainee will be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in different equal parts. - Draw pentagon, Hexagon and Octagon . | - Use circumscribe method to construct a pentagon, Hexagon and Octagon. Practical Activity Construct a pentagon, Hexagon and Octagon by circumscribe method. | Total 3.5 Hrs. Theory: 0.5 Hrs. Practical: 03 Hrs | - Graph and drawing sheet - Drawing Board/Table - Tea-Square - Set Square - Temple - Geometry Box | Class Room and workshop |
| - Construct a pentagon, Hexagon and Octagon by inscribe method | Trainee must be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in different equal parts. - Draw pentagon, Hexagon and Octagon. | - Use inscribe method to construct a pentagon, Hexagon and Octagon. Practical Activity Construct a pentagon, Hexagon and Octagon by inscribe method | Total 3.5 Hrs. Theory: 0.5 Hrs. Practical: 03 Hrs | - Graph and drawing sheet - Drawing Board/Table - Tea-Square - Set Square - Temple - Geometry Box | Class Room and workshop |
| - Construct a Tangents of circles (Inside &Outside) when the centre of the given circle is known and when the circle of centre is not known. | Trainee must be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in different equal parts. - Draw Tangents of circles | Mewthod to draw a Tangents of circles (Inside &Outside) when the centre of the given circle is known and when the circle of centre is not known. Practical Activity Construct a Tangents of circles (Inside &Outside) when the centre of the given circle is known and when the circle of centre is not known. | Total 2.5 Hrs. Theory: 0.5Hrs. Practical: 02 Hrs | - Graph and drawing sheet - Drawing Board/Table - Tea-Square - Set Square - Temple - Geometry Box | Class Room and workshop |
| - Construct an Ellipse by Concentric Circle Method, Rectangle Method, and Oblong Method, Arcs of Circle Method, Rhombus Method and Basic Locus Method. | Trainee must be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in different equal parts. - Draw an Ellipse. | - Different methods are used to construct an Ellipse. Practical Activity Construct an Ellipse by Concentric Circle Method, Rectangle Method, and Oblong Method, Arcs of Circle Method, Rhombus Method and Basic Locus Method. | Total 04 Hrs. Theory: 01Hrs. Practical: 03 Hrs | - Graph and drawing sheet - Drawing Board/Table - Tea-Square - Set Square - Temple - Geometry Box | Class Room and workshop |
| - Construct a parabola curve by Rectangle Method, Method of Tangents( Triangle Method) and Basic Locus Method | Trainee must be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in different equal parts. - Draw a parabola curve. | - Different methods are used to construct a parabola Practical Activity Construct a parabola curve by Rectangle Method, Method of Tangents( Triangle Method) and Basic Locus Method | Total 2.5 Hrs. Theory: 0.5Hrs. Practical: 02 Hrs | - Graph and drawing sheet - Drawing Board/Table - Tea-Square - Set Square - Temple - Geometry Box | Class Room and workshop |
| - Construct a hyperbola curve. | Trainee must be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in different equal parts. - Draw a hyperbola curve. | - Method to construct a hyperbola curve. Practical Activity Construct a hyperbola curve. | Total 2.5 Hrs. Theory: 0.5Hrs. Practical: 02 Hrs | - Graph and drawing sheet - Drawing Board/Table - Tea-Square - Set Square - Temple - Geometry Box | Class Room and workshop |
| - Construct a Archimedean Spiral curve | Trainee must be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in different equal parts. - Draw spiral curve. | - Method to construct a Archimedean Spiral curve Practical Activity Construct a Archimedean Spiral curve | Total 2.5 Hrs. Theory: 0.5 Hrs. Practical: 02 Hrs | - Graph and drawing sheet - Drawing Board/Table - Tea-Square - Set Square - Temple - Geometry Box | Class Room and workshop |
| - Construct a involutes curve of square rectangle hexagon and circle. | Trainee must be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in different equal parts. - Draw involute curve. | - Method to Construct a involutes curve of square rectangle hexagon and circle. Practical Activity Construct a involutes curve of square rectangle hexagon and circle. | Total 2.5 Hrs. Theory: 0.5 Hrs. Practical: 02 Hrs | - Graph and drawing sheet - Drawing Board/Table - Tea-Square - Set Square - Temple - Geometry Box | Class Room and workshop |
| - Construct of cycloid, epicycloids, and hypocycloid. | Trainee must be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in different equal parts. - Draw the generating circle and the base line equal to the circumference of the generating circle - Divide the circle and the base line in to equal number of parts - Draw by completing the cycloid. | - Method to construct a cycloid, epicycloids, and hypocycloid. Practical Activity Construct of cycloid, epicycloids, and hypocycloid.. | Total 2.5 Hrs. Theory: 0.5 Hrs. Practical: 02 Hrs | - Graph and drawing sheet - Drawing Board/Table - Tea-Square - Set Square - Temple - Geometry Box | Class Room and workshop |

### Perform Multi-View Drawings

Objective: This module covers the knowledge and  skills required toSketch Orthographic projection 1st angle, Sketch Orthographic projection 3rd angle, Sketch Oblique Drawing, Construct multi view drawing of Simple Bearing, Construct multi view drawing of Open Bearing, Sketch prism, Sketch cone and Draw pyramid.

Duration: 30 Hours			Theory: 6 Hours				Practice: 24 Hours			Credit Hours: 3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1.Sketch Orthographic projection 1st angle. | Trainee will be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in equal parts. - Draw plan view - Draw front view - Draw side view | - Definition of Orthographic projection 1st angle. Practical Activity: Draw a multi-view box in 1st angle projection | Total : 4 Hrs. Th. 1 Hr. Practical: 3 Hr. | - Graph and drawing sheet - Drawing board/table - Tea-square - Set square - Temples - Geometry | Class Room and workshop |
| LU2.Sketch Orthographic projection 3rd angle. | Trainee will be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in equal parts. - Draw plan view - Draw front view - Draw side view | - Definition of Orthographic projection 3rd angle. Practical Activity: Draw a multi-view box in 3rd angle projection | Total : 4 Hrs. Th. 1 Hr. Practical: 3 Hr. | - Graph and drawing sheet - Drawing board/table - Tea-square - Set square - Temples - Geometry | Class Room and workshop |
| LU3.Sketch Oblique Drawing | Trainee must be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in equal parts - Draw the front or side view of the object. | - Definition of Oblique Drawing. Practical Activity: Draw oblique with side and front view | Total : 4 Hrs. Th. 1 Hr. Practical: 3 Hr. | - Graph and drawing sheet - Drawing board/table - Tea-square - Set square - Temples - Geometry | Class Room and workshop |
| - Construct multi view drawing of Simple Bearing. | Trainee must be able to - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in equal parts. - Draw plan view of simple bearing - Draw front view of simple bearing - Draw side view of simple bearing | - Understanding of Multi view drawing of Simple Bearing. Practical Activity: Draw simple bearing with front , side and plan view | Total : 4 Hrs. Th. 1 Hr. Practical: 3 Hr. | - Graph and drawing sheet - Drawing board/table - Tea-square - Set square - Temples - Geometry | Class Room and workshop |
| - Construct multi view drawing of Open Bearing. | Trainee must be able to - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in equal parts. - Draw plan view of open bearing - Draw front view of open bearing - Draw side view of open bearing | - Identification of Multi view drawing of open Bearing. Practical Activity: Draw multi-view drawing of open bearing | Total : 4 Hrs. Th. 2 Hrs. Practical: 2 Hr. | - Graph and drawing sheet - Drawing board/table - Tea-square - Set square - Temples - Geometry | Class Room |
| - Sketch prism | Trainee must be able to - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in equal parts. - Sketch prism | - Definition of Prism Practical Activity: Draw prism | Total : 3 Hrs. Th. 1.5Hrs. Practical: 1.5 Hrs. | - Graph and drawing sheet - Drawing board/table - Tea-square - Set square - Temples - Geometry |  |
| - Sketch cone | Trainee must be able to - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in equal parts. - Draw horizontal oval - Draw the two sides of a triangle which meets at a common point | - Definition of cone - Definition of horizontal oval Practical Activity: Draw horizontal & oval cone | Total : 3 Hrs. Th. 2 Hrs. Practical: 1 Hr. | - Graph and drawing sheet - Drawing board/table - Tea-square - Set square - Temples - Geometry | Class Room and workshop |
| - Draw pyramid | Trainee must be able to - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Divide the sheets in equal parts. - Sketch pyramid | - Definition of pyramid Practical Activity: Draw pyramid | Total : 4 Hrs. Th. 1.5Hrs. Practical: 2.5 Hrs. | - Graph and drawing sheet - Drawing board/table - Tea-square - Set square - Temples - Geometry | Class Room and workshop |

### Draw Production Drawing

Objective: This module covers the knowledge and  skills required to draw the assembly drawing of Boiler Stop Valve, draw the views of Connecting Rod in detail and assembly drawing, draw the assembly drawing of Screw Jack and draw the assembly of Tail Stock in full section showing its parts.

Duration:24 Hours			Theory: 6 Hours				Practice: 18 Hours			Credit Hours: 2.4

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1.Draw the assembly drawing of Boiler Stop Valve | Trainee will be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Sketch the 1st angle orthographic projection views - Sketch the 3rd angle orthographic projection views - Sketch Assembly of boiler stop valve | - Parts and material of Boiler Stop Valve - Definition of 1stangle orthographic projection. - Definition of 3rd angle orthographic projection. Practical Activity: Draw the parts of boiler stop valve in assembly drawing | Total : 6 Hrs. Th. 1.5Hrs. Practical: 4.5 Hrs. | - Plotter - Multimedia projector - Computer - Scanner - Printer - Computer - Drafting table - Board - Portable drawing - Clutch pencil - Templates | Class Room and workshop |
| LU2.Draw the views of Connecting Rod in detail and assembly drawing | Trainee will be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Sketch the 1st angle orthographic projection views - Sketch the 3rd angle orthographic projection views - Sketch Assembly of connecting rod | - Parts of connecting rod - Definition of 1stangle orthographic projection. - Definition of 3rd angle orthographic projection Practical Activity: Draw the parts of connecting rod in 3rd angle orthographic projection | Total : 6 Hrs. Th. 1.5Hrs. Practical: 4.5 Hrs. | - Plotter - Multimedia projector - Computer - Scanner - Printer - Computer - Drafting table - Board - Portable drawing - Clutch pencil - Templates | Class Room and workshop |
| LU3.Draw the assembly drawing of Screw Jack | Trainee must be able to: - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Sketch the 1st angle orthographic projection views - Sketch the 3rd angle orthographic projection views - Sketch Assembly of screw jack | - Parts of screw jack - Definition of 1stangle orthographic projection. - Definition3rd angle orthographic projection Practical Activity: Draw the parts of screw jack in 3rd angle orthographic projection | Total : 6 Hrs. Th. 1.5 Hrs. Practical: 4.5 Hrs. | - Plotter - Multimedia projector - Computer - Scanner - Printer - Computer - Drafting table - Board - Portable drawing - Clutch pencil - Templates | Class Room and workshop |
| LU4.Draw the assembly of Tail Stock in full section showing its parts | Trainee must be able to - Prepare Drawing sheet. - Select the tools. - Draw Boundaries lines as per standards. - Make title bar - Sketch the 1st angle orthographic projection views - Sketch the 3rd angle orthographic projection views - Sketch Assembly of tail stock | - Parts of Tail Stock - Definition of 1stangle orthographic projection. - Definition of 3rd angle orthographic projection. Practical Activity: Draw the parts of screw jack in 3rd angle orthographic projection | Total : 6 Hrs. Th. 1.5 Hrs. Practical: 4.5 Hrs. | - Plotter - Multimedia projector - Computer - Scanner - Printer - Computer - Drafting table - Board - Portable drawing - Clutch pencil - Templates | Class Room and workshop |

### Design and Simulate the Electronic Circuit by Using Computer Aided Design (CAD) Software

Objective: This module covers the knowledge and  skills required to Analyse customer requirement and specification .Plan and Estimate Domestic electric work. Plan and estimate commercial   electric work and Plan and estimate industrial electric work.

Duration: 33 Hours			Theory: 3 Hours				Practice: 30 Hours			Credit Hours: 3.3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |  |
| --- | --- | --- | --- | --- | --- | --- |
| LU1.Analyze customer requirement and specification | Trainee will be able to: - Draw the general value chain of the end user. - Highlight the various stages and set of activities in the value chain drawing - Enlist the electrical appliances/materials required in electrical development process - Identify critical stages in the development - Identify the safety aspect required in the critical stages of the development - Enlist the possible energy efficient appliance/devices and global trends in electrical works - Analyse the client requirement at broad level. - Generate a report of various stages of electrical works. - Proposed appliance/materials as per global trends and clarify the technical specification. | - Understanding of the term ‘value chain’ of industry. - Standard operating procedure (SOP) of the organization for control panel development process. Practical activity: Analyze the customer requirement and generate a report on appliance used for development process | Total : 10 Hrs. Th. 1 Hrs. Practical: 09 Hrs. | - Tools - Site visit - Protective gear such as helmets, - Goggles - gloves, - Rubber - ,Shoes - Reference material - Clipboard - Calculation sheet - Calculator - Psychometric charts and tables |  | Class Room and workshop |
| LU2.Plan and estimate domestic electric work | Trainee will be able to: - Plan the client requirement at broad level from the proposal. - Plan the electrical appliances/materials / used in different stages of the electrical development process - Plan and estimate electrical wiring - Estimate Installation and Material Cost - Estimate Power consumption for lighting and appliances - Plan a main and sub distribution board. - Ensure safety system. | Understanding of human machine interface (HMI). Practical Activity: Plan and develop main and sub distribution board with its material estimated cost at domestic level | Total : 6.5 Hrs. Th. 0.5 Hrs. Practical: 6Hrs. | - Tools - Site visit - Protective gear such as helmets, - goggles, - gloves, - rubber - shoes - Reference material - Clipboard - Calculation sheet - Calculator - Psychometric charts and tables |  | Class Room and workshop |
| LU3.Plan and estimate commercial electric work. | Trainee must be able to: - Analyze the client requirement at broad level from the proposal. - Plan the electrical equipment /appliances/materials / used in different stages of the commercial electrical work - Plan and estimate electrical wiring - Estimate Installation and Material Cost - Estimate Power consumption for centralize lighting, heating, cooling system and other appliances. - Plan a main and sub distribution board. - Ensure safety measures in development process. - Enlist the material required | - Preparation of a General arrangement drawing? - Description of the standard of electrical components. Practical Activity: Plan and develop main and sub distribution board with its material estimated cost at commercial level | Total : 6.5 Hrs. Th. 0.5 Hrs. Practical: 6 Hrs. | - Tools - Site visit - Protective gear such as helmets, - goggles, - gloves, - rubber, - shoes - Reference material - Clipboard - Calculation sheet - Calculator - Psychometric charts and tables |  | Class Room and workshop |
| LU4.Plan and estimate industrial electric work. | Trainee must be able to - Analyze the client requirement at broad level from the proposal. - Plan the electrical equipment /appliances/materials / used in different stages of the commercial electrical work - Plan and estimate electrical wiring - Estimate Installation and Material Cost - Estimate Power consumption for centralize lighting, heating, cooling system and other appliances. - Plan 3-phase line for heavy loads - Plan a separate control panel box for heavy machinery. - Plan a main and sub distribution board. - Design a safety system for protection of machinery and labor. - Assign color scheme for safety measures | - Definition of IEC standards Practical Activity: Plan and develop main and sub distribution board with its material estimated cost at industrial level | Total : 10 Hrs. Th. 1 Hrs. Practical: 09 Hrs. | - Tools - Site visit - Protective gear such as helmets, - goggles, - gloves, - rubber, - shoes - Reference material - Clipboard - Calculation sheet - Calculator - Psychometric charts and tables |  | Class Room and workshop |

## DC Machine Operator

### Verify Basic Laws of Electrical Machines

Objective: This Module covers the skills and knowledge required to verify Faraday’s law by moving permanent magnet inside the coil, verify Faraday’s law by moving coil near the magnet field, verify Faraday’s law using relative motion of coil and magnet, verify Faraday’s Law using simple loop generator, verify EMF through induction, verify Torque induce in a current carrying loop and verify Mutual induction.

Duration: 27Hours			Theory: 06Hours				Practice: 21 Hours			Cr. Hour 2.7

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Verify Faraday’s law by moving permanent magnet inside the coil. | Trainee will be able to: - Construct a coil. - Connect Galvanometer with coil. - Move permanent magnet inside the coil fast and slow. - Record the effect of movement of magnet on reading of Galvanometer. - Hold the magnet inside the coil and do not move. - Record the effect on reading of Galvanometer again. | - Faraday’s Laws of Electro Magnetic induction. - Coil construction techniques - Definition of Lenz’s Law - Definition of Induction (Self & mutual) - Demonstration - Practicing | Th-01 Hrs. Pr-06 Hrs. Total-7 Hrs. | Galvanometer Coil core Winding Wire Bar magnet Magnetic compass | Class Room and workshop |
| - Verify Faraday’s law by moving coil near the magnet field | Trainee will be able to: - Construct a coil. - Connect Galvanometer with coil. - Fix permanent magnet and move the coil fast and slow on it. - Record the effect of movement of coil on reading of Galvanometer. - Hold the coil near the magnetic field and do not move. - Record the effect on reading of Galvanometer. | - Connection techniques of coil with Galvanometer - Procedure to find the direction of induced EMF - Fixing techniques of permanent magnet and moving the coil fast and slow on it. - Explanation of the Faraday’s first law of Electro-Magnetic Induction - Understanding of second law of Faraday - Use of Galvanometer - Demonstration - Practicing | Th-01 Hrs. Pr-03Hrs. Total- 4 Hrs. | Galvanometer Coil core Winding Wire Bar magnet Magnetic compass | Class Room and workshop |
| - Verify Faraday’s law using relative motion of coil and magnet. | Trainee must be able to: - Construct a coil. - Connect Galvanometer with coil. - Make relative motion of coil and magnet. - Record the effect of movement on reading of Galvanometer | - Techniques to find the direction of induced EMF? - Recording techniques for the effects of movements on reading of Galvanometer - Demonstration - Practicing | Th-0 1Hrs. Pr-03 Hrs. Total- 4 Hrs. | Galvanometer Coil core Winding Wire Bar magnet Magnetic compass | Class Room and workshop |
| - Verify Faraday’s Law using simple loop generator. | Trainee must be able to: - Identify single loop generator and its parts. - Select field winding. - Connect Galvanometer with single loop coil. - Rotate the single loop coil of generator in the field - Measure the voltage induced in loop generator. - Record the effect of movement on reading of Galvanometer. | - Role of magnetic strength in Faraday’s Law - Understanding the Effects of coupling coils - Definition of Self induction - Definition of Mutual Induction - Demonstration - Practicing | Th-01 Hrs. Pr-03 Hrs. Total- 4 Hrs. | Simple loop generator Galvanometer Voltmeter Oscilloscope | Class Room and workshop |
| - Verify Torque induce in a current carrying loop | Trainee must be able to - Construct a coil. - Apply DC voltage to this coil. - Place a current carrying loop in this coil. - Check the direction of force to verify the torque produce. | - Definition of Core - Definition of Torque - Working principles of mutual Induction - Checking techniques of Torque direction - Demonstration - Practicing | Th-01 Hrs. Pr-03 Hrs. Total- 4 Hrs. | Galvanometer Coil core Winding Wire Bar magnet Magnetic compass DC voltage source Ammeter | Class Room and workshop |
| - Verify Mutual induction | - Construct 2 coils on two different legs of single core. - Apply AC voltage to the any one coil. - Check the volts induce in other coil by voltmeter. | - Effects of force produced on current carrying conductor - Causes of EMF induced in 2nd coil, when voltage is applied to 1st coil. - Role of conductor’s length or turns in Faraday’s Law - Demonstration - Practicing | Th-01 Hrs. Pr-03 Hrs. Total- 4 Hrs. | Galvanometer Coil core Winding Wire Bar magnet Magnetic compass AC voltage source Voltmeter | Class Room and workshop |

### Analyze DC Generators

Objective: This Module identifies the competencies required to calculate different terms used in armature winding of DC machines, develop Single Layer Lap Winding, develop Double Layer Wave Winding, measure the resistance of field winding, armature winding and terminal polarity, identify DC shunt generator, identify DC series generator and identify DC compound generator.

Duration: 27 Hours			Theory: 6Hours				Practice: 21Hours			Cr, Hour 2.7

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Calculate different terms used in armature winding of DC machines. | Trainee will be able to: - Count the number of slots (S) of armature. - Calculate pole pitch (Y). - Calculate Coil span/pitch. - Calculate Back pitch (Yb) - Calculate Front pitch (Yf) - Calculate Resultant Pitch (YR) - Calculate commentator pitch (Yc) | - Understanding of Pole, span, back, resultant and commutation pitch. - Calculation techniques of various pitches - Calculation - Practicing | Th-1 Hrs. Pr-3 Hrs. Total- 4 Hrs. | Graph paper Rubber Pencil Armature core | Class Room and workshop |
| - Develop Single Layer Lap Winding | Trainee will be able to: - Count the number of slot in armature core and numbering on it. - Calculate total number of conductors (Z) - Calculate average pitch, back pitch and commentator pitch. - Start winding from slot no 1. - Add the value of back pitch in conductor. - Connect conductor 1 from back side to the added value. - Subtract the value of back pitch from the added value. - Connect added value from front side to subtracted value. - Continue this process till completion of all conductors. - Connect armature segment with armature conductor. - Insert brushes in proper position. | - Definition of various types of Windings - Definition of single and double layer windings - Definition of Armature - Understanding of parallel paths in lap winding - Counting techniques for counting the slots of Armature - Connection techniques of armature segment with armature conductor. - Insertion techniques of brushes in proper position. - Development of Lap winding on graph paper | Th-1 Hrs. Pr-3 Hrs. Total- 4 Hrs. | Armature core Armature coils Commutator Armature Carbon brush Carbon brush holder Rocker | Class Room and workshop |
| - Develop Double Layer Wave Winding. | Trainee must be able to: - Count the number of slot in armature core and numbering on it. - Calculate total number of conductors (Z) - Calculate average pitch, back pitch and commentator pitch. - Start winding from slot no 1. - Add the value of back pitch in conductor. - Connect conductor 1 from back side to the added value. - Add the value of front pitch in previous added value. - Continue this process till completion of all conductors. - Connect armature segment with armature conductor. - Insert brushes in proper position. | - Definition of wave winding - Definition of parallel path in wave winding - How the value of front pitch added in previous value - Pitch calculation techniques - Procedure for development of windings - Technique to identify the terminal polarity - How to disconnect both winding of shunt generator - Types of windings in series Generator - Development of wave winding on graph paper | Th-01 Hrs. Pr-03 Hrs. Total- 4 Hrs. | Graph paper Pencil Rubber | Class Room and workshop |
| - Measure the resistance of field winding, armature winding and terminal polarity | Trainee must be able to - Open the terminal box. - Connect the ohm meter with the terminal of both winding. - Read down ohm meter reading. - Connect the probe of galvanometer with any terminal and touch other probe to other terminals one by one. - Rotate the generator slowly by hand. - Touch the probe of galvanometer with each winding. - Identify armature with the deflection of galvanometer pointer. - Mark the polarity of terminals with the deflection of galvanometer. | - Define terminal Box - Opening techniques of terminal Box - How to disconnect both winding of shunt generator - How many winding in series generator? - Explain the technique to identify the terminal polarity - Identification of armature with the deflection of galvanometer pointer - Marking procedure for the polarity of terminals with the deflection of galvanometer. - Demonstration - Practicing | Th-01 Hrs. Pr-03 Hrs. Total- 4 Hrs. | Ohm meter DC machine Galvanometer Tool Box AVO meter | Class Room and workshop |
| - Identify DC shunt generator | Trainee must be able to - Measure the terminal resistance of generator with ohm meter. - Identify DC shunt generator from measured value of resistance - Disconnect both windings. - Identify the shunt field winding of shunt generator. - Identify armature of shunt generator. - Measure the resistance of both winding separately. - Record the resistance of armature winding and field winding. - Compare the resistance of armature winding and field winding to identify the difference between them. | - Define the Type of DC machines - Explain rules of generators. - Explain the principle of simple loop generator. - How many winding in shunt generator? - Comparison techniques of the resistance of armature winding and field winding to identify the difference between them. - Measurement techniques for the resistance of both winding separately - Demonstration - Practicing | Th-1/2 Hrs. Pr-3 Hrs. Total-3.5 Hrs | Ohm meter DC machine Galvanometer Tool Box AVO meter | Class Room and workshop |
| LU6. Identify DC series generator | - Measure the terminal resistance of generator with ohm meter. - Identify DC series generator from measured value of resistance - Disconnect both windings. - Identify the series field winding of series generator. - Identify armature of series generator. - Measure the resistance of both winding separately. - Record the resistance of armature winding and field winding. - Compare the resistance of armature winding and field winding to identify the difference between them. | - Identification of DC series generator from measured value of resistance - Measurement procedure for the terminal resistance of generator with ohm meter. - Technique to identify the terminal polarity - Demonstration - Practicing | Th-1/2 Hrs. Pr-03 Hrs. Total-3.5 Hrs | Ohm meter DC machine Galvanometer Tool Box AVO meter | Class Room and workshop |
| LU7. Identify DC compound generator | - Measure the terminal resistance of generator with ohm meter. - Identify DC Compound generator from measured value of resistance. - Disconnect both windings. - Identify the series field winding of generator. - Identify the shunt field winding of generator. - Identify armature of shunt generator. - Measure and record the resistance of both winding separately. - Measure and Record the resistance of armature winding. - Compare the resistance of armature winding, series field winding and shunt field winding to identify the difference between them. | - Define a compound Generator. - Identification of various types of winding having low resistance and why? - Identification of various types of winding. - Identification of DC Compound generator from measured value of resistance - Procedure for disconnection of both winding of Generator - Demonstration - Practicing | Th 01 Hrs. Pr-3 Hrs. Total-4 Hrs. | Ohm meter DC machine Galvanometer Tool Box AVO meter | Class Room and workshop |

### Perform Tests on DC Generators

Objective: This Module identifies the competencies required to Plot the Open circuit characteristics of a Separately excited D.C  generator, plot the Open circuit characteristics of a D.C shunt generator, plot the load characteristics of D.C shunt generator, plot the load characteristics of D.C series generator, plot the load characteristics of D.C compound generator for under, flat and over compounding, perform parallel operation of two DC shunt generators and determine copper, iron & friction losses of shunt generator by actual loading.

Duration: 30 Hours			Theory: 6Hours				Practice: 24Hours			Cr. Hour 3.0

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Plot the Open circuit characteristics of a Separately excited D.C generator | Trainee will be able to: - Connect DC supply to field coil through rheostat and ampere meter. - Rotate armature at constant speed. - Connect voltmeter across armature terminal. - Decrease the resistance of rheostat in steps and measure and record the relevant output voltage of armature and field current. - Repeat the P2 to P4 till voltage of armature reach at its saturation point. - Plot the graph between field current and armature voltage from the recorded values | - Define rheostat? - Use rheostat with field winding - Explain core saturation - Explain the effect of rheostat resistance on terminal voltage. - Explain that why the graph between field current and armature voltage is not a straight line - Demonstration - Practicing - Plotting curve on graph paper | Th-01 Hrs. Pr-04 Hrs. Total- 5 Hrs. | DC machine DC supply Tool Box AVO meter Voltmeter Ammeter Rheostat Graph paper Pencil Rubber | Class Room and workshop |
| LU2. Plot the Open circuit characteristics of a D.C shunt generator | Trainee will be able to: - Connect DC supply to field coil through rheostat and ampere meter. - Rotate armature at constant speed. - Connect voltmeter across armature terminal. - Decrease the resistance of rheostat in steps and measure and record the relevant output voltage of armature and field current. - Repeat the P2 to P4 till voltage of armature reach at its saturation point. - Plot the graph between field current and armature voltage from the recorded values. | - Describe the procedure for Connection of DC supply to field coil through rheostat and ampere meter - Define the armature reaction - Explain the reason of voltage reduce due to increase in load. - Techniques of graph plotting between field current and armature voltage from the recorded values - Demonstration - Practicing - Plotting OCC on graph paper | Th-1/2 Hrs. Pr-04 Hrs. Total-4.5Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Graph paper Pencil Rubber | Class Room and workshop |
| LU3. Plot the load characteristics of D.C shunt generator | Trainee must be able to - Select DC shunt generator and connect variable load. - Connect ampere meter and voltmeter across the load. - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. | - Define DC shunt generator - Connection techniques of variable load with Generator - Techniques of graph plotting between field current and armature voltage from the recorded values - Explain the reason of voltage reduce due to increase in load. - Techniques for observation of the specific reduce in terminal voltage - Demonstration - Practicing - Plotting curve on graph paper | Th-1/2 Hrs. Pr-3 Hrs. Total-3.5Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Variable Load Graph paper Pencil Rubber | Class Room and workshop |
| LU4. Plot the load characteristics of D.C series generator. | Trainee must be able to - Select DC series generator and connect variable load. - Connect ampere meter and voltmeter across the load. - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. | - Identification of DC series Generator. - Working of DC series Generator. - Connection techniques of variable load - Techniques for observation of the specific reduction in terminal voltage - Demonstration - Practicing - Plotting curve on graph paper | Th-1 Hrs. Pr-3 Hrs. Total- 4 Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Variable Load Graph paper Pencil Rubber | Class Room and workshop |
| LU5. Plot the load characteristics of D.C compound generator for under, flat and over compounding | - Select DC compound generator and connect variable load. - Connect ampere meter and voltmeter across the load. - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. - Adjust field diverter on zero ohm. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. - Such off the load. - Adjust the field diverter at such position that the terminal voltages are equal to no load voltages. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. - Such off the load. - Adjust the field diverter at such position that the terminal voltages are greater than no load voltages. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. | - Identification of DC Compound Generator. - Working of DC compound generator - Connection techniques of field and armature winding in compound generator - Explain under and over compounding. - Adjustment techniques for field diverter on zero ohm. - Definition of switching off the load - Adjustment procedure for setting of the field diverter at such position that the terminal voltages are equal to no load voltages - Demonstration - Plotting of graph - Practicing | Th-1 Hrs. Pr-4Hrs. Total- 5 Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Variable Load Graph paper Pencil Rubber | Class Room and workshop |
| LU6. Perform parallel operation of two DC shunt generators. | - Connect the circuit according to the circuit diagram. - Place all switches in off position. - Run generator 1 at rated speed. - Reduce field resistance of generator 1 - Connect generator with bus bar after attaining rated voltage. - Run generator 2 with prime mover. - Reduce the field resistance of generator 2 to attain its rated voltage. - Close the switches for parallel operation. - Calculate and record the reading of voltage and current on different loads. | - Conditions of paralleling of DC generators. - Necessity of connecting DC generators in parallel. - Iron loss - Copper loss - Variation in copper loss with loads - Demonstration - Practicing | Th-01 Hrs. Pr-03 Hrs. Total- 04Hrs. | DC machines Tool Box AVO meter Voltmeters Ammeters Rheostats Variable Load | Class Room and workshop |
| LU7. Determine copper, iron & friction losses of shunt generator by actual loading. | - Connect ammeter in series with both winding. - Connect voltmeter in parallel with both winding. - Apply 10-20 DC volt. - Record the readings of voltmeter and ammeter. - Calculate Ra and Rsh. - Run the generator at rated speed with prime mover. - Turn on the load switch and record the meter reading. - Calculate input power and output power. - Calculate total losses (Copper loss, Friction loss, Iron loss) | - Connection techniques of Ammeter and Voltmeter with both the windings. - Define Iron loss - Define copper loss - Explain why the copper loss happens at full load - Calculation of Ra and Rsh. - Running the generator at rated speed with prime mover. - Turn on the load switch and record the meter reading. - Calculation input power and output power. - Calculation of efficiency | Th-01 Hrs. Pr-03 Hrs. Total- 04Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Wattmeter Variable DC supply Graph paper Pencil Rubber | Class Room and workshop |

### Analyze DC Motor

Objective: This module identifies the competencies required to identify DC shunt motor, identify DC series motor and identify DC compound motor.

Duration: 27 Hours			Theory: 6Hours				Practice: 21Hours			Cr, Hour 2.7

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify DC shunt motor | Trainee will be able to: - Measure the terminal resistance of motors with ohm meter. - Identify DC shunt motor from measured value of resistance. - Disconnect both windings. - Identify field winding of shunt motor. - Identify armature of shunt motor. - Measure the resistance of both winding separately. - Record the resistance of armature winding and field winding. - Compare the resistance of armature winding and field winding to identify the difference between them. | - Types of DC machines - Identification of DC shunt motor from measured value of resistance - Measuring techniques of resistance with Ohm’s meter - Identification of field winding of shunt motor. - Identification of armature of shunt motor - The difference between field winding and armature winding - Connection /disconnection techniques of both winding of series generator. - Demonstration - Practicing | Th-02 Hrs. Pr-09 Hrs. Total-11Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Galvanometer Ohm Meter | Class Room and workshop |
| LU2. Identify DC series motor | - Trainee will be able to: - Measure the terminal resistance of DC motors with ohm meter. - Identify DC series motor from measured value of resistance. - Disconnect both windings. - Identify the series field winding of series motor. - Identify armature of series motor. - Measure the resistance of both winding separately. - Record the resistance of armature winding and field winding. - Compare the resistance of armature winding and field winding to identify the difference between them. | - DC Series Motor - Identification of DC series motor from measured value of resistance. - Connection /disconnection techniques of both winding of series motor - Identification of armature of series motor. - Measurement techniques for the resistance of both winding separately. - Recording procedure for the resistance of armature winding and field winding. - Compare of the resistance of armature winding and field winding to identify the difference between them. - Demonstration - Practicing | Th-02 Hrs. Pr-06 Hrs. Total- 8Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Galvanometer Ohm Meter | Class Room and workshop |
| LU3. Identify DC compound motor | - Trainee must be able to - Measure the terminal resistance of DC motor with ohm meter. - Identify DC Compound motor from measured value of resistance. - Disconnect both windings. - Identify the series field winding of motor. - Identify the shunt field winding of motor. - Identify armature of compound motor. - Measure and record the resistance of both winding separately. - Record the resistance of armature winding. - Compare the resistance of armature winding, series field winding and shunt field winding to identify the difference between them. | - DC Compound Motor - Identification of DC compound motor from measured value of resistance. - Connection /disconnection techniques of both winding of Compound motor - Identification of the field winding of the motor. - Identification of the series field winding of motor. - Identification of the shunt field winding of motor. - Identification of the armature of compound motor. - Comparison of the resistance of armature winding and field winding to identify the difference between them. - Demonstration - Practicing | Th-02 Hrs. Pr-06 Hrs. Total- 8 Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Galvanometer Ohm Meter | Class Room and workshop |

### Perform Tests on DC Motors.

Objectives: This Module identifies the competencies required to Plot the load characteristics of D.C shunt motor, plot the load characteristics of D.C series motor, plot the load characteristics of D.C compound motor, control the speed of DC series motor, control the speed of DC shunt motor, start  DC shunt motor with 3 point starter, identify the effect of back EMF in DC motor, calculate BHP of motor by Brake test, calculate efficiency of the motor by Swinburne Test and perform Regenerative / Hopkinson/ Back to back Test.

Duration: 30 Hours				Theory: 6Hours			Practice: 24Hours			Cr. Hour 3.0

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Plot the load characteristics of D.C shunt motor | Trainee will be able to: - Couple electro dynamo meter to the DC motor with belt - Connect shunt motor according to the diagram. - Set the dynamo meter control knob in such position to produce a minimum starting load. - Turn on the power supply - Run the motor at rated RPM. - Apply a load to DC motor by varying the dynamo meter control knob. - Measure and calculate the current, speed and torque. - Plot the load characteristics on DC shunt motor.. | - Dynamo meter - Coupling procedure electro dynamo meter to the DC motor with belt. - Setting techniques of dynamo meter control knob in such position to produce a minimum starting load. - Measurement and calculation of current - Procedure for plotting the load characteristics on DC shunt motor - Demonstration - Practicing | Th-1/2 Hrs. Pr-2.5 Hrs. Total- 3 Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Dynamometer Tachometer Variable Load | Class Room and workshop |
| LU2. Plot the load characteristics of D.C series motor. | - Trainee will be able to: - Select DC series motor and achieve connection as per diagram. - Turn on DC power supply and increase the load to full value. - Record the value of speed and current on each load. - Draw the graph between load current and speed | - DC series Motor - Why series winding having low turns and shunt winding having high number of turns - Why do we never start DC series motor without load? - Demonstration - Practicing | Th-1/2 Hrs. Pr-1.5 Hrs. Total- 2 Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Dynamometer Tachometer Variable Load | Class Room and workshop |
| LU3. Plot the load characteristics of D.C compound motor | - Trainee must be able to: - Connect compound motor according to the diagram. - Set the dynamo meter control knob in such position to produce a minimum starting load. - Turn on the power supply - Run the motor at rated RPM. - Apply a load to DC motor by varying the dynamo meter control knob. - Measure and calculate the current, speed and torque. - Plot the load characteristics on DC compound motor. | - Compound Motor - Connection techniques of compound motor according to the diagram. - Definition of RPM - Measurement and calculation of the current, speed and torque - Demonstration - Practicing - Plotting of curve | Th-1/2 Hrs. Pr-2 Hrs. Total- 2.5 Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Dynamometer Tachometer Variable Load | Class Room and workshop |
| LU4. Control the speed of DC series motor. | - Make the connection as per circuit diagram. - Insert external resistances in series to armature and field coil. - Switch on the supply and increase the voltage gradually to its rated voltage. - Record speed at different supply voltages. - Make graph between speed and applied voltage. | - DC series Motor - Speed control of DC motor with applied voltage. - Effect of motor speed on back EMF - Demonstration - Practicing - Preparation of graph between speed and applied voltage | Th-1/2 Hrs. Pr-2.5 Hrs. Total- 3 Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Dynamometer Tachometer Variable DC supply Graph Paper Pencil Rubber | Class Room and workshop |
| LU5. Control the speed of DC shunt motor. | - Make the connection as per circuit diagram. - Switch on the supply and increase the voltage gradually to its rated voltage. - Record speed at different field current. - Make graph between speed and field current - Fixe the field current and very armature current - Record the speed at different armature current. - Make graph between speed and armature current | - DC shunt Motor - Techniques used used to to to control the speed of DC shunt motor - Role of DC motor starter. - Procedure for Fixing the field current and varying armature current - Demonstration - Practicing - Preparation of speed and current relation graph | Th-1/2 Hrs. Pr-3 Hrs. Total- 3.5 Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Dynamometer Tachometer Variable DC supply Graph Paper Pencil Rubber | Class Room and workshop |
| LU6. Start DC shunt motor with 3 point starter. | - Make the connection as per circuit diagram. - Switch on the supply and move starter handle from off position to position 1. - Move the starter arm from position 1 to position 2 and continue this process till starter arm reach at its extreme position. | - Working of 3-point starter - Techniques to control the speed of DC shunt motor - Demonstration - Practicing | Th-1/2 Hrs. Pr-3 Hrs. Total- 3.5 Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat 3 point starter Tachometer Variable DC supply Graph Paper Pencil Rubber | Class Room and workshop |
| LU7. Identify the effect of back EMF in DC motor | - Select DC series motor and make connection as per diagram. - Turn on DC power supply and increase the load 0 to full value. - Record the value of speed and current on each load. - Calculate back EMF by using the recoded values and appropriate formula. - Make graph between speed and back EMF and interpret the result. | - Definition of back EMF - Effect of motor speed on back EMF - Calculation of Back EMF - Demonstration - Practicing - Making of graph between speed and back EMF and interpretation of result | Th-1/2 Hrs. Pr-1.5 Hrs. Total- 2 Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Dynamometer Tachometer Variable DC supply Variable Load Graph Paper Pencil Rubber | Class Room and workshop |
| LU8. Calculate Brake Horse Power (BHP) of motor by Brake test. | - Connect the spring balance with one end of the rope. - Connect other end of rope with weight (W1). - Measure the radius of the pulley. - Hang the weight on the pulley of the motor and fix the spring balance end with earTheory: - Run the motor. - Measured the RPM of the motor. - Adjust the weight to pass full load current from motor. - Calculate spring balance weight and hanged weight (W1) - Calculate shaft torque. - Calculate BHP of motor by shaft torque. | - Definition of Brake Horse Power (BHP) - Definition of shaft torque - Connection procedure of spring balance and rope with weight - Measurement of RPM of the motor - Calculation of BHP from shaft torque - Demonstration - Practicing | Th-1/2 Hrs. Pr-02Hrs. Total- 2.5 Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Rheostat Dynamometer Tachometer Variable DC supply Brake Test Equipment | Class Room and workshop |
| LU9. Calculate efficiency of the motor by Swinburne Test | - Perform DC test to find the value of armature resistance and field resistance - Run the motor at rated voltage without load. - Adjust the value of shunt regulator to attain rated speed. - Measure Field current and No load current with ampere meter. - Calculate total copper losses and iron losses. - Calculate input and output power. - Calculate efficiency from calculated power. | - Procedure to perform DC test to find the value of armature resistance and field resistance - Adjustment techniques of the value of shunt regulator to attain rated speed. - Calculation of Field current and no load current with ammeter. - Calculation of total copper losses, iron losses, input and output power - Demonstration - Practicing | Th-1 Hrs. Pr-3 Hrs. Total- 4 Hrs. | DC machine Tool Box AVO meter Voltmeter Ammeter Wattmeter Rheostat Dynamometer Tachometer Variable DC supply Graph Paper Pencil Rubber | Class Room and workshop |
| LU10.Perform Regenerative / Hopkinson/ Back to back Test | - Identify two shunt machines. - Couple the shafts of both machines. - Connect the machines electrically in such a way that one machine work as a motor and other as a generator. - Connect external power supply to the machines to overcome the machine losses. - Run the both machine at no load. - Reduce the field excitation of one machine which works as a motor. - Increase the field excitation of one machine which work as a generator. - Adjust the field winding so that voltage of generator becomes equal to the applied voltage which result the machines runs in parallel - Calculate the efficiency by using reading of voltmeter and ammeter. | - Coupling techniques for the shafts of both machines. - Connection procedure for the machines electrically in such a way that one machine work as a motor and other as a generator - Adjustment procedure for the field winding so that voltage of generator becomes equal to the applied voltage which result the machines runs in parallel - Field excitation - Demonstration - Practicing | Th-1 Hrs. Pr-3 Hrs. Total- 4 Hrs. | 2 DC machine mechanically coupled Tool Box AVO meter Voltmeter Ammeter Rheostat Dynamometer Tachometer Variable DC supply 4 point DC Starter | Class Room and workshop |

### Repair/Maintenance and servicing of DC Motors and DC Generator

Objectives: This Module identifies the competencies required to Diagnose Fault in DC Motor, carry out Service/Repair in Electric Motor, and carry out Preventive Service / Maintenance of Generators and Diagnose and Repair Electric Generator carry out repair and maintenance of DC motors and generators in accordance with the manufacturer’s instructions. The underpinning knowledge regarding repair and maintenance of electrical DC motor & generators will be sufficient to provide the basis for your work.

Duration: 30Hours			Theory: 6Hours				Practice: 24Hours			Cr. Hour 3.0

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Diagnose Fault in DC Motor | Trainee will be able to: - Identify the type of electric motor from data / name plate or manual and motor ratting. - Perform Methods of dismantling and assembling DC motor - Inspect visual mechanical defect such as, tight bearings, bent shaft, noisy running, short circuit, and temperatures. - Check the motor by using specified test instruments to detect electrical defects such as loose/or burnt electrical connections, burnt windings, low insulation resistance. - Test short circuit, circuit break, earth fault, wiring fault, bearing fault. - Perform replacing of bearing - Identify the faults of a DC motor and repair them according to procedures. - Rewind a DC motor - Check the tripping of protective device using specified test instruments, while the motor is running with power supply connected with suitable control and protective device, the difficulty in starting/low RPM/ unusual noises/ excessive heat/ / grounded winding etc. | - Identification of the type of electric motor from data / name plate or manual and motor ratting. - Working principal of D.C generator. - Techniques of disassembling assembling of DC motor - Procedure for Inspection of visual mechanical defect such as, tight bearings, bent shaft, noisy running, short circuit, and temperatures. - Checking of motor by using specified test instruments to detect electrical defects such as loose/or burnt electrical connections, defective capacitors, burnt windings, low insulation resistance. - Test short circuit, circuit break, earth fault, wiring fault, bearing fault. - Perform replacing of bearing - Faults detection and repairing techniques of a DC motor - Rewinding techniques of a DC motor - Procedure for Checking of the tripping of protective device using specified test instruments, while the motor is running with power supply connected with suitable control and protective device, the difficulty in starting/low RPM/ unusual noises/ excessive heat/ / grounded winding etc. - Demonstration - Practicing | Th-1 Hrs. Pr-3 Hrs. Total- 4 Hrs. | DC Faulty Machine Rust removing agents Tool Box AVO Meter Megger Volt Meter Wattmeter Ammeter Variable supply Rewinding Machine | Class Room and workshop |
| LU2. Carry out Service / Repair in Electric Motor | - Trainee will be able to: - Repair the motor as per diagnosed fault - Assemble the electric motor for internal tests/servicing/repairs according to manufacturer’s instructions - Clean the parts of the motor with specified cleaning agents/tools & material - Check the windings insulation resistance with insulation tester - Rewind the motor as per requirement - Check the insulation resistance of repaired motor as per standard - Carry out the No load and load tests as per standard practices | - Cleaning techniques for the parts of motor - Identification of specified cleaning agents/tools & material - Use of insulation Tester - Conduct of the No load and load tests as per standard practices - Procedure of rewinding of motor - Demonstration - Practicing | Th-2 Hrs. Pr-10Hrs. Total- 12 Hrs. | DC Faulty Machine Rust removing agents Tool Box AVO Meter Megger Volt Meter Wattmeter Ammeter Variable supply Rewinding Machine | Class Room and workshop |
| LU3. Carry out Preventive Service/ Maintenance of Generators | - Trainee must be able to - Carry out routine maintenance of the generator as specified in the manufacturer’s manual - Check out the switch/ timer, relay, protective device and wire connection - Update the maintenance/service records | - Common faults found in electric motors / generators and troubleshooting methods - Scheduled / preventive maintenance / servicing - Identification of the parts of machine requires servicing/ maintenance - Identification of the required tool/equipment and materials - Servicing/ maintenance techniques - Demonstration - Practicing | Th-1 Hrs. Pr-3 Hrs. Total- 4 Hrs. | DC Faulty Machine Rust removing agents Tool Box AVO Meter Megger Volt Meter Wattmeter Ammeter Variable supply Rewinding Machine | Class Room and workshop |
| LU4. Diagnose and Repair Electric Generator | - Dismantle the electric Generator for internal tests/servicing/repairs according to manufacturer’s instructions - Clean the parts of the generator with specified cleaning agents/tools & material - Check the control equipment of generators. - Find out the root cause of fault according to the signs of fault by applying the working principles of control equipment of generators: Speed controller, Magnetic field control circuit and equipment of the generator. - Check Load regulator of the generator and its control circuit. - Control circuit of the auxiliary generator. - Check Control circuit of the battery unit - Check Circuit breaker and relay. - Repair the fault after finding out the faulty equipment or component | - Working principles of D.C generator. - Faults detection techniques - Interpretation of the machine manual for its servicing/ maintenance - Techniques of dissembling of Machine - Demonstration - Practicing | Th-2 Hrs. Pr-8Hrs. Total- 10 Hrs. | DC Faulty Machine Rust removing agents Tool Box AVO Meter Megger Volt Meter Wattmeter Ammeter Variable supply Rewinding Machine | Class Room and workshop |

## Transformer Winding Supervisor

### Verify Basic Laws of Electrical Machines

Objective: This module covers the knowledge and  skills required to verify Faraday’s law by moving permanent magnet inside the coil, verify Faraday’s law by moving coil near the magnet field, verify Faraday’s law using relative motion of coil and magnet, verify Faraday’s Law using simple loop generator, verify Torque induce in a current carrying loop and verify Mutual induction.

Duration: 24 Hours			Theory: 6 Hours				Practice: 18 Hours			Credit Hours: 2.4

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Verify Faraday’s law by moving permanent magnet inside the coil. | Trainee will be able to: - Construct a coil. - Connect Galvanometer with coil. - Move permanent magnet inside the coil fast and slow. - Record the effect of movement of magnet on reading of Galvanometer. - Hold the magnet inside the coil and do not move. - Record the effect on reading of Galvanometer again. | - Construction technique of coil and connection of coil with galvanometer - Procedure of taking reading from galvanometer after the movement of magnet inside the coil fast and slow. Practical Activity Verify Faraday’s law by moving permanent magnet inside the coil. | Total 04 Hrs. Th. 01 Hrs. Practical: 03 Hrs. | Coil Galvanometer. Connecting leads. Magnet. | Class Room and workshop |
| - Verify Faraday’s law by moving coil near the magnet field. | Trainee will be able to: - Construct a coil. - Connect Galvanometer with coil. - Fix permanent magnet and move the coil fast and slow on it. - Record the effect of movement of coil on reading of Galvanometer. - Hold the coil near the magnetic field and do not move. - Record the effect on reading of Galvanometer. | - Construction technique of coil and connection of coil with galvanometer - Procedure of taking reading from galvanometer after the movement of coil near the magnet. Practical Activity Verify Faraday’s law by moving coil near the magnet field. | Total 04 Hrs. Th. 01 Hrs. Practical: 03 Hrs. | Coil Galvanometer. Connecting leads. Magnet. | Class Room and workshop |
| - Verify Faraday’s law using relative motion of coil and magnet. | Trainee must be able to: - Construct a coil. - Connect Galvanometer with coil. - Make relative motion of coil and magnet. - Record the effect of movement on reading of Galvanometer. | - Construction technique of coil and connection of coil with galvanometer - Procedure of taking reading from galvanometer after the relative motion of coil and magnet. Practical Activity Verify Faraday’s law using relative motion of coil and magnet. | Total 04 Hrs. Th. 01 Hrs. Practical: 03 Hrs. | Coil Galvanometer. Connecting leads. Magnet. | Class Room and workshop |
| - Verify Faraday’s Law using simple loop generator. | Trainee must be able to - Identify single loop generator and its parts. - Select field winding. - Connect Galvanometer with single loop coil. - Rotate the single loop coil of generator in the field - Measure the voltage induces in loop generator. - Record the effect of movement on reading of Galvanometer. | - Parts and working of single loop generator - Rotation of single loop coil in magnetic field. - Effect of movement on reading of Galvanometer. Practical Activity Verify Faraday’s Law using simple loop generator. | Total 04 Hrs. Th. 01 Hrs. Practical: 03 Hrs. | Loop Galvanometer. Voltmeter Connecting leads. coil DC source | Class Room and workshop |
| - Verify Torque induce in a current carrying loop | Trainee must be able to - Construct a coil. - Apply DC voltage to this coil. - Place a current carrying loop in this coil. - Check the direction of force to verify the torque produce. | - Construction technique of coil. - Placement of current carrying loop in the coil. - Measurement of force direction. Practical Activity Verify Torque induce in a current carrying loop | Total 04 Hrs. Th. 01 Hrs. Practical: 03 Hrs. | Coil Voltmeter Connecting leads. DC source Loop | Class Room and workshop |
| - Verify Mutual induction | Trainee must be able to - Construct 2 coils on two different legs of single core. - Apply AC voltage to the any one coil. - Check the volts induce in other coil by voltmeter. | - Construction of two coils on two different legs of single core transformer. - Procedure of checking mutual induction. Practical Activity Verify Mutual induction | Total 04 Hrs. Th. 01 Hrs. Practical: 03 Hrs. | Coils Voltmeter core Connecting leads. AC source | Class Room and workshop |

### Operate Single Phase Transformer

Objective: This module covers the knowledge and  skills required to identify types of transformer, Measure transformer ratio of single phase transformer, make transformer winding, determine voltage regulation of single phase transformer with different load and perform parallel operation of single phase transformer.

Duration: 21 Hours			Theory: 6 Hours			Practice: 18 Hours				Credit Hours: 2.1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Identify types of transformer. | Trainee will be able to: - Identify no of windings on primary and secondary side of transformer. - Identify the types of transformer cores. - Identify connection of the windings. - Separate single phase, three phase and auto transformer. | - Identification of no of winding on primary and secondary side of transformer. - Identification of transformer core. - Connection of transformer winding. Practical Activity Identify types of transformer. | Total 04 Hrs. Th. 01 Hrs. Practical: 03 Hrs. | Single phase transformers. | Class Room and workshop |
| - Measure transformation ratio of single phase transformer. | Trainee will be able to: - Connect volt meters on both side of the transformer. - Apply rated voltage to the primary. - Note the volt meter reading. - Calculate transformation ratio using ratio formula. - Repeat the procedure for different secondary tapping. | - Connection of voltmeters with both side of the transformer. - Calculation of transformation ratio using ratio formula Practical Activity Measure transformation ratio of single phase Transformer. | Total 04 Hrs. Th. 01 Hrs. Practical: 03 Hrs. | Single phase transformer. Voltmeters. Connecting wires. AC source. | Class Room and workshop |
| - Make transformer winding | Trainee must be able to: - Design the core of transformer according to the transformer rating. - Select the wire for primary and secondary winding. - Perform winding according to require turns with the help of winding machine. - Cover the winding with insulating paper. - Adjust the core pieces into the winding. - Remove the insulation of enameled wire. - Cover the ends of wire with sleeve. - Perform continuity test with ohm meter. | - Design of core in single phase transformer. - Selection of wire for primary and secondary winding. - Winding procedure of single phase transformer. - Adjustment of core pieces into the winding. - Checking continuity of winding with ohm meter. Practical Activity Make transformer winding | Total 07 Hrs. Th. 01 Hrs. Practical: 06 Hrs. | Winding wire. Winding machine. Ohmmeter. Sleeve. Hammer. Insulating paper. Single phase transformer. Voltmeters Connecting wires Core | Class Room and workshop |
| - Determine voltage regulation of single phase transformer with different loads. | Trainee must be able to - Connect volt meter to the primary side of transformer. - Connect the voltmeter to secondary side of transformer. - Connect resistive load to secondary side. - Apply rated voltage to primary side of transformer. - Calculate voltage drop and voltage regulations (%) from meter readings. - Repeat procedure for inductive load. - Repeat procedure for capacitive load. | - Connection of voltmeters with primary and secondary sides of transformer. - Calculation of voltage drop and voltage regulation for different loads. Practical Activity Determine voltage regulation of single phase transformer with different loads. | Total 04 Hrs. Th. 01 Hrs. Practical: 03 Hrs. | Different loads Single phase transformer Voltmeters Connecting wires. AC source | Class Room and workshop |
| - Perform parallel operation of single phase transformer. | Trainee must be able to - Identify two transformers having same rated voltage, frequency and transformation ratio. - Mark the terminals with the help of polarity test. - Connect secondary sides of both transformers in parallel. - Connect secondary sides of both transformers with load bus bar having ampere meters between them. - Connect the primary side of both transformers in parallel. - Connect primary side of transformer with generation bus bar. - Adjust the ammeter readings to zero by adding inductor and resistor in series with secondary side of the transformer. | - Identification of transformers. - Conditions for paralleling of single phase transformers. - Polarity test of single phase transformer. - Connection of transformers with generation and load buses. Practical Activity Perform parallel operation of single phase transformer. | Total 05 Hrs. Th. 02 Hrs. Practical: 03 Hrs. | transformers Voltmeters Connecting leads. DC source Resistor Inductor Ammeter | Class Room And workshop |

### Perform Tests on Single Phase Transformer

Objective: This module covers the knowledge and  skills required to perform polarity test of single phase transformer, Perform Open circuit test of transformer, Perform Short Circuit Test of Transformer, calculate efficiency of transformer by direct method and calculate efficiency of transformer by Back to Back test.

Duration:  30 Hours				Theory: 6 Hours			Practice: 24 Hours			Credit Hours: 3.0

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Perform polarity test of single phase transformer. | Trainee will be able to: - Connect the circuit according to the diagram. - Note the reading of both voltmeters. - Identify additive and subtractive polarity. - Mark the terminal according to the additive and subtractive polarity. | - Procedure of polarity test. - Type of polarity Practical Activity Perform polarity test of single phase transformer. | Total 05 Hrs. Th. 01 Hrs. Practical: 04 Hrs. | Single phase transformers. Voltmeters connecting wires AC source. | Class Room and workshop |
| - Perform Open circuit test of transformer. | Trainee will be able to: - Connect watt meter, ampere meter, and volt meter to the lower voltage side of transformer. - Open the high voltage side of transformer. - Apply rated voltage to lower voltage side of transformer. - Read the instrument/meters reading. - Calculate iron losses and excitation branch component (Ro, Xo). | - Connection of watt meter, ampere meter, and volt meter in open circuit test. - Calculation of iron losses and excitation branch component. Practical Activity Perform Open circuit test of Transformer. | Total 06 Hrs. Th. 01 Hrs. Practical: 05 Hrs. | Single phase transformer. Voltmeter. Connecting wires. AC source. Wattmeter. Ammeter. | Class Room and workshop |
| - Perform Short circuit Test of Transformer. | Trainee must be able to: - Connect watt meter, ampere meter, and volt meter to the higher voltage side of transformer. - Connect lower voltage side terminal with each other (Short Circuit) - Apply 10 % to 15 % of rated voltage to higher voltage side of transformer. - Read the instrument/meters readings. - Calculate copper losses and winding component (Ro1, Xo1) | - Connection of watt meter, ampere meter, and volt meter in short circuit test. - Calculation of copper losses and winding component. Practical Activity Perform Short circuit Test of Transformer. | Total 06 Hrs. Th. 01 Hrs. Practical: 05 Hrs. | Single phase transformer. Voltmeter. Connecting wires. AC source. Wattmeter Ammeter | Class Room and workshop |
| - Calculate efficiency of transformer by direct method. | Trainee must be able to - Perform short circuit test. - Calculate iron losses and copper losses from above tests. - Calculate input power and output power. - Calculate efficiency from calculated powers. | - Open circuit test. - Short circuit test. - Calculation of iron losses, copper losses, input power, output power and efficiency. Practical Activity Calculate efficiency of transformer by direct method. | Total 06 Hrs. Th. 01 Hrs. Practical: 05 Hrs. | Single phase transformer. Voltmeter. Connecting wires. AC source. Wattmeter Ammeter | Class Room and workshop |
| - Calculate efficiency of transformer by Back to Back test. | Trainee must be able to - Identify two transformer of same rating. - Connect both transformers in parallel. - Connect another variable voltage transformer to secondary side of parallel transformers. - Connect a switch, watt meter and ammeter between variable voltage transformer and parallel transformer. - Connect voltmeter and watt meter to primary side of transformer parallel transformer. - Apply rated voltage to the primary side of the parallel transformers. - Open the switch. - Calculate iron losses. - Close the switch - Adjust the voltage of variable voltage transformer until the full load current passes from secondary side of parallel transformers. - Calculate copper losses. - Calculate efficiency from above calculated losses. | - Identification of transformers. - Connection of transformers. - Connection of meters and switches. - Calculation of losses and efficiency. Practical Activity Calculate efficiency of transformer by Back to Back test. | Total 07 Hrs. Th. 02 Hrs. Practical: 05 Hrs. | Transformers. Voltmeters Connecting leads. AC sources Switch Ammeter | Class Room And workshop |

### Operate Auto Transformer

Objective: This module covers the knowledge and  skills required to identify the connection of auto transformer, Calculate Voltage ratio of Auto Transformer and calculate Current ratio of Auto Transformer.

Duration: 27 Hours			Theory: 3 Hours				Practice: 24 Hours			Credit Hours: 2.7

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Identify the connection of auto transformer | Trainee will be able to: - Connect voltmeters to the both side of the transformer. - Apply rated voltage to the primary side. - Identify the lower voltage and higher voltage side with the help of volt meter reading. - Identify step up and step down transformer. | - Auto transformer connection. - Identification of connection with voltmeters. Practical Activity Identify the connection of auto transformer | Total 10 Hrs. Th. 01 Hrs. Practical: 09 Hrs. | Voltmeters Auto transformer connecting wires | Class Room and workshop |
| - Calculate Voltage ratio of Auto Transformer | Trainee will be able to: - Connect voltmeters to the both side of the transformer. - Apply rated voltage to the primary side. - Read the voltmeters reading. - Calculate voltage ratio with the help of voltmeters reading. | - Voltage ratio of auto transformer. - Calculation of voltage ratio with the help of voltmeters reading. Practical Activity Calculate Voltage ratio of Auto Transformer | Total 10 Hrs. Th. 01 Hrs. Practical: 09 Hrs. | Voltmeters Auto transformer AC source connecting wires | Class Room and workshop |
| - Calculate Current ratio of Auto Transformer | Trainee must be able to: - Connect ammeters to the both side of the transformer. - Connect a resistive load to secondary side of the transformer. - Apply rated voltage to the primary side. - Read the ammeters reading. - Calculate current ratio with the help of ammeters reading. | - Current ratio of auto transformer. - Calculation of current ratio with the help of ammeters reading. Practical Activity Calculate Current ratio of Auto Transformer | Total 07 Hrs. Th. 01 Hrs. Practical: 06 Hrs. | AC Source Ammeters Resistive load Auto transformer connecting wires | Class Room and workshop |

### Perform Tests on Auto Transformer.

Objective: This module covers the knowledge and  skills required to Perform open circuit Test of auto transformer, perform short circuit test of auto transformer and calculate efficiency of auto transformer.

Duration: 36 Hours				Theory: 6Hours			Practice: 30 Hours			Credit Hours: 3.6

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Perform open circuit Test of auto transformer. | Trainee will be able to: - Connect watt meter, ampere meter, and volt meter to the lower voltage side of transformer. - Open the high voltage side of transformer. - Apply rated voltage to lower voltage side of transformer. - Read the instrument/meters reading. - Calculate iron losses and excitation branch component (Ro, Xo). | - Connection of watt meter, ampere meter, and volt meter in open circuit test. - Calculation of iron losses and excitation branch component. Practical Activity Perform open circuit Test of auto transformer. | Total 12 Hrs. Th. 02 Hrs. Practical: 10 Hrs. | Voltmeter Wattmeter Ammeter connecting wires Auto transformer AC Source | Class Room and workshop |
| - Perform short circuit test of auto transformer | Trainee will be able to: - Connect watt meter, ampere meter, and volt meter to the higher voltage side of transformer. - Connect lower voltage side terminal with each other (Short Circuit) - Apply 10 % to 15 % of rated voltage to higher voltage side of transformer. - Read the instrument/meters readings. - Calculate copper losses and winding component (Ro1, Xo1) | - Connection of watt meter, ampere meter, and volt meter in short circuit test. - Calculation of copper losses and winding component. Practical Activity Perform short circuit test of auto transformer | Total 12 Hrs. Th. 02 Hrs. Practical: 10 Hrs. | Voltmeter Wattmeter Ammeter connecting wires Auto transformer AC Source | Class Room and workshop |
| - Calculate efficiency of auto transformer. | Trainee must be able to: - Perform open circuit test. - Perform short circuit test. - Calculate iron losses and copper losses from above tests. - Calculate input power and output power. - Calculate efficiency from calculated powers. | - Open circuit test. - Short circuit test. - Calculation of iron losses, copper losses, input power, output power and efficiency. Practical Activity Calculate efficiency of auto transformer. | Total 12 Hrs. Th. 02 Hrs. Practical: 10 Hrs. | Voltmeter Wattmeter Ammeter connecting wires Auto transformer AC Source | Class Room and workshop |

### Operate Three Phase Transformer

Objective: This module covers the knowledge and  skills required to Make Three Phase Transformer Winding, Perform Star to Star Connection of Three Phase Transformer, Perform Star to Delta Connection of Three Phase Transformer, Perform Delta to Delta Connection of Three Phase Transformer, Perform Delta to Star Connection of Three Phase Transformer, Connect Two Single Phase Transformers in Open Delta and perform Parallel operation of 3 phase transformers.

Duration: 33 Hours			Theory: 6 Hours				Practice: 27 Hours			Credit Hours: 3.3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Make Three Phase Transformer Winding. | Trainee will be able to: - Design the core of transformer according to the transformer rating. - Select the connection of primary and secondary. - Select the wire for primary and secondary winding. - Perform winding according to require turns with the help of winding machine. - Cover the winding with insulating paper. - Adjust the core pieces into the winding. - Remove the insulation of enameled wire. - Cover the ends of wire with sleeve. - Connect the winding terminals in star or delta. - Perform continuity test with ohm meter. | - Design of core in three phase transformer. - Selection of wire for primary and secondary winding. - Winding procedure of three phase transformer. - Adjustment of core pieces into the winding. - Checking continuity of winding with ohm meter. Practical Activity Make Three Phase Transformer Winding. | Total 10 Hrs. Th. 01 Hrs. Practical: 09 Hrs. | Core. Winding wire. Winding machine. Insulating paper. Knife. Sleeve. Ohm meter. Connecting wires. Electrical tools kit. | Class Room and workshop |
| - Perform Star to Star Connection Of Three Phase Transformer. | Trainee will be able to: - Select three same rated single phase transformers. - Mark the polarity of the winding terminals. - Connect primary terminals and secondary terminals in star. - Connect voltmeters with primary and secondary. - Apply rated voltage to the primary. - Calculate and Verify line voltage and phase voltage | - Definition of Star to star connection of three phase transformer. - Procedure for marking polarity of the winding terminals. - Relation between line voltage and phase voltage in star connection. Practical Activity Perform Star to Star Connection Of Three Phase Transformer. | Total 3.5 Hrs. Th. 0.5 Hrs. Practical: 03 Hrs. | Single phase transformers. Voltmeters connecting wires AC Source | Class Room and workshop |
| - Perform Star To Delta Connection Of Three Phase Transformer | Trainee must be able to: - Select three same rated single phase transformers. - Mark the polarity of the winding terminals. - Connect primary terminals in star and secondary terminals in delta. - Connect voltmeters with primary and secondary. - Apply rated voltage to the primary. - Calculate and Verify line voltage and phase voltage | - Definition of star to Delta connection - Procedure of polarity marking. - Calculation of line voltage and phase voltage in star to delta connection. - Relation between line voltage and phase voltage in star to delta connection. Practical Activity Perform Star To Delta Connection Of Three Phase Transformer | Total 3.5 Hrs. Th. 0.5 Hrs. Practical: 03 Hrs. | Single phase transformers. Voltmeters connecting wires AC Source | Class Room and workshop |
| - Perform Delta to Delta Connection Of Three Phase Transformer | Trainee will be able to: - Select three same rated single phase transformers. - Mark the polarity of the winding terminals. - Connect primary terminals and secondary terminals in delta. - Connect voltmeters with primary and secondary. - Apply rated voltage to the primary. - Calculate and Verify line voltage and phase voltage | - Definition of delta to delta connection - Procedure of polarity marking. - Procedure of Delta to Delta connection. - Calculation of line voltage and phase voltage. - Relationship between line voltage and phase voltage in delta to delta connection. Practical Activity Perform Delta to Delta Connection Of Three Phase Transformer | Total 04 Hrs. Th. 01 Hrs. Practical: 03 Hrs. | Single phase transformers. Voltmeters connecting wires AC Source | Class Room and workshop |
| - Perform Delta to Star Connection Of Three Phase Transformer | Trainee will be able to: - Select three same rated single phase transformers. - Mark the polarity of the winding terminals. - Connect primary terminals in Delta and secondary terminals in Star. - Connect voltmeters with primary and secondary. - Apply rated voltage to the primary. - Calculate and Verify line voltage and phase voltage. | - Definition of delta to star connection - Procedure of polarity marking. - Calculation of line voltage and phase voltage in delta to star connection. - Relation between line voltage and phase voltage in to delta to star connection. Practical Activity Perform Delta to Star Connection Of Three Phase Transformer | Total 04 Hrs. Th. 01 Hrs. Practical: 03 Hrs. | Single phase transformers. Voltmeters connecting wires AC Source | Class Room and workshop |
| - Connect Two Single Phase Transformers In Open Delta. | Trainee will be able to: - Select two same rated single phase transformers. - Mark the polarity of the winding terminals. - Connect opposite terminals of primary winding of both transformers - Take out connected terminals and other two terminals. - Repeat the procedure for secondary side of transformer. - Connect voltmeters with primary and secondary sides of transformers. - Apply rated voltage to the primary. - Calculate and verify line voltage and phase voltage. | - Definition open delta connection - Selection of transformers. - Polarity marking. - Connection of transformers. - Relation between line voltage and phase voltage in open delta connection Practical Activity Connect Two Single Phase Transformers In Open Delta. | Total 04 Hrs. Th. 01 Hrs. Practical: 03 Hrs. | Single phase transformers. Voltmeters connecting wires AC Source | Class Room and workshop |
| - Perform Parallel operation of 3 phase transformers. | Trainee will be able to: - Identify two three phase transformer having same rated voltage, frequency and transformation ratio. - Connect the primary of each transformer in star connection. - Connect the secondary of each transformer in Delta connection. - Connect secondary sides of both transformers in parallel. - Connect secondary sides of both transformers with load bus bar having indicator between them. - Connect the primary side of both transformers in parallel. - Connect primary side of transformer with generation bus bar. - Adjust the series resistance and series inductance to off the indicator. | - Identification of transformers. - Conditions for paralleling of three phase transformers. - Polarity test of three phase transformer. - Connection of transformers with generation and load buses. Practical Activity Perform Parallel operation of 3 phase transformers. | Total 04 Hrs. Th. 01 Hrs. Practical: 03 Hrs. | Three phase transformers. Voltmeters connecting wires indicator variable resistor variable inductor AC Source | Class Room and workshop |

### Identify Vector Group of Three Phase Transformer

Objective: This module covers the knowledge and  skills required to Connect 3-phase transformers as per given vector group Yyo and Yy6, connect 3-phase transformers as per given vector group Ddo and Dd6 and connect 3-phase transformers as per given vector group Yd11 and Yd1.

Duration: 30 Hours				Theory: 6 Hours			Practice: 24 Hours			Credit Hours: 3.0

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Connect 3-phase transformers as per given vector group Yyo and Yy6 | Trainee will be able to: - Connect three identical single phase transformer in star to star connection. - Connect phase angle meter between primary and secondary. - Apply rated voltage to the primary side of transformer. - Measure the phase angle between primary and secondary with the help of phase angle meter (00 and 1800). | - Definition of star to star connection. - Connection of phase angle meter between primary and secondary of the transformers. - Phase angle of vector group Yy0. - Phase angle of vector group Yy6 Practical Activity Connect 3-phase transformers as per given vector group Yyo and Yy6 | Total 10 Hrs. Th. 02 Hrs. Practical: 08 Hrs. | Single phase transformers. Phase angle meter. Connecting wires. AC source. | Class Room and workshop |
| - Connect 3-phase transformers as per given vector group Ddo and Dd6 | Trainee will be able to: - Connect three identical single phase transformer in delta to delta connection. - Connect phase angle meter between primary and secondary. - Apply rated voltage to the primary side of transformer. - Measure the phase angle between primary and secondary with the help of phase angle meter (00 and 1800). | - Definition of delta to delta connection. - Connection of phase angle meter between primary and secondary of the transformers. - Phase angle of vector group Ddo. - Phase angle of vector group Dd6. Practical Activity Connect 3-phase transformers as per given vector group Ddo and Dd6 | Total 10 Hrs. Th. 02 Hrs. Practical: 08 Hrs. | Single phase transformers. Phase angle meter. Connecting wires. AC source. | Class Room and workshop |
| - Connect 3-phase transformers as per given vector group Yd11 and Yd1 | Trainee must be able to: - Connect three identical single phase transformer in star to delta connection. - Connect phase angle meter between primary and secondary. - Apply rated voltage to the primary side of transformer. - Measure the phase angle between primary and secondary with the help of phase angle meter (300 lag or 300 lead). | - Definition of star to delta connection. - Connection of phase angle meter between primary and secondary of the transformers. - Phase angle of vector group Yd11. - Phase angle of vector group Yd1. Practical Activity Connect 3-phase transformers as per given vector group Yd11 and Yd1 | Total 10 Hrs. Th. 02 Hrs. Practical: 08 Hrs. | Single phase transformers. Phase angle meter. Connecting wires. AC source. | Class Room and workshop |

### Repair/ Maintenance and Service of Transformer

Objective: This module covers the knowledge and  skills required to Diagnose Fault in transformer, carry out Service/Repair of Transformer and Carry out Preventive Service/ Maintenance of transformer.

Duration: 30 Hours			Theory: 6 Hours				Practice: 24 Hours			Credit Hours: 3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Diagnose Fault in transformer | Trainee will be able to: - Identify the type of transformer from data / name plate or manual and transformer rating. - Check the tripping/continuity of protective device using specified test - Dismantle the transformer, inspect visual mechanical defect such as, leakage of tank, noisy running, short circuit, LT, HT, coil, insulation and temperatures. - Before dissembling the transformer from assembly take snapshot ore draw layout diagram. - Check the transformer by using specified test instruments to detect electrical defects such as loose/or burnt electrical connections, burnt coil. Transformer oil, low insulation resistance etc. - Test Coil by humming method ore any standard method. - Check core lamination - Check continuity of Buchholz relay. - Check Short circuit faults such as inter turn faults, incipient winding faults, and core faults may occur due to the impulse breakdown of the insulating transformer oil. - Diagnose the faulty area | - Identification of faulty transformer. - Definition of tripping/continuity of protective device - Inspect visual mechanical and electrical defect - Testing of coil by humming. - Continuity of Buchholz relay - Short circuit fault in transformer. Practical Activity Diagnose Fault in transformer | Total 11 Hrs. Th. 02 Hrs. Practical: 09 Hrs. | Various type of transformers Ammeters Voltmeters Connecting leads. Electrical tools kit. Oil testing set. Meager. | Class Room and workshop |
| - Carry out Service/Repair of Transformer | Trainee will be able to: - Clean the parts of the transformer with specified cleaning agents/tools & material. - Repair the transformer as per diagnosed fault - Rewind and assembled the transformer as per requirement - Check the insulation resistance of repaired transformer as per standard - Carry out the No load and load tests as per standard practices - Carry out de-hydration of oil - Carry out de-hydration of silica gel - Check and repair leakage in transformer tank | - Definition and type of cleaning agents. - Repair of winding - Checking of the insulation resistance of repaired transformer as per standard. - Tests on transformer after repair. - De-hydration of oil. - De-hydration of silica gel. Practical Activity Carry out Service/Repair of Transformer | Total 11 Hrs. Th. 02 Hrs. Practical: 09 Hrs. | Transformer. Cleaning agents Electrical tools kit. Voltmeters. Ammeters. Wattmeter. Winding wire. | Class Room and workshop |
| - Carry out Preventive Service/ Maintenance of transformer | Trainee must be able to: - Carry out routine maintenance of the transformer as specified in the manufacturer’s manual - Check out the, protective relay and other allied device and wire connection - Update the maintenance/service records. | - Preventive maintenance work on transformer. - Update the maintenance/service records. Practical Activity Carry out Preventive Service/ Maintenance of transformer | Total 08 Hrs. Th. 02 Hrs. Practical: 06 Hrs. | Various type of transformers. Manufacturer’s manual. Electrical tools kit. Maintenance/service records of transformer. | Class Room and workshop |

## Industrial Electrician

### Maintain Tools & Equipment for Three Phase

Objective: This module covers the knowledge and  skills required to Maintain tool & equipment. After completion of this module the trainee must be able to arrange tools/equipment, maintain tool box, insulate tools/equipment, calibrate measuring tools and manage proper inventory of used/unused tools/equipment.

Duration: 27 Hours				Theory: 06 Hours			Practice: 21Hours			Credit Hours	2.7

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Arrange Tools and Equipment | Trainee will be able to: - Identify tools and equipment - Interpret job card - Prepare list of tools and equipment as per requirement - Collect tools and equipment from store | The trainees must be able to understand: - Various tools and equipment and their functions - Job card/work order - Arrangement of tools/equipment as per job requirements. Practical Task: Arrange tools and equipment for 3 phase distribution board. | Th-1.5Hrs. Pr-03 Hrs. Total- 4.5Hrs | Electrical tools, Mechanical tools, Electrical accessories for 3 phase Installation, Multi meter, | Class Room and workshop |
| Maintain Tool Box | Trainee will be able to: - Check physical conditions of tools and equipment before use - Perform preventive maintenance as per standards - Perform corrective maintenance of tools as per requirements - Clean tools and equipment after use - Place tools and equipment at appropriate place | The trainees must be able to understand: - corrective and preventive maintenance - Arrangement of tools and equipment in tool box - Storage methods of tools and equipment Practical Task: Maintain tool box for a domestic 3 phase network | Th-01Hrs. Pr-06Hrs. Total- 07Hrs. | Electrical tools, Mechanical tools, Electrical | Class Room and workshop |
| Insulate Tools and Equipment | Trainee must be able to: - Collect the required tools and equipment - Check insulation of Tools and Equipment - Perform insulation of the faulty tool/equipment | The trainees must be able to understand: - Insulation procedure - Types of insulation - Importance of insulation Practical Task: Prepare insulated connectors for 3 phase supply. | Th-1.5Hrs. Pr-03Hrs. Total-4.5Hrs. | Electrical tools, Insulating materials, | Class Room and workshop |
| Calibrate measuring tools | Trainee must be able to: - Check calibration status of the measuring tools - Perform calibration of measuring tools as per standards - Record calibration test results | The trainees must be able to understand: - calibration - Types of calibration - Methods of equipment calibration Practical Task: Calibrate a multi meter current measurement. | Th-01Hrs. Pr-6.Hrs. Total-7 Hrs. | Electrical measuring tools |  |
| Manage Inventory of tools and equipment | Trainee must be able to: - Check tools and equipment as per record - Report for faulty tools and equipment to supervisor - Generate demand for deficit tools and equipment - Maintain all records of tools and Equipment’s | The trainees must be able to understand: - Methods of tools and equipment inventory - Procedure of tools and equipment’s inventory | Th-01Hrs. Pr-3 Hrs. Total-4 Hrs. | Inventory registers, Computer system, Printer. |  |

### Make Cable/Wire Joints for Three Phase

Objective: This module covers the knowledge and  skills required to Make cable wire joints for three-phase. After completion of this module the trainee will be able to make Cross/Twist joint, Make Straight/Married joint, Make T- Joint, Make Rat tail joint and Make Britannia joint.

Duration: 30Hours				Theory: 06Hours			Practice: 24Hours				Credit Hours 03

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Make Cross/Twist joint | Trainee will be able to: - Select the cable. - Strip the wire according to 50mm. - Twist the conductors. - Solder the conductor - Insulate the joint | The trainees must be able to understand: - Conductor. - Cable and wire. - Striping of cables. - Twisting of cable - Cable joint - Types of cable joints - Soldering - Soldering procedures - Usage of micro meter screw gauge Practical Task: Make twist joint | Th-02 Hrs. Pr-03Hrs. Total- 05Hrs. | Wire deferent gauge, cables deferent types, soldering wire, Soldering Iron, Plier, Micro meter screw gauge. Nose plier. Wire stripper | Class Room and workshop |
| Make Straight/Married joint | Trainee will be able to: - Select the cable. - Strip wire to 75mm according to joint requirement. - Intermingle the conductors to 60mm into each other. - Twist 60mm conductors leaving behind 15mm of each cable. - Solder the conductor. - Insulate the joint. | The trainees must be able to understand: - Straight/Married joint - Procedure for making staight/married joint. - Applications of Straight/Married joint Practical Task: Make Straight joint. | Th-1 Hrs. Pr-6Hrs. Total- 07Hrs. | Wire deferent gauge, cables deferent types, soldering wire, Soldering Iron, Plier, Micro meter screw gauge. Nose plier. Wire stripper | Class Room and workshop |
| Make T- Joint | Trainee must be able to: - Select the cable. - Remove the insulation of cable 1 to 50mm from where a connection is required. - Separate conductors of cable 1 equally. - Take another 12 mm stripped wire 2. - Insert between two equally half conductors of cable 1 and twist. Half conductors clockwise and half anti-clock wise of cable 2. - Solder the joint. | The trainees must be able to understand: - T- Joint - Procedure for making T- joint. - Applications of T- Joint Practical Task: Make T- joint. | Th-1Hrs. Pr-6 Hrs. Total- 7 Hrs. | Wire deferent gauge, cables deferent types, soldering wire, Soldering Iron, Plier, Micro meter screw gauge. Nose plier. Wire stripper | Class Room and workshop |
| Make Rat tail joint | Trainee must be able to: - Select the single conductor wires. - Strip both the wires to 5mm. - Twist the conductor. - Insulate the joint. - Solder the joint. | The trainees must be able to understand: - Rat tail joint - Procedure for making Rat tail joint - Applications of Rat tail joint Practical Task: Make Rat tail joint | Th-1Hrs. Pr-3Hrs. Total- 4Hrs. | Wire deferent gauge, cables deferent types, soldering wire, Soldering Iron, Plier, Micro meter screw gauge. Nose plier. Wire stripper |  |
| Make Britannia joint | Trainee must be able to: - Select the cable. - Strip both cables to 75mm. - Bend the tips of both cable right angle about to 6mm. - Hold the two cables overlap 50mm with tips in opposite direction. - Take another bare conductor of 1mm and wrap around in both directions to 6mm. - Solder the joint. - Insulate the joint. | The trainees must be able to understand: - Britannia joint - Procedure for making Britannia joint - Applications of Britannia joint Practical Task: Make Britannia joint | Th-1 Hrs. Pr-6 Hrs. Total- 7 Hrs. | Wire deferent gauge, cables deferent types, soldering wire, Soldering Iron, Plier, Micro meter screw gauge, Nose plier. Wire stripper |  |

### Prepare and Install Distribution Boards for Three Phase

Objective: This module covers the knowledge and  skills required to prepare and install distribution board according to provide protection and load division. After completion of this module the trainee must be able to prepare estimate for wiring material, Prepare Distribution Board and Install Distribution Board and wiring.

Duration: 33Hours				Theory: 06Hours			Practice: 27 Hours 				Credit Hours 3.3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Prepare estimate for wiring material. | Trainee will be able to: - Develop Basic Drawing - Perform Estimation of Materials - Calculate Labor Cost | The trainees must be able to understand: - Basic drawing concepts. - Electrical Symbols. - Basic electrical parameters with units - Basic electrical standard. - Basic parts of distribution board and its functionality. - Procedure for estimation. Practical Task: Prepare estimate for 3 phase installation of two class rooms. | Th-02Hrs. Pr-09Hrs. Total- 11Hrs. | Drawing board, Drawing Sheet, Drawing tools, Note book | Class Room and workshop |
| Prepare Distribution Board | Trainee will be able to: - Select Distribution board w.r.t. size, current rating, voltage, No. of C.Bs and phases. - Select Main Incoming Residual Current Circuit Breaker (RCCB) having minimum sensitivity. - Select outgoing Miniature Circuit Breaker (MCB) according to load. - Provide space for future MCB. - Select Voltmeter, ampere meter and indicator according to load and phases. - Select wire according to load and for wiring in DB. - Make neutral common for all load. - Connect accessories according to the circuit diagram. | The trainees must be able to understand: - D.B. w.r.t. size, current rating, voltage, No. of C.Bs and phases etc. - Circuit Breaker - Various types of Circuit Breaker - Fuse and its types. - Residual current - Sensitivity. Practical Task: Prepare and Install a distribution board. | Th-2Hrs. Pr-09Hrs. Total- 11 Hrs | Distribution board, Electrical accessories, Plier, Screw driver set, | Class Room and workshop |
| Install Distribution Board and wiring | Trainee must be able to: - Fix the distribution board. - Take wire from DB to load without joint. - Distribute load equally on all phases. | The trainees must be able to understand: - Testing procedures - Installation procedure Practical Task: Wind, test, install and connect a 3 phase distribution board with input supply. | Th-2Hrs. Pr-09Hrs. Total- 11 Hrs | Plier, Screw driver set, insulation tape, Multi meter. | Class Room and workshop |

### Install Three Phase Electrical Wiring

Objective: This module covers the knowledge and  skills required to Make and Install 3 phase electrical wiring.  After completion of this module the trainee will be able to make and install three-phase motor connection ON/OFF by CAM Switch, Make and Install 3 phase motor connection reversing by CAM Switch, Make and Install 3 phase motor connection ON/OFF by Magnetic Contactor and Make and Install 3 phase motor connection ON/OFF by Magnetic Contactor.

Duration: 30Hours				Theory: 06 Hours			Practice: 24 Hours			Credit Hours 03

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Make and Install 3 phase motor connection ON/OFF by CAM Switch | Trainee will be able to: - Draw power diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | The trainees must be able to understand: - Electromagnetic induction - Motor Rule - Power diagram - Installation diagram - Control diagram. - Three phase supply. - Three phase motor. - types of three phase motor. - CAM switch. - Types of cam switch - On/Off Cam Switch circuit. And its Uses. - Relay - types of three phase motor connection. - Star/ Delta connection - Procedure for connection of cam switch. - Testing procedure. Practical Task: Make 3 phase motor ON/OF through a CAM Switch. | Th-4.5Hrs. Pr-06Hrs. Total-10.5Hrs | Electrician Tool kit, Mechanical tool kit, 3 phase motor, connecting wires, Cam Switch. Multi meter. Contactors, | Class Room and workshop |
| Make and Install 3 phase motor connection reversing by CAM Switch | Trainee will be able to: - Draw power diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | The trainees must be able to understand: - Motor connection forwarding by cam switch - Motor connection Revising by cam switch - Working principles of a Cam Switch - Working principal of circuit diagram. Practical Task: Make 3 phase motor Reversing through a CAM Switch. | Th-0.5Hrs. Pr-06Hrs. Total-6.5Hrs | Electrician Tool kit, Mechanical tool kit, 3 phase motor, connecting wires, Cam Switch. Multi meter. Contactors, | Class Room and workshop |
| Make and Install 3 phase motor connection ON/OFF by Magnetic Contactor | Trainee must be able to: - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | The trainees must be able to understand: - Types of contactors - Functionality of magnetic contactor - Types of magnetic contactor - Working principle of Circuit diagram Practical Task: Make 3 phase motor ON/OF through a magnetic contactor. | Th-0.5Hrs. Pr-06Hrs. Total-6.5Hrs | Electrician Tool kit, Mechanical tool kit, 3 phase motor, connecting wires, Magnetic contactor Multi meter. Contactors, | Class Room and workshop |
| Perform Electrical Work in Commercial Area. | Trainee must be able to: - Install wire for grounding - Perform pre Installation module based Tests - Perform integrated tests. - Install conduits or Trunks in the building as per drawing - Install electrical wiring, as per drawing and standard. - Install centralize lighting, heating, cooling system and other appliances - Install main box and distribution box. - Install Electric Breakers in main box, as per load for safety measures - Install fire alarm and smoke detector system - Install the appliances used in electrical work as per drawing - Install emergency light system in main box. | The trainees must be able to understand: - Procedure for wire grounding. - Various testing methods. - Types of wiring. - Functionality of electrical accessories Practical activity: Carry out electrical wiring For a single room and a tube well . | Th-0.5Hrs. Pr-06Hrs. Total-6.5Hrs | Electrician Tool kit, Mechanical tool kit, 3 phase motor, connecting wires, Cam Switch. Multi meter. Contactors, Contactor. Cables. Insulation tape. |  |

### Install Three Phase Complex Electrical Wiring

Objective: This module covers the knowledge and  skills required to install three phase complex electrical wiring. After completion of this module the trainees will be able to Make and Install 3 phase motor connection Reverse/ forward by Magnetic contactor, Make and Install 3 phase motor connection Reverse/ forward by Magnetic contactor with indicator, Make and Install 3 phase motor connection Star/Delta (Manual) by Magnetic contactor, Make and Install 3 phase motor connection Star/Delta (Manual) by Magnetic contactor with indicator, Make and Install 3 phase motor connection Star/Delta (Auto) by Magnetic contactor, Make and Install 3 phase motor connection Star/Delta (Auto) by Magnetic contactor with indicator, Make and Install 3 phase motor connection 2 speed by Magnetic contactor, Make and Install 3 phase motor connection 2 speed by Magnetic contactor with indicator.

Duration: 33 Hours				Theory: 06Hours			Practice: 27Hours			Credit hours	3.3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Make and Install 3 phase motor connection Reverse/ forward by Magnetic contactor. | Trainee will be able to: - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | The trainees must be able to understand: - Functionality of Power Diagram - Functionality of Control Diagram - Functionality of Connection diagram - Application of forward and reverse motor. Practical task: Assembled the power and control of a 3 phase forward and reverse starter. | Th-01Hrs. Pr-03Hrs. Total-04Hrs | Electrician Tool kit, Mechanical tool kit, 3 phase motor, connecting wires, Cam Switch. Multi meter. Contactors, | Class Room and workshop |
| Make and Install 3 phase motor connection Reverse/ forward by Magnetic contactor with indicator. | Trainee will be able to: - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | The trainees must be able to understand: - Functionality of Power Diagram - Functionality of Control Diagram - Functionality of Connection diagram Practical task: Assembled 3 phase motor connection Reverse/ forward by Magnetic contactor with indicator. | Th-0.5Hrs. Pr-03Hrs. Total-3.5Hrs | Electrician Tool kit, Mechanical tool kit, 3 phase motor, connecting wires, Cam Switch. Multi meter. Contactors, | Class Room and workshop |
| Make and Install 3 phase motor connection Star/Delta (Manual) by Magnetic contactor. | Trainee must be able to: - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply . | The trainees must be able to understand: - Functionality of Power Diagram - Functionality of Control Diagram - Functionality of Connection diagram - Functionality of star/delta starter. Practical task: Assembled Control circuit by using magnetic contactor for three-phase motor | Th-01Hrs. Pr-03Hrs. Total-4Hrs. | Electrician Tool kit, Mechanical tool kit, 3 phase motor, connecting wires, Magnetic contactor Multi meter. Contactors, | Class Room and workshop |
| Make and Install 3 phase motor connection Star/Delta (Manual) by Magnetic contactor with indicator. | Trainee must be able to: - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | The trainees must be able to understand: - Functionality of Power Diagram - Functionality of Control Diagram - Functionality of Connection diagram Practical activity: Assembled power circuit for three-phase motor using magnetic contactor | Th-0.5Hrs. Pr-03Hrs. Total-3.5Hrs | Electrician Tool kit, Mechanical tool kit, 3 phase motor, connecting wires. Multi meter. Contactors, Cables. Insulation tape. Indicator | Class Room and workshop |
| Make and Install 3 phase motor connection Star/Delta (Auto) by Magnetic contactor. | Trainee must be able to: - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | Demonstrate: - Functionality of Power Diagram - Functionality of Control Diagram - Functionality of Connection diagram Practical activity: Assembled 3 phase motor connection Star/Delta (Auto) by Magnetic contactor. | Th-0.5Hrs. Pr-03Hrs. Total-3.5Hrs | Electrician Tool kit, Mechanical tool kit, 3 phase motor, Star/Delta starter, connecting wires. Multi meter. Contactors, Cables. Insulation tape. | Class Room and workshop |
| Make and Install 3 phase motor connection Star/Delta (Auto) by Magnetic contactor with indicator | Trainee must be able to: - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | The trainees must be able to understand: - Functionality of Power Diagram - Functionality of Control Diagram - Functionality of Connection diagram Practical activity: Make 3 phase motor connection Star/Delta (Auto) by Magnetic contactor with indicator | Th-0.5Hrs. Pr-06Hrs. Total-6.5Hrs | Electrician Tool kit, Mechanical tool kit, 3 phase motor, Star/Delta starter, connecting wires. Multi meter. Contactors, Cables. | Class Room and workshop |
| Make and Install 3 phase motor connection 2 speed by Magnetic contactor. | Trainee must be able to: - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | The trainees must be able to understand: - Functionality of Power Diagram - Functionality of Control Diagram - Functionality of Connection diagram. - RYB - Application of 2 speed motor. Practical activity: Make 3 phase motor connection 2 speed by Magnetic contactor | Th-01Hrs. Pr-03Hrs. Total-4Hrs. | Electrician Tool kit, Mechanical tool kit, 3 phase moto 2 speed, Star/Delta starter, connecting wires. Multi meter. Contactors, Cables. | Class Room and workshop |
| Make and Install 3 phase motor connection 2 speed by Magnetic contactor with indicator | Trainee must be able to: - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply. | The trainees must be able to understand: - Functionality of Power Diagram - Functionality of Control Diagram - Functionality of Connection diagram Practical activity: Make 3 phase motor connection 2 speed by Magnetic contactor with indicator | Th-01Hrs. Pr-03Hrs. Total- 04Hrs | Electrician Tool kit, Mechanical tool kit, 3 phase moto 2 speed, Star/Delta starter, connecting wires. Multi meter. Contactors, Cables. indicator | Class Room and workshop |

### Perform Testing of Electrical Wiring

Objective: This module covers the knowledge and  skills required to perform Testing of Electrical Wiring. After completion earth leakage test, perform open circuit test, perform short circuit test, perform continuity/loop test, perform visual test, perform insulation test, perform polarity test, perform earth resistance test, perform Murray loop test, and perform Blavier & earth loop test

Duration: 30Hours			Theory: 06Hours				Practice: 24Hours			Credit Hours	03

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Perform Earth leakage Test. | Trainee will be able to: - Ensure the socket must be at least 13A for RCD plug in. - Adjust the sensitivity of RCD. - Ensure tripping time must not exceed than 200msec. - Plug the RCD in socket and switch on socket outlet. - Ensure P-N and P-E light up. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. - Move the selection switch to 180o. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. - Move selection switch to 00. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. | The trainees must be able to understand: - RCD - function of RCD. - Sensitivity - P-E and P-N light - function of distribution box. - function of fuse. - Function of ELCB - Functionality of megger tester. - Electrical tests - Earth leakage Test. - Purpose Earth leakage Test - Procedure for Earth leakage test Practical Task: Perform Earth leakage Test | Th-1.5Hrs. Pr-03Hrs. Total-4.5Hrs | Earth leakage clamp meter/Magger tester,ELCB, Circuit breaker, Power supply | Class Room and workshop |
| Perform Open Circuit Test | Trainee will be able to: - Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. - Connect ohmmeter between starting and ending terminals of live conductor. - Ensure the reading must be near to 0 ohm. - Repeat P2 to P3 for neutral and earth conductor. | The trainees must be able to understand: - Open Circuit Test. - Procedure for Open Circuit Test. - Purpose of open circuit test Practical Task: Perform Open Circuit Test | Th-0.5Hrs. Pr-1.5Hrs. Total- 02Hrs | Electrical Circuit, DB, OHM meter ,Power supply | Class Room and workshop |
| Perform Short Circuit Test | Trainee will be able to: - Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. - Connect one terminal of ohmmeter with live conductor. - Connect the other terminals of ohmmeter with neutral conductor. - Ensure the reading must be infinity (No reading). - Connect ohmmeter between live conductor and earth conductor. - Ensure the reading must be infinity (No reading) | The trainees must be able to understand: - Short Circuit Test - Purpose of Short Circuit Test - Procedure for Short Circuit Test. Practical Task: Perform Short Circuit Test. | Th-0.5Hrs. Pr-1.5Hrs. Total- 02Hrs | Electrical Circuit, DB, OHM meter ,Power supply | Class Room and workshop |
| Perform Continuity/Loop Test | Trainee must be able to: - Connect all metal clad switches, metal parts, conduits with ear Theory: - Open the main switch. - Turn on all the switches. - Connect earth continuity tester with conduit and independent ear Theory: - Measure the resistance value with tester which must not be more than 1 ohm. | The trainees must be able to understand: - Continuity - Loop - Functionality of earth continuity tester - Continuity/Loop Test - Purpose of Continuity/Loop Test - Procedure of Continuity/Loop Test Practical activity: Perform Continuity/Loop Test | Th-0.5Hrs. Pr-02Hrs. Total-2.5Hrs |  | Electrical Circuit, DB, earth continuity tester, Power supply |
| Perform Visual Test | Trainee must be able to: - Check the wires joints. - Check if there is any spark. - Check over heating of wires. - Check all the appliances are On or fluctuating. - Check all indications of meters. - Check Voltages on all phases. - Check the DB and Breakers. - Check the main supply is coming properly. | The trainees must be able to understand: - Visual test. - Procedure for visual test of electrical wiring - Purpose of visual test in electrical wiring Practical Task: Perform Visual Test of the electrical installation of the respective workshop. | Th-0.5Hrs. Pr-03Hrs. Total-3.5Hrs |  | Active electrical assembly, Electrical tool kit |
| Perform Insulation Test | Trainee must be able to: - Switch off the main breaker. - Short circuit all lighting connections. - Connect meger between line and earTheory: - Rotate the merger to generate the voltage. - Read the meger dial and ensure that the insulation resistance should not be less than 50M ohm of any single circuit. | The trainees must be able to understand: - Insulation Test - Purpose of Insulation Test - Procedure of Insulation Test Practical Task: Perform Insulation Test of any equipment | Th-0.5Hrs. Pr-02Hrs. Total-2.5Hrs |  | Megger, DB, Electrical tools kit , power supply |
| Perform Polarity Test | Trainee must be able to: - Switch off the main switch. - Disconnect all loads. - Switch on all circuit control switches. - Connect ohm meter between main line and all the terminal of sockets and load points one by one. - Ensure meter reading value must be less than 1 ohm. | The trainees must be able to understand: - Polarity Test - Purpose Polarity Test - Procedure for Polarity Test Practical Task: Perform Polarity Test. | Th-0.5Hrs. Pr-02Hrs. Total-2.5Hrs |  | Multi meter, DB, Electrical tools kit , power supply |
| Perform Earth Resistance Test | Trainee must be able to: - Place 3 electrodes in earth at distance of 10m apart between every electrode. - Connect terminal E of earth resistance tester to first electrode. - Connect terminal P of earth resistance tester to the second electrode. - Connect terminal C of the earth resistance tester with third electrode. - Measure the resistances after applying specific voltage. - Repeat P1 to P5 by interacting earthling regions. - Ensure 3 readings must be equal. | The trainees must be able to understand: - Electrode - Earth resistance - Earth Resistance Test - Purpose of Earth Resistance Test - Procedure of Earth Resistance Test Practical Task: Perform Earth Resistance Test | Th-0.5Hrs. Pr-03Hrs. Total-3.5Hrs |  | Electrodes, connecting wires, earth resistance tester, Power supply. |
| Perform Murray Loop Test | Trainee must be able to: - Connect galvanometer with Wheatstone bridge. - Connect positive terminal of DC source with Wheatstone bridge. - Connect negative terminal of DC source with ground. - Connect remaining two terminal of Wheatstone bridge with two cores of the cable. - Short the other end of these two cores of cable. - Note the reading of galvanometer. - Calculate Rx. - Repeat the P1 to P7 for other cores of the cable. | The trainees must be able to understand: - Wheatstone bridge. - Function of Wheatstone bridge. - Murray Loop Test - Purpose Murray Loop Test - Procedure Murray Loop Test - Purpose of Wheatstone bridge used in Murray loop test. - Purpose of DC Power used in Murray loop test Practical Task: Perform Murray Loop Test | Th-0.5Hrs. Pr-03Hrs. Total-3.5Hrs |  | Galvanometer, Wheatstone bridge, DC Power supply. Two core cable. |
| Perform BLAVIER & Earth Loop Test | Trainee must be able to: - Connect galvanometer with Wheatstone bridge. - Connect positive terminal of DC source with Wheatstone bridge. - Connect negative terminal of DC source with ground. - Connect remaining two terminal of Wheatstone bridge with two cores of the cable. - Short the other end of these two cores of cable. - Note the reading of galvanometer. - Calculate Rx. - Repeat the P1 to P7 for other cores of the cable. | The trainees must be able to understand: - BLAVIER & Earth Loop Test - Purpose of BLAVIER & Earth Loop Test - Procedure BLAVIER & Earth Loop Test Practical Task: Perform BLAVIER & Earth Loop Test | Th-0.5Hrs. Pr-03Hrs. Total-3.5Hrs |  | Galvanometer, Wheatstone bridge, Power supply. Two core cable |

### Diagnose Electrical Fault in Generator

Objective: This module covers the knowledge and  skills required to Diagnose Electrical Fault in Generator. After completion of this module the trainees will be able to inspect and service ignition system, inspect and service alternator, inspect and service display panel, inspect and service governor /Actuator System, inspect and service charging system, inspect and service warning system, and to diagnose electric fault (s) in generator.

Duration: 30Hours				Theory: 06Hours			Practice: 24Hours			Credit Hours	03

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Inspect and service Ignition system . | Trainee will be able to: - Identify the tools and equipment - Check DC power supply of ignition coil and distributor - Check HT leads - Check spark plug | The trainees must be able to understand: - Ignition coil - Distributor - High Tension (HT) Leads - Functions of Spark Plug. - Procedure for inspection and service of Ignition system. Practical task: Check and connect High Tension (HT) Leads of the alternator. | Th-01Hrs. Pr-06Hrs. Total- 07Hrs. | DC power supply. Spark plugs. HT Leads. | Class Room and workshop |
| Inspect and service alternator | Trainee will be able to: - Identify the tools and equipment - Check DC output voltage - Check belt - Make connections of alternator | The trainees must be able to understand: - Alternator - Working principle of alternator - Making connections of alternator - Connection diagram of alternator - Procedure for Inspection and service of alternator. Practical task: Check the belt and out DC voltage of an alternator | Th-01Hrs. Pr-03Hrs. Total- 04Hrs. | Alternator Electrical tool kit, Mechanical tool kit | Class Room and workshop |
| Inspect and service display panel | Trainee will be able to: - Identify tools and equipment - . Check gauges, circuit breakers, relays and wiring as per standard parameters | The trainees must be able to understand: - Display Panel/ Data Screen - Types of circuit breakers / Relays - Ratings of circuit breakers / Relays Practical task: Check and circuit breaker of the main board as per standard. | Th-0.5Hrs. Pr-03Hrs. Total- 3.5Hrs | Multi meter, Electrical tool kit, display panel | Class Room and workshop |
| Inspect and service governor /Actuator System | Trainee must be able to: - . Identify the tools and equipment - Check actuator card supply - Check magnetic pick up - Check power supply on actuator/governor | The trainees must be able to understand: - Governor / Actuator - actuator card - magnetic pick up - Procedure for Inspection and service of governor/actuator - purpose of Inspection and service of governor/actuator Practical task: Check and service power supply on actuator card and check magnetic pick up. | Th-01Hrs. Pr-03Hrs. Total- 04Hrs. | magnetic pick up tool. Electrical tool kit. |  |
| Inspect and service charging system | Trainee must be able to: - Identify the tools and equipment - Check battery power leads - Check charging circuit of alternator | The trainees must be able to understand: - charging system - Functionality of charging circuit. - Procedure for Inspection and service of charging system Practical task: Check and service charging card of alternator. | Th-0.5Hrs. Pr-03Hrs. Total- 3.5Hrs | Battery, Electrical tool kit, Alternator. |  |
| Inspect and service warning system | Trainee must be able to: - Identify tools and equipment - Check oil sensor - Check temperature sensor - Check fuel sensor - Check over/under load module | The trainees must be able to understand: - Sensor - Types and functionality of sensor - miniature circuit breaker - Warning system and its functionality. Practical task: Check temperature and oil sensors. | Th-01Hrs. Pr-03Hrs. Total- 04Hrs. | Electrical tool kit, oil sensor, Temperature sensor, Fuel sensor, |  |
| - Inspect and repair wiring | Trainee must be able to: - Identify the tools and equipment for checking of supply. - Check the main supply. - Check the breakers. - Ensure the supply off. - Perform open circuit and short Circuit test with meter. - Identify the faults. - Remove the fault. | The trainees must be able to understand: - cables with respect to insulation, core, voltage grade & current carrying capacity. - Earthling system. - the earth fault current - Earthling components. Practical task: Perform open and short circuit test of alternator | Th-01Hrs. Pr-03Hrs. Total- 04Hrs. | Electrical tool kit, Electrical wiring accessories. |  |

### Repair/ Maintenance of Electrical Installations for Three Phase

Objective: This module covers the knowledge and  skills required to repair/Maintenance of electrical installation for three-phase. After completion of this module the will be able to Analyze Fault in Electrical Installations, troubleshooting of electrical equipment’s and Carry out Preventive Maintenance. Carry out repair and maintenance of electrical installations at workplace in accordance with the manufacturer’s instructions and organizational requirements.

Duration: 30Hours			Theory:  03Hours				Practice: 27 Hours			Credit Hours	03

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Analyze Fault in Electrical Installations | Trainee will be able to: - Inspect visually the electrical wiring, fixtures, equipment, soldering, connection, appliances and machinery for discovering the faults and defects - Check the installation for consistency with the electrical drawing - Draw the layout of equipment's before disassembling of electrical components - Check the faulty components with scope or meter - Re assembled the components as per drawing and the installation | The trainees must be able to understand: - Interpretation of layout diagrams, technical sketches, graphic symbols, wiring diagrams, and manufacturer’s specifications etc. - Types of electrical tools used for testing and preventive maintenance purposes - Methods of tracing the fault Practical Task: Analyze and repair Electrical wiring of the class room | Th-1.5Hrs. Pr-12Hrs. Total13.5Hrs. | Multi meter, Megger, Electrical tool kit, Mechanical tool kit, Battery Cleaning Kit, Earth Tester, Filler gauge, Generator, | Class Room and workshop |
| - Repair Fault in Electrical Installations | - Prepare a list of items/material(s) required for repair /replacement as per specifications - Draw circuit diagram of electrical equipment's be disassembling - Make necessary adjustments in the control and protective switchgear - Replace defective control & protective switch gear, cables and accessories with standard items - Replace defective earth electrode & faulty/damaged earthling conductors - Test installed electrical equipment for safe and optimum performance according to standards & regulations - Record the results of the test performed on a standard format | - Tools/equipment required for repair and maintenance - Various tests in Electrical Installations Practical Task: Perform repairing task for given scenario | Th-1.5Hrs. Pr-15Hrs. Total16.5Hrs. | Multi meter, Megger, Electrical tool kit, Mechanical tool kit, Battery Cleaning Kit, Earth Tester, Filler gauge, Generator, | Class Room and workshop |

### Carry Out Manual Electrical Planning and Estimation

Objective: This module covers the knowledge and  skills required to analyse customer requirement and specification, Plan and estimate domestic electric work, Plan and estimate commercial   electric work and Plan and estimate industrial electric work This module covers the skills and knowledge in the estimation, planning and installation of an electrical work, keeping in view the necessary rules and regulations.

Duration: 33Hours			Theory: 09Hours				Practice: 24Hours			Credit Hours	3.3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Analyze customer requirement and specification | Trainee will be able to: - Draw the general value chain of the end user. - Highlight the various stages and set of activities in the value chain drawing - Enlist the electrical appliances/materials required in electrical development process - Identify critical stages in the development - Identify the safety aspect required in the critical stages of the development - Enlist the possible energy efficient appliance/devices and global trends in electrical works - Analyze the client requirement at broad level. - Generate a report of various stages of electrical works. - Proposed appliance/materials as per global trends and clarify the technical specification. | The trainees must be able to understand: - term ‘value chain’ of industry. - human machine interface (HMI) - Standard operating procedure (SOP) of the organization for control panel development process. - General arrangement drawing - IEC standards - Basic communication skills - Report writing. - Proposal writing. | Th-03Hrs. Pr-06Hrs. Total- 09Hrs. |  | Class Room and workshop |
| Plan and estimate domestic electric work | Trainee will be able to: - Plan the client requirement at broad level from the proposal. - Plan the electrical appliances/materials / used in different stages of the electrical development process - Plan and estimate electrical wiring - Estimate Installation and Material Cost - Estimate Power consumption for lighting and appliances - Plan a main and sub distribution board. - Ensure safety system. | The trainees must be able to understand: - Standard of electrical components - Standard of electronic component. - Planning procedure. - Estimation procedure. - Energy saving techniques - Home appliances standards | Th-03Hrs. Pr-06Hrs. Total- 9Hrs. |  | Class Room and workshop |
| Plan and estimate commercial electric work. | Trainee will be able to: - Analyze the client requirement at broad level from the proposal. - Plan the electrical equipment /appliances/materials / used in different stages of the commercial electrical work - Plan and estimate electrical wiring - Estimate Installation and Material Cost - Estimate Power consumption for centralize lighting, heating, cooling system and other appliances. - Plan a main and sub distribution board. - Ensure safety measures in development process. - Enlist the material required. | The trainees must be able to understand: - Market Demands - Quality assurance as per client demand - Safety Hazard | Th-02Hrs. Pr-06Hrs. Total- 08Hrs. |  | Class Room and workshop |
| Plan and estimate industrial electric work. | Trainee must be able to: - Analyze the client requirement at broad level from the proposal. - Plan the electrical equipment /appliances/materials / used in different stages of the commercial electrical work - Plan and estimate electrical wiring - Estimate Installation and Material Cost - Estimate Power consumption for centralize lighting, heating, cooling system and other appliances. - Plan 3-phase line for heavy loads - Plan a separate control panel box for heavy machinery. - Plan a main and sub distribution board. - Design a safety system for protection of machinery and labor. - Assign color scheme for safety measures | The trainees must be able to understand: - QA as per Industries demand. | Th-01Hrs. Pr-06Hrs. Total- 07Hrs. |  |  |

# List of Personal Protective Equipment

(FOR A CLASS OF 25 STUDENTS)

| Name of Trade |  | Electrical Technology Diploma Level 5 |  |
| --- | --- | --- | --- |
| Duration of Course |  | 36 Months |  |
| Sr. # |  | Description |  | Quantity |
| 1. |  | Safety gloves, |  | 30 |
| 2. |  | Appropriate safety glasses, |  | 30 |
| 3. |  | Breathing apparatus, |  | 30 |
| 4. |  | Fire extinguishers, |  | 30 |
| 5. |  | Fire blankets, |  | 30 |
| 6. |  | Respirators, masks, |  | 30 |
| 7. |  | Fire hoses, |  | 04 |
| 8. |  | First aid kits, stretchers and other related tools and gear |  | 10 |

# Complete List of Tools, Equipment, Machines and Consumables

Tools

| S# | Description | Quantity |
| --- | --- | --- |
|  | Wire Stripper. | 25 |
|  | Plier. | 25 |
|  | Long Nose Plier. | 25 |
|  | Insulation Remover. | 25 |
|  | Combination Plier. | 25 |
|  | Cutter Plier | 25 |
|  | Insulation Remover | 25 |
|  | Electrician Tool Kit. | 25 |
|  | Bearing Puller | 25 |
|  | Bench Vice. | 25 |
|  | Spanner. | 25 |
|  | Philips Screw Drivers Set | 25 |
|  | Winding Tools | 25 |
|  | Safety Tools. | 25 |
|  | Set Of Screw Drivers | 25 |
|  | Set Of Nose Pliers | 25 |
|  | Combination Plier Set | 25 |
|  | Cutter Plier | 25 |
|  | Lathe Cutting Tool | 25 |
|  | Steel Foot Rule | 25 |
|  | Center Drill Bit | 25 |
|  | Hand Sheet Cutter | 25 |
|  | Tool Post Key | 25 |
|  | Drill Chuck | 25 |
|  | Flat File | 25 |
|  | Drills Of Required Dia | 25 |
|  | Right Hand Side Facing Tool | 25 |
|  | Right Hand Turing Tool | 25 |
|  | Knurling Tool | 25 |
|  | Parting Tool | 25 |
|  | Boring Bar | 25 |
|  | Steel Rule | 25 |
|  | Drill Chuck | 25 |
|  | Flat File | 25 |
|  | Drills Bits Of Required Dia | 25 |
|  | Reamer Dia 12 Mm | 25 |
|  | Wood Saws | 25 |
|  | Wood Jackplane | 25 |
|  | Wood Marking Tools | 25 |
|  | Die Set | 25 |
|  | Pipe Vice | 25 |
|  | Pipe Cutter | 25 |
|  | Electrode Holder | 25 |
|  | Tap & Die Set | 25 |
|  | Thread Gauge | 25 |
|  | Tri-Square | 25 |
|  | Grinding Gauge | 25 |
|  | Work Bench | 25 |
|  | Bench Vice | 25 |
|  | Hammer | 25 |
|  | Tri-Square | 25 |
|  | Hand Hacksaw | 25 |
|  | Scriber | 25 |
|  | Flat File | 25 |
|  | Tool Bit | 25 |
|  | Wheel Dresser | 25 |
|  | Dead Center | 25 |
|  | Surface Gauge | 25 |
|  | Angle Gauge | 25 |
|  | Threads Gauge | 25 |
|  | Number/Alphabet Punch | 25 |
|  | MS Flats | 25 |
|  | Chipping Hammer | 25 |
|  | Wire Brush | 25 |
|  | Face Shield | 25 |
|  | Electrode Holder | 25 |
|  | Electrical Measuring Tools | 25 |
|  | Wire Stripper | 25 |
|  | Wire Gauge | 25 |
|  | Drawing Tools | 25 |
|  | Drawing Board | 25 |
|  | Electrical Wiring Accessories | 25 |
|  | Tool Cleaning Kit | 25 |
|  | Tri-Square | 25 |
|  | Set Square | 25 |
|  | Temples | 25 |
|  | Geometry | 25 |
|  | Chain Block | 25 |
|  | Crimping Tool | 25 |
|  | Knife Installation Kit | 25 |
|  | Knife. | 25 |
|  | Pre Electroplating Tools. | 25 |
|  | Cleaning Solvents | 25 |
|  | Re-Electroplating Tools. | 25 |
|  | Tweezers | 25 |
|  | Test Bench | 25 |
|  | Test Probes | 25 |
|  | Wrenches | 25 |
|  | Box End Wrench Insulated. | 25 |
|  | Socket Wrench, Insulated. | 25 |
|  | Torque Wrench Calibrated In Inch-Pounds, Insulated. | 25 |
|  | Rubber Hammer. | 25 |
|  | Phase Tester. | 25 |
|  | Neon Tester | 25 |
|  | Allen Key Set | 25 |

Equipment

| S# | Description | Quantity |
| --- | --- | --- |
|  | Soldering Iron | 25 |
|  | PCB Kits | 25 |
|  | Analog Multimeter | 25 |
|  | Digital Multimeter | 25 |
|  | Wattmeter | 25 |
|  | Voltmeter | 25 |
|  | Ammeter | 25 |
|  | Megger | 10 |
|  | AVO Meter. | 25 |
|  | Multimeter | 25 |
|  | Galvanized Wire. | 200 Mtr. |
|  | RPM Meter. | 10 |
|  | Phase Sequence Meter | 25 |
|  | Clamp Meter | 25 |
|  | Continuity Tester | 25 |
|  | AC/DC Supply Source | 10 |
|  | Protection Equipment. | 25 |
|  | Variable Power Supply | 10 |
|  | Power Factor Meter | 15 |
|  | Transformer. | 25 |
|  | Timer/Time Relay. | 50 |
|  | Compressor. | 25 |
|  | D.C. Power Supply Unit. | 10 |
|  | Multimeter. (With Option Of Capacitance Measurement). | 25 |
|  | Rheostat. | 25 |
|  | Horse Shoe Magnet. | 25 |
|  | D.C Analog Or Preferably Digital Voltmeter Range 0-50V. | 25 |
|  | Variable D.C Powers Supply 0-30 Voltas. | 15 |
|  | Galvanometer | 25 |
|  | Three Phase Load (3 Phase Motor) | 25 |
|  | Coil | 25 |
|  | Breadboard. | 25 |
|  | Compass Needle | 25 |
|  | Bar Magnet | 25 |
|  | Magnet. | 25 |
|  | Outside Caliper. | 25 |
|  | FM & AM Trainer | 10 |
|  | FM & AM Demodulation Trainers | 10 |
|  | RLC Meter | 25 |
|  | Theodolite | 25 |
|  | Power Factor Meter | 25 |
|  | Insulators For Transmission | 100 Mtr. |
|  | Poles | 15 |
|  | Lightning Arrestor | 10 |
|  | Earthing Loop | 10 |
|  | Impedance Meter | 25 |
|  | Flashlight | 10 |
|  | Electrical & Electronics Trainer For Experiments | 10 |
|  | Center Drill | 10 |
|  | Vernier Caliper | 25 |
|  | Power Cables | 25 |
|  | Multimedia | 2 |
|  | MS Office | 2 |
|  | Plotter | 1 |
|  | Drafting Table | 25 |
|  | Magnetic Compass | 25 |
|  | Armature Core | 25 |
|  | Armature Coils | 25 |
|  | Cammutator | 25 |
|  | Armature | 25 |
|  | Carbon Brush | 25 |
|  | Carbon Brush Holder | 25 |
|  | Rocker | 10 |
|  | Variable Load | 15 |
|  | Dynamometer | 10 |
|  | Tachometer | 15 |
|  | Variable DC Supply | 10 |
|  | 3 Point Starter | 15 |
|  | Brake Test Equipment | 10 |
|  | 4 Point DC Starter | 10 |
|  | Phase Angle Meter. | 15 |
|  | Thermometer | 25 |
|  | Frequency Meter | 20 |
|  | OHM Meter | 20 |
|  | Connecting Wires | 25 |
|  | Cam Switch. | 75 |
|  | Magnetic Contactors | 100 |
|  | Star/Delta Starter | 25 |
|  | Micro Meter Screw Gauge | 25 |
|  | Oil Sensor For Generator | 15 |
|  | Temperature Sensor For Generator | 15 |
|  | Fuel Sensor For Generator | 15 |
|  | Display Panel Of Generator | 10 |
|  | Earth Tester | 10 |
|  | Filler Gauge | 15 |
|  | Battery | 5 |
|  | Drawing Board/Table | 25 |
|  | Keyboard | 25 |
|  | Mouse | 25 |
|  | Dvds, Cds Etc. | 10 |
|  | Relevant Software Disks | 10 |
|  | 3 Phase Starter | 15 |
|  | Electro Dynamometer Apparatus | 20 |
|  | Stroboscope | 25 |
|  | 3 Phase DOL Starter | 25 |
|  | 3 Phase Auto Transformer Starter | 25 |
|  | 3 Phase Rheostat | 25 |
|  | 3 Phase Supply Synchronizing Panel | 25 |
|  | DC Motor Starter | 25 |
|  | Variable Field Resistance | 25 |
|  | Potentiometer 500 O | 15 |
|  | Power Electronics Trainer Kit | 10 |
|  | Electronic Hygrometer | 10 |
|  | Anemometer | 10 |
|  | Electronic Pressure Gauge | 10 |
|  | Simulating Software(Emulator) | 15 |
|  | Sensors/Transducers | 25 |
|  | Analog Telephone Set | 10 |
|  | Digital Telephone Set | 10 |
|  | Amplitude Modulation / Demodulation Trainer | 05 |
|  | Frequency Modulation Trainer | 05 |
|  | FM Demodulation Trainers | 05 |

Machines

| S# | Description | Quantity |
| --- | --- | --- |
|  | Soldering Iron | 25 |
|  | Washing Machine | 10 |
|  | Dryer. | 10 |
|  | Juicer. | 10 |
|  | Grinder. | 10 |
|  | Sandwich Maker. | 10 |
|  | Toaster | 10 |
|  | Refrigerator. | 5 |
|  | Air Conditioner. | 5 |
|  | Exhaust Fan | 10 |
|  | Fan | 15 |
|  | AC/DC Supply Source | 5 |
|  | D.C. Power Supply Unit. | 5 |
|  | Variable Power Supply | 5 |
|  | Transformer. | 15 |
|  | Single Phase Transformers. | 2 |
|  | Three Phase Transformer. | 2 |
|  | Auto- Transformer | 2 |
|  | Center Tapped Transformer | 5 |
|  | Cathode-Ray Oscilloscope. | 3 |
|  | Oscillator/Signal Generator. | 10 |
|  | Function Generator. | 15 |
|  | Drill Machine With Different Drill Bits. | 5 |
|  | Pedestal Grinder | 2 |
|  | Spot Welding Machine (0.5 Mm MS Sheets) | 2 |
|  | Seam Welding Machine (0.5 Mm MS Sheet) | 2 |
|  | Welding Transformer Or Welding Rectifier | 2 |
|  | TIG/MIG Welding Plant | 2 |
|  | Flash Back Arrester | 2 |
|  | Spark Lighter | 2 |
|  | Back Fire Arrester, | 2 |
|  | Center Drill Machine | 5 |
|  | Grinding Machine | 5 |
|  | Shearing Machine | 5 |
|  | Lathe Machine | 5 |
|  | Universal Milling Machine | 5 |
|  | CNC Lathe Machine | 2 |
|  | CNC Milling Machine | 2 |
|  | Surface Grinder Machine | 5 |
|  | Computer | 25 |
|  | Printer. | 2 |
|  | Photo Copier | 1 |
|  | Scanner | 2 |
|  | Plotter | 1 |
|  | 3 Phase Motor | 2 |
|  | Universal Motor | 2 |
|  | DC Motors | 2 |
|  | 3 Phase Motor 2 Speed | 2 |
|  | Single Phase Induction Motor | 2 |
|  | Stepper Motor | 2 |
|  | 2 DC Machine Mechanically Coupled | 2 |
|  | Rewinding Machine | 2 |
|  | Single Phase Shaded Pole Motor | 2 |
|  | 3 Phase Special Purpose Motor | 2 |
|  | 3 Phase Wound Rotor Motors With Coupled Shafts | 2 |
|  | 3 Phase Synchronous Motor Coupled With DC Shunt Motor | 2 |
|  | Diesel Generator | 2 |
|  | Petrol Generator | 2 |
|  | Alternator | 2 |
|  | Simple Loop Generator | 10 |
|  | Variable DC Supply | 10 |
|  | Synchrony Transmitter & Receiver | 2 |
|  | Analog Telephone Set | 5 |
|  | Digital Telephone Set | 5 |
|  | Cordless Telephone | 5 |
|  | Signal Generator | 5 |
|  | Dish Receiver | 2 |
|  | Dish Antenna | 2 |
|  | TV Receiver | 2 |
|  | PBX | 2 |
|  | Crane | 1 |
|  | Flashlight | 5 |

Consumable

| S# | Description | Quantity |
| --- | --- | --- |
|  | Cables. | As required according to Practical |
|  | Wires. | As required according to Practical |
|  | Solder Wire. | As required according to Practical |
|  | Soldering Paste | As required according to Practical |
|  | PCB | As required according to Practical |
|  | Socket Of All Types | As required according to Practical |
|  | Switches Of All Types | As required according to Practical |
|  | Distribution Board (DB) | As required according to Practical |
|  | Miniature Circuit Breaker (MCB) | As required according to Practical |
|  | Molded Case Circuit Breaker (MCCB) | As required according to Practical |
|  | Residual Current Device (RCD) | As required according to Practical |
|  | Earth Leakage Circuit Breaker (ELCB) | As required according to Practical |
|  | Earth Plate. | As required according to Practical |
|  | PVC Pipe/Duct. | As required according to Practical |
|  | PVC Clamp. | As required according to Practical |
|  | Wooden/PVC Board. | As required according to Practical |
|  | PVC Wire According To Load | As required according to Practical |
|  | Screw | As required according to Practical |
|  | Single Pole And Two Pole Switch. | As required according to Practical |
|  | Bulb Holder | As required according to Practical |
|  | Bulb | As required according to Practical |
|  | Test Indicator | As required according to Practical |
|  | Capacitor. | As required according to Practical |
|  | Bearing | As required according to Practical |
|  | Duct Rod. | As required according to Practical |
|  | Gloves. | As required according to Practical |
|  | Wire. | As required according to Practical |
|  | Gas | As required according to Practical |
|  | Circuit Boards | As required according to Practical |
|  | Tube Light. | As required according to Practical |
|  | Tube Patti. | As required according to Practical |
|  | Chock. | As required according to Practical |
|  | Starter. | As required according to Practical |
|  | Sleeves | As required according to Practical |
|  | Series Board | As required according to Practical |
|  | Impulse Switch | As required according to Practical |
|  | Power Plug. | As required according to Practical |
|  | Three Pin Socket. | As required according to Practical |
|  | Three Pin Switch | As required according to Practical |
|  | Bell | As required according to Practical |
|  | Bell Button | As required according to Practical |
|  | Iron Nail As Core. | As required according to Practical |
|  | Thin Coated Copper Wire. | As required according to Practical |
|  | Current Carrying Conductor. | As required according to Practical |
|  | Capacitors Of Different Ratings | As required according to Practical |
|  | Bridging Plugs. | As required according to Practical |
|  | Connecting Leads. | As required according to Practical |
|  | Dry Cell Battery. | As required according to Practical |
|  | Capacitor (Sanyo Operated Volts 6.3 V, SE 30) | As required according to Practical |
|  | Resistor Of Different Ratings. | As required according to Practical |
|  | L.E.D (3 To 9 V) Optional. | As required according to Practical |
|  | Incandescent Lamp Of Different Watts. | As required according to Practical |
|  | Small Pieces Of Copper Wire. | As required according to Practical |
|  | Cotton Cloth | As required according to Practical |
|  | Lubricants | As required according to Practical |
|  | Brush | As required according to Practical |
|  | M.S Round Bar | As required according to Practical |
|  | Oxygen Cylinder, | As required according to Practical |
|  | Acetylene Gas Cylinder, | As required according to Practical |
|  | Rubber House Pipe, | As required according to Practical |
|  | Extension Leads | As required according to Practical |
|  | Electrode | As required according to Practical |
|  | Drawing Sheet, | As required according to Practical |
|  | Insulation Tape | As required according to Practical |
|  | Cables | As required according to Practical |
|  | Spark Plugs. | As required according to Practical |
|  | HT Leads | As required according to Practical |
|  | Graph And Drawing Sheet | As required according to Practical |
|  | Clutch Pencil | As required according to Practical |
|  | Calculation Sheet | As required according to Practical |
|  | Calculator | As required according to Practical |
|  | Psychometric Charts And Tables | As required according to Practical |
|  | Rust Removing Agents | As required according to Practical |
|  | Thermometer | As required according to Practical |
|  | MATLAB Software | As required according to Practical |
|  | P-Spice Software | As required according to Practical |
|  | PLC Software | As required according to Practical |
|  | Safety Signs | As required according to Practical |
|  | Hand Gloves. | As required according to Practical |
|  | Alkalis | As required according to Practical |
|  | Antidotes | As required according to Practical |
|  | Acids | As required according to Practical |
|  | Electroplate Solution. | As required according to Practical |
|  | Laboratory Dress | As required according to Practical |
|  | Cyanides | As required according to Practical |
|  | Hand Gloves | As required according to Practical |
|  | Brass Solution For Cyanide. | As required according to Practical |
|  | Different Colors For Plating | As required according to Practical |
|  | Electrodes. | As required according to Practical |
|  | Different Inductors | As required according to Practical |
|  | Different AC & DC Capacitors | As required according to Practical |
|  | Different Metals | As required according to Practical |
|  | 2 Pole Single Way Switch | As required according to Practical |
|  | 2 Pole 2 Way Switch | As required according to Practical |
|  | Transformer Oil | As required according to Practical |
|  | Transformer Oil Testing Set | As required according to Practical |
|  | Buffer | As required according to Practical |
|  | Electroplates | As required according to Practical |
|  | Centrifugal Switch | As required according to Practical |
|  | 3 Pole 2 Way Switch | As required according to Practical |
|  | Diode | As required according to Practical |
|  | Transistors | As required according to Practical |
|  | Bread Board | As required according to Practical |
|  | Data Sheets | As required according to Practical |
|  | Zener Diode | As required according to Practical |
|  | FET Transistor | As required according to Practical |
|  | MOSFET Transistor | As required according to Practical |
|  | UJT & BJT | As required according to Practical |
|  | SCR | As required according to Practical |
|  | Thyristor | As required according to Practical |
|  | DIAC | As required according to Practical |
|  | TRIAC | As required according to Practical |
|  | Op-Amplifier | As required according to Practical |
|  | AND Gate (7408 2-Input Quad) | As required according to Practical |
|  | OR Gate (7432 2-Input Quad) | As required according to Practical |
|  | NOT Gate (7404 Hex) | As required according to Practical |
|  | NAND Gate (7400 2-Input Quad) | As required according to Practical |
|  | NOR Gate (7402 2-Input Quad) | As required according to Practical |
|  | X-OR Gate (7486 2-Input Quad) | As required according to Practical |
|  | X-NOR Gate (74266 2-Input Quad) | As required according to Practical |
|  | Schottky Diodes | As required according to Practical |
|  | IC 7408 | As required according to Practical |
|  | Power Diodes | As required according to Practical |
|  | General Purpose Diode | As required according to Practical |
|  | Resistor Of 1to100 K Ohms | As required according to Practical |
|  | Power MOSFET IRF 840 | As required according to Practical |
|  | IC 7410 | As required according to Practical |
|  | Power Diode 1N4007 | As required according to Practical |
|  | DC Source 12V | As required according to Practical |
|  | IC 7404 | As required according to Practical |
|  | Controller IC | As required according to Practical |
|  | Firing Circuit | As required according to Practical |
|  | Power Diode 1N4007 | As required according to Practical |
|  | Psychometrics Chart | As required according to Practical |
|  | Data Loggers | As required according to Practical |
|  | HDMI CABLE | As required according to Practical |
|  | HMI Software For PLC | As required according to Practical |
|  | Change Over Switch | As required according to Practical |
|  | Wooden/Glass Rod | As required according to Practical |
|  | H2 SO4 | As required according to Practical |
|  | Different Glass Reflectors | As required according to Practical |
|  | Different Types Of Paints | As required according to Practical |
|  | HT & LT Conductors. | As required according to Practical |
|  | Fuses | As required according to Practical |
|  | RJ-11 Connectors | As required according to Practical |
|  | VGA Cable. | As required according to Practical |
|  | Coaxial Cable. | As required according to Practical |
|  | Nitric Acid | As required according to Practical |
|  | Copper Coated Sheet | As required according to Practical |
|  | DC Capacitors of Different Range. | As required according to Practical |

List of Stationary for 3 Years

| S# | Description | Quantity |
| --- | --- | --- |
|  | Handbooks | 25 |
|  | Design books | 25 |
|  | Pencils | 300 |
|  | Rubber | 300 |
|  | Sharpeners | 300 |
|  | Paper Cutter | 50 |
|  | Seizers | 25 |
|  | Colors | 15 each color (Read, Green, Yellow, Blue, white and Black) |
|  | White charts | 50 Nos. |
|  | Brown sheets | 100 Nos. |
|  | White board markers | 15 Dozen |
|  | Permanent markers | 3 Dozen |
|  | File cover and files | 50 Nos. |
|  | A4 Paper | 150 Ream |

Learning hours in training provider premises,

Training workshop, laboratory and on-the-job workplace