Instruction Sheet for the Candidate

| Qualification | AC Machines (Transformer) |
| --- | --- |
| Competency Standard | Perform Tests On Auto Transformer |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name______________________________________________________ Registration/Roll Number_______________________________________ |
| Guidance for Candidate | To meet this standard, you are required to complete the following within time frame (for practical demonstration & assessment): - Perform open circuit Test of auto transformer. - Perform short circuit test of auto transformer - Calculate efficiency of auto transformer. |
| Time: 03 Hrs. | During a practical assessment, under observation by an assessor, you are required to |
| Minimum Evidence Required | Perform open circuit Test of auto transformer. - Connect watt meter, ampere meter, and volt meter to the lower voltage side of transformer. - Open the high voltage side of transformer. - Apply rated voltage to lower voltage side of transformer. - Read the instrument/meters reading. - Calculate iron losses and excitation branch component (Ro, Xo). Perform short circuit test of auto transformer - Connect watt meter, ampere meter, and volt meter to the higher voltage side of transformer. - Connect lower voltage side terminal with each other (Short Circuit) - Apply 10 % to 15 % of rated voltage to higher voltage side of transformer. - Read the instrument/meters readings. - Calculate copper losses and winding component (Ro1, Xo1) Calculate efficiency of auto transformer. - Perform open circuit test. - Perform short circuit test. - Calculate iron losses and copper losses from above tests. - Calculate input power and output power. - Calculate efficiency from calculated powers. |

Self-Assessment Checklist

| Candidate Name |  |
| --- | --- |
| Registration No. |  |
| Qualification | AC Machines (Transformer) |
| Competency Standard | Perform Tests On Auto Transformer |
| Purpose of Assessment | Formative Assessment |
| Assessment Task | - Perform open circuit Test of auto transformer. - Perform short circuit test of auto transformer - Calculate efficiency of auto transformer. |

I can……………….

| Performance Criteria | Yes | No |
| --- | --- | --- |
| - Connect watt meter, ampere meter, and volt meter to the lower voltage side of transformer. |  |  |
| - Open the high voltage side of transformer. |  |  |
| - Apply rated voltage to lower voltage side of transformer. |  |  |
| - Read the instrument/meters reading. |  |  |
| - Calculate iron losses and excitation branch component (Ro, Xo). |  |  |
| - Connect watt meter, ampere meter, and volt meter to the higher voltage side of transformer. |  |  |
| - Connect lower voltage side terminal with each other (Short Circuit) |  |  |
| - Apply 10 % to 15 % of rated voltage to higher voltage side of transformer. |  |  |
| - Read the instrument/meters readings. |  |  |
| - Calculate copper losses and winding component (Ro1, Xo1) |  |  |
| - Perform open circuit test. |  |  |
| - Perform short circuit test. |  |  |
| - Calculate iron losses and copper losses from above tests. |  |  |
| - Calculate input power and output power. |  |  |
| - Calculate efficiency from calculated powers. |  |  |

Candidate’s Signature__________________ Assessor’s Signature____________________

Date: _______________________________

Assessors Judgment Guide

| Qualification | AC Machines (Transformer) |
| --- | --- |
| Competency Standard | Perform Tests On Auto Transformer |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name: ______________________________________________________________ Registration/Roll Number: ______________________ Signature: _______________ |
| Assessment Outcome | COMPETENT NOT YET COMPETENT Name of the Assessor________________________________________________ Assessor’s code:____________________________________________________ Signature: ________________________________ |

| Assessment Summary (to be filled by the assessor) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Activity | Method |  |  |  |  | Result |  |
| Nature of Activity | Written | Oral | Observation | Portfolio | Role Play | Competent | Not Yet Competent |
| Practical Skill Demonstration |  |  |  |  |  |  |  |
| Knowledge Assessment |  |  |  |  |  |  |  |
| Other Requirement |  |  |  |  |  |  |  |

Observation Checklist

| Assessment Task |  | - Perform open circuit Test of auto transformer. - Perform short circuit test of auto transformer - Calculate efficiency of auto transformer. |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| During the practical assessment, candidate demonstrated the following: |  |  |  | Yes | No | Remarks |
|  | Connected watt meter, ampere meter, and volt meter to the lower voltage side of transformer. |  |  |  |  |  |
|  | Opened the high voltage side of transformer. |  |  |  |  |  |
|  | Applied rated voltage to lower voltage side of transformer. |  |  |  |  |  |
|  | Read the instrument/meters reading. |  |  |  |  |  |
|  | Calculated iron losses and excitation branch component (Ro, Xo). |  |  |  |  |  |
|  | Connected watt meter, ampere meter, and volt meter to the higher voltage side of transformer. |  |  |  |  |  |
|  | Connected lower voltage side terminal with each other (Short Circuit) |  |  |  |  |  |
|  | Applied 10 % to 15 % of rated voltage to higher voltage side of transformer. |  |  |  |  |  |
|  | Read the instrument/meters readings. |  |  |  |  |  |
|  | Calculated copper losses and winding component (Ro1, Xo1) |  |  |  |  |  |
|  | Performed open circuit test. |  |  |  |  |  |
|  | Performed short circuit test. |  |  |  |  |  |
|  | Calculated iron losses and copper losses from above tests. |  |  |  |  |  |
|  | Calculated input power and output power. |  |  |  |  |  |
|  | Calculated efficiency from calculated powers. |  |  |  |  |  |
| Competent |  |  | Not Yet Competent |  |  |  |

Knowledge Assessment

| Qualification | AC Machines (Transformer) |
| --- | --- |
| Competency Standard | Perform Tests On Auto Transformer |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name:______________________________________________________________ Registration/Roll Number: _________________ Candidate Signature:___________ |
| Assessment Outcome | COMPETENT NOT YET COMPETENT Name of the Assessor:________________________________________________ Assessor’s code:____________________________________________________ Signature of the Assessor:_______________________ |

Candidate’s response is not required to be identical, but similar concepts and/or keywords must be used. Oral questioning may be used to clarify candidate understanding of topic and its application.

| Questions (Candidate confidently answered questions correctly and demonstrated understanding of the topics and their application) |  | Satisfactory | Not Satisfactory |
| --- | --- | --- | --- |
|  | How to use watt meter ? |  |  |
|  | Why we perform open circuit test in transformer? |  |  |
|  | Why we perform short circuit test in transformer? |  |  |
|  | What is copper loss? |  |  |
|  | How to calculate efficiency of auto transformer by using open circuit and short circuit tests data? |  |  |

Feedback to the Candidate

Candidate’s Signature__________________ Assessor’s Signature _________________