Instruction Sheet for the Candidate

| Qualification | AC Machines (Transformer) |
| --- | --- |
| Competency Standard | Perform Tests On Single Phase Transformer. |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name______________________________________________________ Registration/Roll Number_______________________________________ |
| Guidance for Candidate | To meet this standard, you are required to complete the following within time frame (for practical demonstration & assessment): - Perform polarity test of single phase transformer. - Perform Open circuit test of transformer. - Perform Short circuit Test of Transformer. - Calculate efficiency of transformer by direct method. - Calculate efficiency of transformer by Back to Back test. |
| Time: 05 Hrs. | During a practical assessment, under observation by an assessor, you are required to |
| Minimum Evidence Required | Perform polarity test of single phase transformer - Connect the circuit according to the diagram. - Note the reading of both volt meter. - Identify additive and subtractive polarity. - Mark the terminal according to the additive and subtractive polarity. Perform Open circuit test of transformer. - Connect watt meter, ampere meter, and volt meter to the lower voltage side of transformer. - Open the high voltage side of transformer. - Apply rated voltage to lower voltage side of transformer. - Read the instrument/meters reading. - Calculate iron losses and excitation branch component (Ro, Xo). Perform Short circuit Test of Transformer. - Connect watt meter, ampere meter, and volt meter to the higher voltage side of transformer. - Connect lower voltage side terminal with each other (Short Circuit) - Apply 10 % to 15 % of rated voltage to higher voltage side of transformer. - Read the instrument/meters readings. - Calculate copper losses and winding component (Ro1, Xo1) Calculate efficiency of transformer by direct method. - Perform open circuit test. - Perform short circuit test. - Calculate iron losses and copper losses from above tests. - Calculate input power and output power. - Calculate efficiency from calculated powers. Calculate efficiency of transformer by Back to Back test. - Identify two transformer of same rating. - Connect both transformer in parallel. - Connect another variable voltage transformer to secondary side of parallel transformers. - Connect a switch, watt meter and ammeter between variable voltage transformer and parallel transformer. - Connect voltmeter and watt meter to primary side of transformer parallel transformer. - Apply rated voltage to the primary side of the parallel transformers. - Open the switch. - Calculate iron losses. - Close the switch - Adjust the voltage of variable voltage transformer until the full load current passes from secondary side of parallel transformers. - Calculate copper losses. - Calculate efficiency from above calculated losses. |

Self-Assessment Checklist

| Candidate Name |  |
| --- | --- |
| Registration No. |  |
| Qualification | AC Machines (Transformer) |
| Competency Standard | Perform Tests On Single Phase Transformer. |
| Purpose of Assessment | Formative Assessment |
| Assessment Task | - Perform polarity test of single phase transformer. - Perform Open circuit test of transformer. - Perform Short circuit Test of Transformer. - Calculate efficiency of transformer by direct method. - Calculate efficiency of transformer by Back to Back test. |

I can……………….

| Performance Criteria | Yes | No |
| --- | --- | --- |
| - Connect the circuit according to the diagram. |  |  |
| - Note the reading of both volt meter. |  |  |
| - Identify additive and subtractive polarity. |  |  |
| - Mark the terminal according to the additive and subtractive polarity. |  |  |
| - Connect watt meter, ampere meter, and volt meter to the lower voltage side of transformer. |  |  |
| - Open the high voltage side of transformer. |  |  |
| - Apply rated voltage to lower voltage side of transformer. |  |  |
| - Read the instrument/meters reading. |  |  |
| - Calculate iron losses and excitation branch component (Ro, Xo). |  |  |
| - Connect watt meter, ampere meter, and volt meter to the higher voltage side of transformer. |  |  |
| - Connect lower voltage side terminal with each other (Short Circuit) |  |  |
| - Apply 10 % to 15 % of rated voltage to higher voltage side of transformer. |  |  |
| - Read the instrument/meters readings. |  |  |
| - Calculate copper losses and winding component (Ro1, Xo1) |  |  |
| - Perform open circuit test. |  |  |
| - Perform short circuit test. |  |  |
| - Calculate iron losses and copper losses from above tests. |  |  |
| - Calculate input power and output power. |  |  |
| - Calculate efficiency from calculated powers. |  |  |
| - Identify two transformer of same rating. |  |  |
| - Connect both transformer in parallel. |  |  |
| - Connect another variable voltage transformer to secondary side of parallel transformers. |  |  |
| - Connect a switch, watt meter and ammeter between variable voltage transformer and parallel transformer. |  |  |
| - Connect voltmeter and watt meter to primary side of transformer parallel transformer. |  |  |
| - Apply rated voltage to the primary side of the parallel transformers. |  |  |
| - Open the switch. |  |  |
| - Calculate iron losses. |  |  |
| - Close the switch |  |  |
| - Adjust the voltage of variable voltage transformer until the full load current passes from secondary side of parallel transformers. |  |  |
| - Calculate copper losses. |  |  |
| - Calculate efficiency from above calculated losses. |  |  |

Candidate’s Signature__________________ Assessor’s Signature____________________

Date: _______________________________

Assessors Judgment Guide

| Qualification | AC Machines (Transformer) |
| --- | --- |
| Competency Standard | Perform Tests On Single Phase Transformer. |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name: ______________________________________________________________ Registration/Roll Number: ______________________ Signature: _______________ |
| Assessment Outcome | COMPETENT NOT YET COMPETENT Name of the Assessor________________________________________________ Assessor’s code:____________________________________________________ Signature: ________________________________ |

| Assessment Summary (to be filled by the assessor) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Activity | Method |  |  |  |  | Result |  |
| Nature of Activity | Written | Oral | Observation | Portfolio | Role Play | Competent | Not Yet Competent |
| Practical Skill Demonstration |  |  |  |  |  |  |  |
| Knowledge Assessment |  |  |  |  |  |  |  |
| Other Requirement |  |  |  |  |  |  |  |

Observation Checklist

| Assessment Task |  | - Perform polarity test of single phase transformer. - Perform Open circuit test of transformer. - Perform Short circuit Test of Transformer. - Calculate efficiency of transformer by direct method. - Calculate efficiency of transformer by Back to Back test. |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| During the practical assessment, candidate demonstrated the following: |  |  |  | Yes | No | Remarks |
|  | Connected the circuit according to the diagram. |  |  |  |  |  |
|  | Noted the reading of both volt meter. |  |  |  |  |  |
|  | Identified additive and subtractive polarity. |  |  |  |  |  |
|  | Marked the terminal according to the additive and subtractive polarity. |  |  |  |  |  |
|  | Connected watt meter, ampere meter, and volt meter to the lower voltage side of transformer. |  |  |  |  |  |
|  | Opened the high voltage side of transformer. |  |  |  |  |  |
|  | Applied rated voltage to lower voltage side of transformer. |  |  |  |  |  |
|  | Read the instrument/meters reading. |  |  |  |  |  |
|  | Calculated iron losses and excitation branch component (Ro, Xo). |  |  |  |  |  |
|  | Connected watt meter, ampere meter, and volt meter to the higher voltage side of transformer. |  |  |  |  |  |
|  | Connected lower voltage side terminal with each other (Short Circuit) |  |  |  |  |  |
|  | Applied 10 % to 15 % of rated voltage to higher voltage side of transformer. |  |  |  |  |  |
|  | Read the instrument/meters readings. |  |  |  |  |  |
|  | Calculated copper losses and winding component (Ro1, Xo1) |  |  |  |  |  |
|  | Performed open circuit test. |  |  |  |  |  |
|  | Performed short circuit test. |  |  |  |  |  |
|  | Calculated iron losses and copper losses from above tests. |  |  |  |  |  |
|  | Calculated input power and output power. |  |  |  |  |  |
|  | Calculated efficiency from calculated powers. |  |  |  |  |  |
|  | Identified two transformer of same rating. |  |  |  |  |  |
|  | Connected both transformers in parallel. |  |  |  |  |  |
|  | Connected another variable voltage transformer to secondary side of parallel transformers. |  |  |  |  |  |
|  | Connected a switch, watt meter and ammeter between variable voltage transformer and parallel transformer. |  |  |  |  |  |
|  | Connected voltmeter and watt meter to primary side of transformer parallel transformer. |  |  |  |  |  |
|  | Applied rated voltage to the primary side of the parallel transformers. |  |  |  |  |  |
|  | Opened the switch. |  |  |  |  |  |
|  | Calculated iron losses. |  |  |  |  |  |
|  | Closed the switch |  |  |  |  |  |
|  | Adjusted the voltage of variable voltage transformer until the full load current passes from secondary side of parallel transformers. |  |  |  |  |  |
|  | Calculated copper losses. |  |  |  |  |  |
|  | Calculated efficiency from above calculated losses. |  |  |  |  |  |
| Competent |  |  | Not Yet Competent |  |  |  |

Knowledge Assessment

| Qualification | AC Machines (Transformer) |
| --- | --- |
| Competency Standard | Perform Tests On Single Phase Transformer. |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name:______________________________________________________________ Registration/Roll Number: _________________ Candidate Signature:___________ |
| Assessment Outcome | COMPETENT NOT YET COMPETENT Name of the Assessor:________________________________________________ Assessor’s code:____________________________________________________ Signature of the Assessor:_______________________ |

Candidate’s response is not required to be identical, but similar concepts and/or keywords must be used. Oral questioning may be used to clarify candidate understanding of topic and its application.

| Questions (Candidate confidently answered questions correctly and demonstrated understanding of the topics and their application) |  | Satisfactory | Not Satisfactory |
| --- | --- | --- | --- |
|  | What is difference between additive and subtractive polarity? |  |  |
|  | Why we connect watt meter, ampere meter, and volt meter to the higher voltage side of transformer in short circuit test? |  |  |
|  | Explain the reason to apply 10 % to 15 % of rated voltage to higher voltage side of transformer. |  |  |
|  | What is copper loss? |  |  |
|  | What is iron loss? |  |  |

Feedback to the Candidate

Candidate’s Signature__________________ Assessor’s Signature _________________