Instruction Sheet for the Candidate

| Qualification | Telecom operator (Power) |
| --- | --- |
| Competency Standard | Maintain Lead Acid Batteries and Implement Their Series Parallel Combination. |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name______________________________________________________ Registration/Roll Number_______________________________________ |
| Guidance for Candidate | To meet this standard, you are required to complete the following within 04 Hrs. time frame (for practical demonstration & assessment): - Construct series combination of batteries. - Construct Parallel combination of batteries. - Prepare Electrolyte for battery - Check specific gravity of Electrolyte. - Determine internal resistance of cell - Charge the battery with the help of Charger. |
| Time: 04 Hrs. | During a practical assessment, under observation by an assessor, you are required to |
| Minimum Evidence Required | Construct series combination of batteries. - Select the specific quantity cells. - Connect them in series with proper polarity. - Measure the voltage of series combined cell. - Increase the number of cells and note the voltage. - Interpret the effect Construct Parallel combination of batteries - Select the specific quantity cells. - Connect them in parallel with proper polarity. - Measure the voltage of parallel combined cell. - Increase the number of cells and note the voltage. - Interpret the effect. Prepare Electrolyte for battery - Select the proper container & and use proper safety equipment to prepare electrolyte - Pour H2SO4 in the container as per specification. - Put the water as per specification into the container and slowly - Mix the mixture with wooden/glass rod so that two solutions mix completely. Check specific gravity of Electrolyte. - Open the vent plug of battery - Fill the hydrometer with electrolyte - Keep the hydrometer vertical and take reading form hydrometer Determine internal resistance of cell - Adjust the apparatus as per diagram. - Turn the switch off and take the reading of voltmeter and note its value as “E”. - Turn on the switch and again take the reading of voltmeter and note its value as “V”. - Note the reading of ammeter as well. - Use above measured values and find out internal resistance using appropriate formula Charge the battery with the help of Charger - Set proper voltage and current setting of charger. - Connect the battery at the output terminal of charger. - Turn on the supply and note the current reading of ammeter from charger. - Remain connect the battery with charger till the ammeter show minimum or zero reading. - Disconnect the battery and check its specific gravity with hydrometer |

Self-Assessment Checklist

| Candidate Name |  |
| --- | --- |
| Registration No. |  |
| Qualification | Telecom operator (Power) |
| Competency Standard | Maintain Lead Acid Batteries and Implement Their Series Parallel Combination. |
| Purpose of Assessment | Formative Assessment |
| Assessment Task |  |

I can……………….

| Performance Criteria | Yes | No |
| --- | --- | --- |
| - Select the specific quantity cells. |  |  |
| - Connect them in series with proper polarity. |  |  |
| - Measure the voltage of series combined cell. |  |  |
| - Increase the number of cells and note the voltage. |  |  |
| - Interpret the effect |  |  |
| - Select the specific quantity cells. |  |  |
| - Connect them in parallel with proper polarity. |  |  |
| - Measure the voltage of parallel combined cell. |  |  |
| - Increase the number of cells and note the voltage. |  |  |
| - Interpret the effect. |  |  |
| - Select the proper container & and use proper safety equipment to prepare electrolyte |  |  |
| - Pour H2SO4 in the container as per specification. |  |  |
| - Put the water as per specification into the container and slowly |  |  |
| - Mix the mixture with wooden/glass rod so that two solutions mix completely. |  |  |
| - Open the vent plug of battery |  |  |
| - Fill the hydrometer with electrolyte |  |  |
| - Keep the hydrometer vertical and take reading form hydrometer |  |  |
| - Adjust the apparatus as per diagram. |  |  |
| - Turn the switch off and take the reading of voltmeter and note its value as “E”. |  |  |
| - Turn on the switch and again take the reading of voltmeter and note its value as “V”. |  |  |
| - Note the reading of ammeter as well. |  |  |
| - Use above measured values and find out internal resistance using appropriate formula |  |  |
| - Set proper voltage and current setting of charger. |  |  |
| - Connect the battery at the output terminal of charger. |  |  |
| - Turn on the supply and note the current reading of ammeter from charger. |  |  |
| - Remain connect the battery with charger till the ammeter show minimum or zero reading. |  |  |
| - Disconnect the battery and check its specific gravity with hydrometer |  |  |

Candidate’s Signature__________________ Assessor’s Signature____________________

Date: _______________________________

Assessors Judgment Guide

| Qualification | Telecom operator (Power) |
| --- | --- |
| Competency Standard | Maintain Lead Acid Batteries and Implement Their Series Parallel Combination. |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name: ______________________________________________________________ Registration/Roll Number: ______________________ Signature: _______________ |
| Assessment Outcome | COMPETENT NOT YET COMPETENT Name of the Assessor________________________________________________ Assessor’s code: ____________________________________________________ Signature: ________________________________ |

| Assessment Summary (to be filled by the assessor) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Activity | Method |  |  |  |  | Result |  |
| Nature of Activity | Written | Oral | Observation | Portfolio | Role Play | Competent | Not Yet Competent |
| Practical Skill Demonstration |  |  |  |  |  |  |  |
| Knowledge Assessment |  |  |  |  |  |  |  |
| Other Requirement |  |  |  |  |  |  |  |

Observation Checklist

| Assessment Task |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| During the practical assessment, candidate demonstrated the following: |  |  |  | Yes | No | Remarks |
|  | Select the specific quantity cells. |  |  |  |  |  |
|  | Connect them in series with proper polarity. |  |  |  |  |  |
|  | Measure the voltage of series combined cell. |  |  |  |  |  |
|  | Increase the number of cells and note the voltage. |  |  |  |  |  |
|  | Interpret the effect |  |  |  |  |  |
|  | Select the specific quantity cells. |  |  |  |  |  |
|  | Connect them in parallel with proper polarity. |  |  |  |  |  |
|  | Measure the voltage of parallel combined cell. |  |  |  |  |  |
|  | Increase the number of cells and note the voltage. |  |  |  |  |  |
|  | Interpret the effect. |  |  |  |  |  |
|  | Select the proper container & and use proper safety equipment to prepare electrolyte |  |  |  |  |  |
|  | Pour H2SO4 in the container as per specification. |  |  |  |  |  |
|  | Put the water as per specification into the container and slowly |  |  |  |  |  |
|  | Mix the mixture with wooden/glass rod so that two solutions mix completely. |  |  |  |  |  |
|  | Open the vent plug of battery |  |  |  |  |  |
|  | Fill the hydrometer with electrolyte |  |  |  |  |  |
|  | Keep the hydrometer vertical and take reading form hydrometer |  |  |  |  |  |
|  | Adjust the apparatus as per diagram. |  |  |  |  |  |
|  | Turn the switch off and take the reading of voltmeter and note its value as “E”. |  |  |  |  |  |
|  | Turn on the switch and again take the reading of voltmeter and note its value as “V”. |  |  |  |  |  |
|  | Note the reading of ammeter as well. |  |  |  |  |  |
|  | Use above measured values and find out internal resistance using appropriate formula |  |  |  |  |  |
|  | Set proper voltage and current setting of charger. |  |  |  |  |  |
|  | Connect the battery at the output terminal of charger. |  |  |  |  |  |
|  | Turn on the supply and note the current reading of ammeter from charger. |  |  |  |  |  |
|  | Remain connect the battery with charger till the ammeter show minimum or zero reading. |  |  |  |  |  |
|  | Disconnect the battery and check its specific gravity with hydrometer |  |  |  |  |  |
| Competent |  |  | Not Yet Competent |  |  |  |

Knowledge Assessment

| Qualification | Telecom operator (Power) |
| --- | --- |
| Competency Standard | Maintain Lead Acid Batteries and Implement Their Series Parallel Combination. |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name: ______________________________________________________________ Registration/Roll Number: _________________ Candidate Signature: ___________ |
| Assessment Outcome | COMPETENT NOT YET COMPETENT Name of the Assessor: ________________________________________________ Assessor’s code: ____________________________________________________ Signature of the Assessor: _______________________ |

Candidate’s response is not required to be identical, but similar concepts and/or keywords must be used. Oral questioning may be used to clarify candidate understanding of topic and its application.

| Questions (Candidate confidently answered questions correctly and demonstrated understanding of the topics and their application) |  | Satisfactory | Not Satisfactory |
| --- | --- | --- | --- |
|  | What is the difference between cell and battery? |  |  |
|  | What is the necessity of series combination of batteries? |  |  |
|  | What is the necessity of parallel combination of batteries? |  |  |
|  | Differentiate between primary cell and secondary cell. |  |  |
|  | Write down charging equation of lead acid battery. |  |  |
|  | What is hydrometer? |  |  |
|  | What is the proportion between H2O (water) and H2SO4 (sulphuric acid) for making electrolyte of Lead acid battery? |  |  |
|  | Define specific gravity. |  |  |
|  | Differentiate between “E” and “V” of a cell. |  |  |
|  | What are different methods used for charging of a battery? |  |  |
|  | Differentiate between constant current and constant voltage method used for battery charging. |  |  |

Feedback to the Candidate

Candidate’s Signature__________________ Assessor’s Signature _________________