Instruction Sheet for the Candidate

| Qualification | DC machines (Motor and Generator) |
| --- | --- |
| Competency Standard | Perform Tests On DC Generators |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name______________________________________________________ Registration/Roll Number_______________________________________ |
| Guidance for Candidate | To meet this standard, you are required to complete the following within time frame (for practical demonstration & assessment): - Plot the Open circuit characteristics of a Separately excited D.C generator - Plot the Open circuit characteristics of a D.C shunt generator - Plot the load characteristics of D.C shunt generator. - Plot the load characteristics of D.C series generator. - Plot the load characteristics of D.C compound generator for under, flat and over compounding - Perform parallel operation of two DC shunt generators. - Determine copper, iron & friction losses of shunt generator by actual loading. |
| Time: 05 Hrs. | During a practical assessment, under observation by an assessor, you are required to |
| Minimum Evidence Required | Plot the Open circuit characteristics of a Separately excited D.C generator - Connect DC supply to field coil through rheostat and ampere meter. - Rotate armature at constant speed. - Connect voltmeter across armature terminal. - Decrease the resistance of rheostat in steps and measure and record the relevant output voltage of armature and field current. - Repeat the 2 to 4 till voltage of armature reach at its saturation point. - Plot the graph between field current and armature voltage from the recorded values. Plot the Open circuit characteristics of a D.C shunt generator - Connect DC supply to field coil through rheostat and ampere meter. - Rotate armature at constant speed. - Connect voltmeter across armature terminal. - Decrease the resistance of rheostat in steps and measure and record the relevant output voltage of armature and field current. - Repeat the 8 to 10 till voltage of armature reach at its saturation point. - Plot the graph between field current and armature voltage from the recorded values. Subtract the value of back pitch from the added value. Plot the load characteristics of D.C shunt generator. - Select DC shunt generator and connect variable load. - Connect ampere meter and voltmeter across the load. - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. Plot the load characteristics of D.C series generator. - Select DC series generator and connect variable load. - Connect ampere meter and voltmeter across the load. - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. Plot the load characteristics of D.C compound generator for under, flat and over compounding - Select DC compound generator and connect variable load. - Connect ampere meter and voltmeter across the load. - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. - Adjust field diverter on zero ohm. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. - Such off the load. - Adjust the field diverter at such position that the terminal voltages are equal to no load voltages. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. - Switch off the load. - Adjust the field diverter at such position that the terminal voltages are greater than no load voltages. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. Perform parallel operation of two DC shunt generators. - Connect the circuit according to the circuit diagram. - Place all switches in off position. - Run generator 1 at rated speed. - Reduce field resistance of generator 1 - Connect generator with bus bar after attaining rated voltage. - Run generator 2 with prime mover. - Reduce the field resistance of generator 2 to attain its rated voltage. - Close the switches for parallel operation. - Calculate and record the reading of voltage and current on different loads. Determine copper, iron & friction losses of shunt generator by actual loading. - Connect ammeter in series with both winding. - Connect voltmeter in parallel with both winding. - Apply 10-20 DC volt. - Record the readings of voltmeter and ammeter. - Calculate Ra and Rsh. - Run the generator at rated speed with prime mover. - Turn on the load switch and record the meter reading. - Calculate input power and output power. - Calculate total losses (Copper loss, Friction loss, Iron loss) |

Self-Assessment Checklist

| Candidate Name |  |
| --- | --- |
| Registration No. |  |
| Qualification | DC machines (Motor and Generator) |
| Competency Standard | Perform Tests On DC Generators |
| Purpose of Assessment | Formative Assessment |
| Assessment Task | - Plot the Open circuit characteristics of a Separately excited D.C generator - Plot the Open circuit characteristics of a D.C shunt generator - Plot the load characteristics of D.C shunt generator. - Plot the load characteristics of D.C series generator. - Plot the load characteristics of D.C compound generator for under, flat and over compounding - Perform parallel operation of two DC shunt generators. - Determine copper, iron & friction losses of shunt generator by actual loading. |

I can……………….

| Performance Criteria | Yes | No |
| --- | --- | --- |
| - Connect DC supply to field coil through rheostat and ampere meter. |  |  |
| - Rotate armature at constant speed. |  |  |
| - Connect voltmeter across armature terminal. |  |  |
| - Decrease the resistance of rheostat in steps and measure and record the relevant output voltage of armature and field current. |  |  |
| - Repeat the 2 to 4 till voltage of armature reach at its saturation point. |  |  |
| - Plot the graph between field current and armature voltage from the recorded values. |  |  |
| - Connect DC supply to field coil through rheostat and ampere meter. |  |  |
| - Rotate armature at constant speed. |  |  |
| - Connect voltmeter across armature terminal. |  |  |
| - Decrease the resistance of rheostat in steps and measure and record the relevant output voltage of armature and field current. |  |  |
| - Repeat the 8 to 10 till voltage of armature reach at its saturation point. |  |  |
| - Plot the graph between field current and armature voltage from the recorded values. Subtract the value of back pitch from the added value. |  |  |
| - Select DC shunt generator and connect variable load. |  |  |
| - Connect ampere meter and voltmeter across the load. |  |  |
| - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. |  |  |
| - Increase the load in steps till specific reduce in terminal voltage observed. |  |  |
| - Plot the graph between load current and terminal voltage from the recorded values. |  |  |
| - Select DC series generator and connect variable load. |  |  |
| - Connect ampere meter and voltmeter across the load. |  |  |
| - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. |  |  |
| - Increase the load in steps till specific reduce in terminal voltage observed. |  |  |
| - Plot the graph between load current and terminal voltage from the recorded values. |  |  |
| - Select DC compound generator and connect variable load. |  |  |
| - Connect ampere meter and voltmeter across the load. |  |  |
| - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. |  |  |
| - Adjust field diverter on zero ohm. |  |  |
| - Increase the load in steps till specific reduce in terminal voltage observed. |  |  |
| - Plot the graph between load current and terminal voltage from the recorded values. |  |  |
| - Such off the load. |  |  |
| - Adjust the field diverter at such position that the terminal voltages are equal to no load voltages. |  |  |
| - Increase the load in steps till specific reduce in terminal voltage observed. |  |  |
| - Plot the graph between load current and terminal voltage from the recorded values. |  |  |
| - Switch off the load. |  |  |
| - Adjust the field diverter at such position that the terminal voltages are greater than no load voltages. |  |  |
| - Increase the load in steps till specific reduce in terminal voltage observed. |  |  |
| - Plot the graph between load current and terminal voltage from the recorded values. |  |  |
| - Connect the circuit according to the circuit diagram. |  |  |
| - Place all switches in off position. |  |  |
| - Run generator 1 at rated speed. |  |  |
| - Reduce field resistance of generator 1 |  |  |
| - Connect generator with bus bar after attaining rated voltage. |  |  |
| - Run generator 2 with prime mover. |  |  |
| - Reduce the field resistance of generator 2 to attain its rated voltage. |  |  |
| - Close the switches for parallel operation. |  |  |
| - Calculate and record the reading of voltage and current on different loads. |  |  |
| - Connect ammeter in series with both winding. |  |  |
| - Connect voltmeter in parallel with both winding. |  |  |
| - Apply 10-20 DC volts. |  |  |
| - Record the readings of voltmeter and ammeter. |  |  |
| - Calculate Ra and Rsh. |  |  |
| - Run the generator at rated speed with prime mover. |  |  |
| - Turn on the load switch and record the meter reading. |  |  |
| - Calculate input power and output power. |  |  |
| - Calculate total losses (Copper loss, Friction loss, Iron loss) |  |  |

Candidate’s Signature__________________ Assessor’s Signature____________________

Date: _______________________________

Assessors Judgment Guide

| Qualification | DC machines (Motor and Generator) |
| --- | --- |
| Competency Standard | Perform Tests On DC Generators |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name: ______________________________________________________________ Registration/Roll Number: ______________________ Signature: _______________ |
| Assessment Outcome | COMPETENT NOT YET COMPETENT Name of the Assessor________________________________________________ Assessor’s code:____________________________________________________ Signature: ________________________________ |

| Assessment Summary (to be filled by the assessor) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Activity | Method |  |  |  |  | Result |  |
| Nature of Activity | Written | Oral | Observation | Portfolio | Role Play | Competent | Not Yet Competent |
| Practical Skill Demonstration |  |  |  |  |  |  |  |
| Knowledge Assessment |  |  |  |  |  |  |  |
| Other Requirement |  |  |  |  |  |  |  |

Observation Checklist

| Assessment Task |  | 1. Plot the Open circuit characteristics of a Separately excited D.C generator 2. Plot the Open circuit characteristics of a D.C shunt generator 3. Plot the load characteristics of D.C shunt generator. 4. Plot the load characteristics of D.C series generator. 5. Plot the load characteristics of D.C compound generator for under, flat and over compounding 6. Perform parallel operation of two DC shunt generators. 7. Determine copper, iron & friction losses of shunt generator by actual loading. |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| During the practical assessment, candidate demonstrated the following: |  |  |  | Yes | No | Remarks |
|  | Connected DC supply to field coil through rheostat and ampere meter. |  |  |  |  |  |
|  | Rotated armature at constant speed. |  |  |  |  |  |
|  | Connected voltmeter across armature terminal. |  |  |  |  |  |
|  | Decreased the resistance of rheostat in steps and measure and recorded the relevant output voltage of armature and field current. |  |  |  |  |  |
|  | Repeated the 2 to 4 till voltage of armature reach at its saturation point. |  |  |  |  |  |
|  | Plotted the graph between field current and armature voltage from the recorded values. |  |  |  |  |  |
|  | Connected DC supply to field coil through rheostat and ampere meter. |  |  |  |  |  |
|  | Rotated armature at constant speed. |  |  |  |  |  |
|  | Connected voltmeter across armature terminal. |  |  |  |  |  |
|  | Decreased the resistance of rheostat in steps to measure and record the relevant output voltage of armature and field current. |  |  |  |  |  |
|  | Repeated the 8 to 10 till voltage of armature reach at its saturation point. |  |  |  |  |  |
|  | Plotted the graph between field current and armature voltage from the recorded values. Subtract the value of back pitch from the added value. |  |  |  |  |  |
|  | Selected DC shunt generator and connect variable load. |  |  |  |  |  |
|  | Connected ampere meter and voltmeter across the load. |  |  |  |  |  |
|  | Rotated armature at constant speed and note the readings of ampere meter and voltmeter. |  |  |  |  |  |
|  | Increased the load in steps till specific reduce in terminal voltage observed. |  |  |  |  |  |
|  | Plotted the graph between load current and terminal voltage from the recorded values. |  |  |  |  |  |
|  | Selected DC series generator and connect variable load. |  |  |  |  |  |
|  | Connected ampere meter and voltmeter across the load. |  |  |  |  |  |
|  | Rotated armature at constant speed and note the readings of ampere meter and voltmeter. |  |  |  |  |  |
|  | Increased the load in steps till specific reduce in terminal voltage observed. |  |  |  |  |  |
|  | Plotted the graph between load current and terminal voltage from the recorded values. |  |  |  |  |  |
|  | Selected DC compound generator and connected variable load. |  |  |  |  |  |
|  | Connected ampere meter and voltmeter across the load. |  |  |  |  |  |
|  | Rotated armature at constant speed and note the readings of ampere meter and voltmeter. |  |  |  |  |  |
|  | Adjusted field diverter on zero ohm. |  |  |  |  |  |
|  | Increased the load in steps till specific reduce in terminal voltage observed. |  |  |  |  |  |
|  | Plotted the graph between load current and terminal voltage from the recorded values. |  |  |  |  |  |
|  | Switched off the load. |  |  |  |  |  |
|  | Adjusted the field diverter at such position that the terminal voltages are equal to no load voltages. |  |  |  |  |  |
|  | Increased the load in steps till specific reduce in terminal voltage observed. |  |  |  |  |  |
|  | Plotted the graph between load current and terminal voltage from the recorded values. |  |  |  |  |  |
|  | Switched off the load. |  |  |  |  |  |
|  | Adjusted the field diverter at such position that the terminal voltages are greater than no load voltages. |  |  |  |  |  |
|  | Increased the load in steps till specific reduce in terminal voltage observed. |  |  |  |  |  |
|  | Plotted the graph between load current and terminal voltage from the recorded values. |  |  |  |  |  |
|  | Connected the circuit according to the circuit diagram. |  |  |  |  |  |
|  | Placed all switches in off position. |  |  |  |  |  |
|  | Run generator 1 at rated speed. |  |  |  |  |  |
|  | Reduced field resistance of generator 1 |  |  |  |  |  |
|  | Connected generator with bus bar after attaining rated voltage. |  |  |  |  |  |
|  | Run generator 2 with prime mover. |  |  |  |  |  |
|  | Reduced the field resistance of generator 2 to attain its rated voltage. |  |  |  |  |  |
|  | Closed the switches for parallel operation. |  |  |  |  |  |
|  | Calculated and recorded the reading of voltage and current on different loads. |  |  |  |  |  |
|  | Connected ammeter in series with both winding. |  |  |  |  |  |
|  | Connected voltmeter in parallel with both winding. |  |  |  |  |  |
|  | Applied 10-20 DC volt. |  |  |  |  |  |
|  | Recorded the readings of voltmeter and ammeter. |  |  |  |  |  |
|  | Calculated Ra and Rsh. |  |  |  |  |  |
|  | Run the generator at rated speed with prime mover. |  |  |  |  |  |
|  | Turned on the load switch and recorded the meter reading. |  |  |  |  |  |
|  | Calculated input power and output power. |  |  |  |  |  |
|  | Calculated total losses (Copper loss, Friction loss, Iron loss) |  |  |  |  |  |
| Competent |  |  | Not Yet Competent |  |  |  |

Knowledge Assessment

| Qualification | DC machines (Motor and Generator) |
| --- | --- |
| Competency Standard | Perform Tests On DC Generators |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name:______________________________________________________________ Registration/Roll Number: _________________ Candidate Signature:___________ |
| Assessment Outcome | COMPETENT NOT YET COMPETENT Name of the Assessor:________________________________________________ Assessor’s code:____________________________________________________ Signature of the Assessor:_______________________ |

Candidate’s response is not required to be identical, but similar concepts and/or keywords must be used. Oral questioning may be used to clarify candidate understanding of topic and its application.

| Questions (Candidate confidently answered questions correctly and demonstrated understanding of the topics and their application) |  | Satisfactory | Not Satisfactory |  |
| --- | --- | --- | --- | --- |
|  | What is different between shunt and separately excited generator? |  |  |  |
|  | Explain the effect of rheostat resistance on terminal voltage. |  |  |  |
|  | What is armature reaction? |  |  |  |
|  | Explain the reason of voltage reduce due to increase in load. |  |  |  |
|  | How to compensate armature reaction? |  |  |  |
|  | What is copper loss? |  |  |  |
|  | What is iron loss? |  |  |  |

Feedback to the Candidate

Candidate’s Signature__________________ Assessor’s Signature _________________