|  | Assessment Evidence Guide For HVACR Technician Level-3 Level-3 Equivalent to G-II Formative Assessment 5. Perform Installation of Commercial Air Conditioning System |
| --- | --- |
|  | Date 13-14 April, 2023 Lahore |
|  | National Vocational & Technical Training Commission |

Instruction Sheet for the Candidate

| Qualification | HVACR Technician Level-3 |
| --- | --- |
| Competency Standard | Perform Installation of Commercial Air Conditioning System |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name______________________________________________________ Registration/Roll Number_______________________________________ |
| Guidance for Candidate | To meet this standard, you are required to complete the following within time frame (for practical demonstration & assessment): - Install Packaged unit - Install Variable Refrigerant Flow (VRF) / Variable Refrigerant Volume (VRV) System - Install Air/Water-cooled Chiller - Install Air Handling Units (AHU) / Fan Coil Unit (FCU) - Install water circulating pump - Install Cooling Tower - Carry out Commissioning - Install HVACR Accessories for commercial Air Conditioning Systems |
| Time: 10 Hrs. | During a practical assessment, under observation by an assessor, you are required to - Mark the location to install Packaged unit. - Select tools, equipment, and accessories according to the job requirements. - Prepare foundation as per given drawing. - Adjust and level the Packaged unit by following safety precautions. - Insulate the supply and return air ducts as per drawings. - Connect the electric power supply and control wire with the unit. - Switch ON the power supply and check the performance according to the given standards. - Mark the locations to install both indoor and outdoor units of VRF / VRV system. - Select tools, equipment, and accessories according to the given job requirements. - Place, adjust and level the outdoor unit on the given foundation. - Cut the copper tube using tube cutter as per given sizes. - Swedge the copper tube for soldering / brazing. - Prepare piping, weld / braze by passing the nitrogen though the tubes. - Connect copper tubes from indoor to outdoor unit. - Fix Shut-off valves with service ports on every indoor unit as per manufacture’s recommendation. - Check leaks by applying nitrogen pressure / soapy method before the joints’ insulation. - Repair leakages (if any) after the removal of nitrogen pressure. - Insulate the copper pipe joints according to the given manufacturer instructions and standards. - Evacuate the system. - Switch ON the system and charge the refrigerant as per requirement. - Mark the location to install Air/Water-cooled chiller. - Select tools, equipment, and accessories according to the given job requirements. - Prepare foundation as per given drawing. - Fix anchors on foundation with vibration isolators. - Place, adjust and level the chiller on isolators. - Mark the location of AHU/FCU as per drawing - Drill the slab for fixing of rod for FCU. - Install FCU with hanging rod with drop-in anchor. - Place AHU on the given foundation as per manufacture’s standard. - Fix anchors on foundation with vibration isolators. - Install AHU on isolators. - Connect duct connection with supply, return and fresh air points of the unit. - Connect pipes for supply, return and drain connections. - Insulate insulation on ducts and pipes. - Establish electric power and control connections. - Mark location to install the pump. - Mount vibration isolators between pump base and foundation. - Fix the pump with chemical anchor bolts. - Level and align the pump as per standard. - Mark the location for cooling tower installation as per drawing. - Bifurcate cooling tower section/parts for its assembly. - Assemble sump base and fix it with anchor blots on foundation. - Fix all sides panels on sump base as per manufacturer’s drawing. - Fix water distribution sump, fan hub, fix fan and motor with allied components. - Install PVC fills in cooling tower as per manufacturer’s guidelines. - Select tools, equipment and related accessories according to the given job requirements. - Switch ON power supply of condenser and chilled water pump for water circulation in the system - Start the chiller and take reading of all parameters regarding temperature / pressure and electric power, check and remove unusual vibrations / noises etc. from unit, if any - Check the system performance as per given design criteria. - Record the results. - Select tools, equipment, and related allied components according to job requirements. - Install filter drier according to manufacturer’s specifications. - Install Sight Glass according to manufacturer’s specifications. - Install Vibration Absorber according to manufacturer’s specifications. - Install Liquid Receiver as per manufacturer’s specifications. - Install Service Valves as per manufacturer’s specifications. - Install Heat Exchanger by following manufacturer’s specifications. - Install Solenoid Valve according to manufacturer’s specifications. - Install Oil Separator by following manufacturer’s specifications. - Switch ON commercial air conditioning unit and check the performance. - Record the results. |
| Minimum Evidence Required |  |

Self-Assessment Checklist

| Candidate Name |  |
| --- | --- |
| Registration No. |  |
| Qualification | HVACR Technician Level-3 |
| Competency Standard | Perform Installation of Commercial Air Conditioning System |
| Assessment Task | - Install Packaged unit - Install Variable Refrigerant Flow (VRF) / Variable Refrigerant Volume (VRV) System - Install Air/Water-cooled Chiller - Install Air Handling Units (AHU) / Fan Coil Unit (FCU) - Install water circulating pump - Install Cooling Tower - Carry out Commissioning - Install HVACR Accessories for commercial Air Conditioning Systems |

| Performance Criteria | Yes | No |
| --- | --- | --- |
| - Mark the location to install Packaged unit. |  |  |
| - Select tools, equipment, and accessories according to the job requirements. |  |  |
| - Prepare foundation as per given drawing. |  |  |
| - Connect Packaged unit with supply, return, and fresh air ducts through flexible connections as per given drawing. |  |  |
| - Insulate the supply and return air ducts as per drawings. |  |  |
| - Connect the electric power supply and control wire with the unit. |  |  |
| - Switch ON the power supply and check the performance according to the given standards. |  |  |
| - Mark the locations to install both indoor and outdoor units of VRF / VRV system. |  |  |
| - Select tools, equipment, and accessories according to the given job requirements. |  |  |
| - Place, adjust and level the outdoor unit on the given foundation. |  |  |
| - Install indoor units according to given layout diagrams, client requirements and manufacturer instruction manual |  |  |
| - Swedge the copper tube for soldering / brazing. |  |  |
| - Prepare piping, weld / braze by passing the nitrogen though the tubes. |  |  |
| - Connect copper tubes from indoor to outdoor unit. |  |  |
| - Fix Shut-off valves with service ports on every indoor unit as per manufacture’s recommendation |  |  |
| - Check leaks by applying nitrogen pressure / soapy method before the joints’ insulation. |  |  |
| - Repair leakages (if any) after the removal of nitrogen pressure. |  |  |
| - Insulate the copper pipe joints according to the given manufacturer instructions and standards. |  |  |
| - Evacuate the system. |  |  |
| - Switch ON the system and charge the refrigerant as per requirement. |  |  |
| - Mark the location to install Air/Water-cooled chiller. |  |  |
| - Select tools, equipment, and accessories according to the given job requirements. |  |  |
| - Prepare foundation as per given drawing. |  |  |
| - Fix anchors on foundation with vibration isolators. |  |  |
| - Place, adjust and level the chiller on isolators. |  |  |
| - Mark the location of AHU/FCU as per drawing |  |  |
| - Drill the slab for fixing of rod for FCU. |  |  |
| - Install FCU with hanging rod with drop-in anchor. |  |  |
| - Place AHU on the given foundation as per manufacture’s standard. |  |  |
| - Fix anchors on foundation with vibration isolators. |  |  |
| - Install AHU on isolators. |  |  |
| - Connect duct connection with supply, return and fresh air points of the unit. |  |  |
| - Connect pipes for supply, return and drain connections. |  |  |
| - Insulate insulation on ducts and pipes. |  |  |
| - Establish electric power and control connections. |  |  |
| - Mark location to install the pump. |  |  |
| - Mount vibration isolators between pump base and foundation. |  |  |
| - Fix the pump with chemical anchor bolts. |  |  |
| - Level and align the pump as per standard. |  |  |
| - Mark the location for cooling tower installation as per drawing. |  |  |
| - Bifurcate cooling tower section/parts for its assembly. |  |  |
| - Assemble sump base and fix it with anchor blots on foundation. |  |  |
| - Fix all sides panels on sump base as per manufacturer’s drawing. |  |  |
| - Fix water distribution sump, fan hub, fix fan and motor with allied components. |  |  |
| - Install PVC fills in cooling tower as per manufacturer’s guidelines. |  |  |
| - Select tools, equipment and related accessories according to the given job requirements. |  |  |
| - Switch ON power supply of condenser and chilled water pump for water circulation in the system |  |  |
| - Start the chiller and take reading of all parameters regarding temperature / pressure and electric power, check and remove unusual vibrations / noises etc. from unit, if any |  |  |
| - Check the system performance as per given design criteria. |  |  |
| - Record the results. |  |  |
| - Select tools, equipment, and related allied components according to job requirements. |  |  |
| - Install filter drier according to manufacturer’s specifications. |  |  |
| - Install Sight Glass according to manufacturer’s specifications. |  |  |
| - Install Vibration Absorber according to manufacturer’s specifications. |  |  |
| - Install Liquid Receiver as per manufacturer’s specifications. |  |  |
| - Install Service Valves as per manufacturer’s specifications. |  |  |
| - Install Heat Exchanger by following manufacturer’s specifications. |  |  |
| - Install Solenoid Valve according to manufacturer’s specifications. |  |  |
| - Install Oil Separator by following manufacturer’s specifications. |  |  |
| - Switch ON commercial air conditioning unit and check the performance. |  |  |
| - Record the results |  |  |

Candidate’s Signature__________________ Assessor’s Signature____________________

Date: _______________________________

Assessors Judgment Guide

| Qualification | HVACR Technician Level-3 |
| --- | --- |
| Competency Standard | Perform Installation of Commercial Air Conditioning System |
| Candidate Details | Name: ______________________________________________________________ Registration/Roll Number: ______________________Signature: _______________ |
| Assessment Outcome | COMPETENT NOT YETCOMPETENT Name of the Assessor________________________________________________ Assessor’s code: ____________________________________________________ Signature: ________________________________ |

| Assessment Summary (to be filled by the assessor) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Activity | Method |  |  |  |  | Result |  |
| Nature of Activity | Written | Oral | Observation | Portfolio | Role Play | Competent | Not Yet Competent |
| Practical Skill Demonstration |  |  |  |  |  |  |  |
| Knowledge Assessment |  |  |  |  |  |  |  |
| Other Requirement |  |  |  |  |  |  |  |

Observation Checklist

| Assessment Task |  | - Install Packaged unit - Install Variable Refrigerant Flow (VRF) / Variable Refrigerant Volume (VRV) System - Install Air/Water-cooled Chiller - Install Air Handling Units (AHU) / Fan Coil Unit (FCU) - Install water circulating pump - Install Cooling Tower - Carry out Commissioning - Install HVACR Accessories for commercial Air Conditioning Systems. |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| During the practical assessment, candidate demonstrated the following: |  |  |  | Yes | No | Remarks |
|  | Mark the location to install Packaged unit. |  |  |  |  |  |
|  | Select tools, equipment, and accessories according to the job requirements. |  |  |  |  |  |
|  | Prepare foundation as per given drawing. |  |  |  |  |  |
|  | Connect Packaged unit with supply, return, and fresh air ducts through flexible connections as per given drawing. |  |  |  |  |  |
|  | Insulate the supply and return air ducts as per drawings. |  |  |  |  |  |
|  | Connect the electric power supply and control wire with the unit. |  |  |  |  |  |
|  | Switch ON the power supply and check the performance according to the given standards. |  |  |  |  |  |
|  | Mark the locations to install both indoor and outdoor units of VRF / VRV system. |  |  |  |  |  |
|  | Select tools, equipment, and accessories according to the given job requirements. |  |  |  |  |  |
|  | Place, adjust and level the outdoor unit on the given foundation. |  |  |  |  |  |
|  | Install indoor units according to given layout diagrams, client requirements and manufacturer instruction manual |  |  |  |  |  |
|  | Swedge the copper tube for soldering / brazing. |  |  |  |  |  |
|  | Prepare piping, weld / braze by passing the nitrogen though the tubes. |  |  |  |  |  |
|  | Connect copper tubes from indoor to outdoor unit. |  |  |  |  |  |
|  | Fix Shut-off valves with service ports on every indoor unit as per manufacture’s recommendation |  |  |  |  |  |
|  | Check leaks by applying nitrogen pressure / soapy method before the joints’ insulation. |  |  |  |  |  |
|  | Repair leakages (if any) after the removal of nitrogen pressure. |  |  |  |  |  |
|  | Insulate the copper pipe joints according to the given manufacturer instructions and standards. |  |  |  |  |  |
|  | Evacuate the system. |  |  |  |  |  |
|  | Switch ON the system and charge the refrigerant as per requirement. |  |  |  |  |  |
|  | Mark the location to install Air/Water-cooled chiller. |  |  |  |  |  |
|  | Select tools, equipment, and accessories according to the given job requirements. |  |  |  |  |  |
|  | Prepare foundation as per given drawing. |  |  |  |  |  |
|  | Fix anchors on foundation with vibration isolators. |  |  |  |  |  |
|  | Place, adjust and level the chiller on isolators. |  |  |  |  |  |
|  | Mark the location of AHU/FCU as per drawing |  |  |  |  |  |
|  | Drill the slab for fixing of rod for FCU. |  |  |  |  |  |
|  | Install FCU with hanging rod with drop-in anchor. |  |  |  |  |  |
|  | Place AHU on the given foundation as per manufacture’s standard. |  |  |  |  |  |
|  | Fix anchors on foundation with vibration isolators. |  |  |  |  |  |
|  | Install AHU on isolators. |  |  |  |  |  |
|  | Connect duct connection with supply, return and fresh air points of the unit. |  |  |  |  |  |
|  | Connect pipes for supply, return and drain connections. |  |  |  |  |  |
|  | Insulate insulation on ducts and pipes. |  |  |  |  |  |
|  | Establish electric power and control connections. |  |  |  |  |  |
|  | Mark location to install the pump. |  |  |  |  |  |
|  | Mount vibration isolators between pump base and foundation. |  |  |  |  |  |
|  | Fix the pump with chemical anchor bolts. |  |  |  |  |  |
|  | Level and align the pump as per standard. |  |  |  |  |  |
|  | Mark the location for cooling tower installation as per drawing. |  |  |  |  |  |
|  | Bifurcate cooling tower section/parts for its assembly. |  |  |  |  |  |
|  | Assemble sump base and fix it with anchor blots on foundation. |  |  |  |  |  |
|  | Fix all sides panels on sump base as per manufacturer’s drawing. |  |  |  |  |  |
|  | Fix water distribution sump, fan hub, fix fan and motor with allied components. |  |  |  |  |  |
|  | Install PVC fills in cooling tower as per manufacturer’s guidelines. |  |  |  |  |  |
|  | Select tools, equipment and related accessories according to the given job requirements. |  |  |  |  |  |
|  | Switch ON power supply of condenser and chilled water pump for water circulation in the system |  |  |  |  |  |
|  | Start the chiller and take reading of all parameters regarding temperature / pressure and electric power, check and remove unusual vibrations / noises etc. from unit, if any |  |  |  |  |  |
|  | Check the system performance as per given design criteria. |  |  |  |  |  |
|  | Record the results. |  |  |  |  |  |
|  | Select tools, equipment, and related allied components according to job requirements. |  |  |  |  |  |
|  | Install filter drier according to manufacturer’s specifications. |  |  |  |  |  |
|  | Install Sight Glass according to manufacturer’s specifications. |  |  |  |  |  |
|  | Install Vibration Absorber according to manufacturer’s specifications. |  |  |  |  |  |
|  | Install Liquid Receiver as per manufacturer’s specifications. |  |  |  |  |  |
|  | Install Service Valves as per manufacturer’s specifications. |  |  |  |  |  |
|  | Install Heat Exchanger by following manufacturer’s specifications. |  |  |  |  |  |
|  | Install Solenoid Valve according to manufacturer’s specifications. |  |  |  |  |  |
|  | Install Oil Separator by following manufacturer’s specifications. |  |  |  |  |  |
|  | Switch ON commercial air conditioning unit and check the performance. |  |  |  |  |  |
|  | Record the results |  |  |  |  |  |
| Competent |  |  | Not Yet Competent |  |  |  |

Knowledge Assessment

| Qualification | HVACR Technician Level-3 |
| --- | --- |
| Competency Standard | Perform Installation of Commercial Air Conditioning System |
| Candidate Details | Name: ______________________________________________________________ Registration/Roll Number: _________________ Candidate Signature: ___________ |
| Assessment Outcome | COMPETENT NOT YETCOMPETENT Name of the Assessor: ________________________________________________ Assessor’s code: ____________________________________________________ Signature of the Assessor: _______________________ |

Candidate’s response is not required to be identical, but similar concepts and/or keywords must be used. Oral questioning may be used to clarify candidate understanding of topic and its application.

| Questions (Candidate confidently answered questions correctly and demonstrated understanding of the topics and their application) |  | Satisfactory | Not Satisfactory |
| --- | --- | --- | --- |
|  | What is the commercial application of Air conditioning? |  |  |
|  | What are different types of commercial air conditioners? |  |  |
|  | What is the difference between commercial and domestic air conditioning? |  |  |
|  | What are different types of HVAC system of commercial air conditioning system? |  |  |
|  | What is the procedure to find the air conditioning size of commercial builing? |  |  |
|  | What is the approximate time to install the commercial air conditioner? |  |  |
|  | What is the procedure to calculate the BTU of commercial building? |  |  |
|  | What are the safety measures adopting to install the commercial air conditioner? |  |  |
|  | What is the preventive maintenance time interval for commercial air conditioning system? |  |  |
|  | What are the basic steps to install the commercial air conditioning system? |  |  |

Feedback to the Candidate

Candidate’s Signature__________________ Assessor’s Signature _________________