National Curriculum Level -5 in HVACR Technology

National Vocational and Technical Training Commission (NAVTTC)

Government of Pakistan

Contents

1.	Introduction	9

2.	Purpose of the Qualification:	9

3.	Overall objectives of training program	10

4.	Date of Validation	10

5.	Entry level of trainees	10

6.	Minimum qualification for teachers	11

7.	Duration of the course:	11

8.	Description and structure of the course	12

9.	Detail of Modules	23

0713E&E-1.	Apply Occupational Health and Safety on HVAC Systems	23

0713E&E-2.	Maintain Safe Work Environment	25

0713E&E-3.	Make PVC Cable Joints and Construct Electrical Test Box	28

0713E&E-4.	Connect Loads in Electrical Circuit	32

0713E&E-5.	Measure Electrical Quantities in Electric Circuits	38

0713E&E-6.	Establish Electrical Circuits for Commercial Refrigeration Systems	43

0713E&E-7.	Evaluate Transformer & Verify Kirchhoff’s Law	47

0713E&E-8.	Apply Basics of Drawing	53

0713E&E-9.	Draw Pictorial Drawing	55

0713E&E-10.	Apply Basic Dimensioning System in Working Drawing	56

0713E&E-11.	Draw Sectioning Drawing	57

0713E&E-12.	Draw Auxiliary Drawing	59

0713E&E-13.	Identify and Use HVAC Tools	60

0713E&E-14.	Joint Copper Tubes	62

0713E&E-15.	Use of Pressure Gauges and Meters for Measuring Refrigerants Pressure	64

0713E&E-16.	Check and Test Compressors	67

0713E&E-17.	Check and Test Electrical Accessories	69

0713E&E-18.	Check and Test Electric Motors	72

0713E&E-19.	Perform Sheet Metal Processes.	74

0713E&E-20.	Perform Threading with Tap & Die	77

0713E&E-21.	Perform Machining Operation	80

0713E&E-22.	Perform Taper Turning, Drilling and Thread Cutting by Lathe Machine	83

0713E&E-23.	Perform Welding Process	86

0713E&E-24.	Analyse Thermodynamic performance of HVACR System	90

0713E&E-25.	Prepare Low Pressure Boiler for Smooth Operation	92

0713E&E-26.	Perform Water Treatment	95

0713E&E-27.	Service and Maintain Transport / Mobile Refrigeration Units	99

0713E&E-28.	Apply principles of refrigeration in Cold Storage Technology	102

0713E&E-29.	Maintain and Repair Multi-Stage, Cascade & Ultra-Low Temperature Refrigeration System	106

0713E&E-30.	Monitor Refrigeration in Food Processing	110

0713E&E-31.	Perform Refrigerant Recovery	114

0713E&E-32.	Install Residential Air Conditioner	116

0713E&E-33.	Repair Refrigerator, Deep Freezer, Display Unit, Bottle Cooler and Water Cooler	119

0713E&E-34.	Repair and Service Residential Air Conditioner	122

0713E&E-35.	Overhaul the compressors	128

0713E&E-36.	Repair and Service Residential Refrigeration Units	133

0713E&E-37.	Test, recover, evacuate and charge refrigeration system	138

0713E&E-38.	Calculate Fundamental Properties of Gasses	144

0713E&E-39.	Calculate Psychrometric Processes of Air	149

0713E&E-40.	Calculate Psychrometric Properties of System Air	152

0713E&E-41.	Analyze Psychrometric Performance of HVAC Systems	156

0713E&E-42.	Develop Geometrical Solids	159

0713E&E-43.	Draw Projection of Pipes	161

0713E&E-44.	Draw Building Drawings	163

0713E&E-45.	Prepare Computer Added Drawings File (Auto CAD)	164

0713E&E-46.	Contribute to the Design of Commercial Refrigeration system	166

0713E&E-47.	Design HVAC System and Select Components	169

0713E&E-48.	Develop specifications and prepare drawings for HVAC Systems	172

0713E&E-49.	Calculate Cooling Load of Commercial Buildings	175

0713E&E-50.	Design and Select Fans for HVAC system	178

0713E&E-51.	Design Piping for Commercial HVAC System	180

0713E&E-52.	Design & Select Pumps for HVAC system	182

0713E&E-53.	Design Duct system for Commercial HVAC system	183

0713E&E-54.	Attenuate Noise and Vibration Encounter in HVAC Applications	186

0713E&E-55.	Perform Water Treatment in HVAC System	188

0713E&E-56.	Analyse the operation of HVAC Air and Hydronic system	191

0713E&E-57.	Calculate Quantity of Heat Transfer for Different Applications	194

0713E&E-58.	Plot Refrigeration Cycle on PH Chart	197

0713E&E-59.	Calculate Different Process on PH Chart	198

0713E&E-60.	Calculate the Quantity of Gasses in a flue gas Sample	200

0713E&E-61.	Make Circuits Using Electronic Components.	202

0713E&E-62.	Make Temperature Control & Sensing Devices	205

0713E&E-63.	Connect the Accessories in Control Circuits	207

0713E&E-64.	Make Opto-Coupler Devices	208

0713E&E-65.	Install Commercial Refrigeration System.	212

0713E&E-66.	Install, Maintain & Repair Industrial Refrigeration System.	220

0713E&E-67.	Install, Maintain & Repair Commercial Refrigeration System.	228

0713E&E-68.	Install, Maintain & Repair Package Type Air Conditioning System.	234

0713E&E-69.	Install Central Air Conditioning System.	245

0713E&E-70.	Repair and Service Central Air Conditioning System.	269

0713E&E-71.	Service and Maintain Ceiling Mounted Cassette Type Air Conditioner	277

0713E&E-72.	Service and Maintain Cooling Tower.	286

0713E&E-73.	Perform Preventive Maintenance.	298

0713E&E-74.	Diagnose faults in complex HVAC control system	302

0713E&E-75.	Service and Maintain Automobile Air Conditioner.	308

0713E&E-76.	Perform Commissioning of HVAC Systems	316

0713E&E-77.	Install and Commission Carbon Dioxide Refrigeration Systems, Components and Accessories	322

0713E&E-78.	Operate & Maintain Absorption Air Conditioning System	329

0713E&E-79.	Check and Inspect Air Washer System in Respect of Preventive Maintenance	336

0713E&E-80.	Check and Inspect Central Air Conditioning system	340

0713E&E-81.	Install and Commission Ammonia Refrigeration System, Components & Accessories	345

0713E&E-82.	Check and Inspect HVAC Variable Refrigerant Flow (VRF) System	349

0713E&E-83.	Check and Inspect Centrifugal HVAC system	355

0713E&E-84.	Check and Inspect Screw Type HVAC system	359

0713E&E-85.	Install, Maintain and Repair Industrial Refrigeration System	366

0713E&E-86.	Service and Maintain Air Handling Unit (AHU)	372

0713E&E-87.	Check and Connect Basic Controls used in HVAC	377

0713E&E-88.	Prepare Control Circuits	379

0713E&E-89.	Measure Air Velocity	382

0713E&E-90.	Produce HVAC Control System Drawings	385

0713E&E-91.	Adjust and Balance HVAC Controls	387

0713E&E-92.	Operate HVAC Building Management System (BMS)	389

0713E&E-93.	Develop Entrepreneurial Skills	392

0713E&E-94.	Apply project information management and communications techniques	395

0713E&E-95.	Apply Project Human Resources Management Approaches	397

0713E&E-96.	Direct Human Resources Management Of A Project Program	400

0713E&E-97.	Develop A Project Management Plan	404

0713E&E-98.	Maintain Business Resources	407

0713E&E-99.	Develop A Sales Plan	409

0713E&E-100.	Plan And Implement Business-To-Business Marketing	412

0713E&E-101.	Address Customer Needs	414

0713E&E-102.	Manage Personal Finances	418

0713E&E-103.	Solve Problems Which Jeopardize Safety And Security	420

0713E&E-104.	Coordinate a Work Team	425

0713E&E-105.	Lead Small Teams	428

0713E&E-106.	Plan and organize work	432

0713E&E-107.	Develop teams and individuals	435

0713E&E-108.	Apply problem solving techniques in the workplace using critical thinking	438

0713E&E-109.	Manage Human Resource Services	441

0713E&E-110.	Develop workplace policy and procedures for sustainability.	445

0713E&E-111.	Manage meetings	447

0713E&E-112.	Manage recruitment selection and induction processes	449

0713E&E-113.	Manage personal work priorities and professional development	452

0713E&E-114.	Manage workforce planning	455

0713E&E-115.	Undertake project work	458

0713E&E-116.	Identify and communicate trends in career development	461

0713E&E-117.	Apply specialist interpersonal and counseling interview skills	463

0713E&E-118.	Work safely in an office environment	469

0713E&E-119.	Develop workplace documents	472

0713E&E-120.	Prepare and implement negotiation	476

0713E&E-121.	Maintain professionalism in the workplace	480

0713E&E-122.	Maintain professional development and career professionalism	482

0713E&E-123.	Organize schedules	484

0713E&E-124.	Perform word-processing applications	486

0713E&E-125.	Operate Basics Computer Functions	490

0713E&E-126.	Develop Computer Application skills	493

0713E&E-127.	Operate Presentation Packages	497

0713E&E-128.	Operate Spreadsheet Application	501

0713E&E-129.	Install computer operating systems and hardware	504

0713E&E-130.	Perform writing and editing skills	507

10.	Members of Curriculum Development Committee	510

# Introduction

The HVACR Industry is a worldwide enterprise, having role including operation, maintenance, system design, construction, equipment manufacturing, sales, education and research. The HVACR industry is being regulated by the manufacturers of HVACR equipment, but organizations such as HARDI, ASHRAE, SMACNA, ACCA, etc. have been established to support the industry and to encourage high standards of achievements.

HVACR is a necessity of the day for personal comfort, medical health, food preservation, water supply and work productivity. In fact, all human activities rely on HVACR in one way or the other. This industry produces thousands of jobs in the market for its products.

The HVACR experts plan, install and maintain the climate control system that makes our environment more comfortable and functional. The areas mentioned above continuously upgrading existing system for economical cost and environment efficiency.

The HVACR field also offers variety of jobs and opportunities to grow for obtaining better bread and butter and its professionals can use their skills at any place in the world.

Homes, Office Buildings, Industries such as Chemical, Food Preservation, Medical & Textile, Airplanes, Railways, Vehicles, Mobile Refrigerating Units and Electronic Equipment, all rely on HVACR systems for their better working. Hence the HVACR technology/industry provides huge employment opportunities for HVACR professionals in the field of Designing, Manufacturing, Erection, Operation & Maintenance throughout Pakistan and abroad.

# Purpose of the Qualification:

The purpose of this qualification is to set high professional standards for HVACR industry. The specific objectives for developing this qualification are as under:

- Improve the professional competence of the trainees

- Provide opportunities for the recognition of skills attained by a person through formal or informal pathways

- Improve the quality & effectiveness of training and assessment for HVACR industry

- Enable the existing workforce to capacitate themselves in new techniques and methods

# Overall objectives of training program

The HVACR qualification of level 5 consists of both the theoretical and practical details and having the following Occupations

| HVACR System Designer II | Level 5 |
| --- | --- |
| HVACR BMS Technician | Level 5 |
| Industrial HVACR Technician | Level 5 |

# Date of Validation

The level 5 of National qualification on HVACR Technology has been validated by the Qualifications Development Committee (QDC) members on 04-08-2020 to 08-08-2020 and will remain valid for 10 years

# Entry level of trainees

The entry for D.A. E National Diploma level 5, in HVACR Technology are

- A person having National Vocational Certificate level 4, in HVACR Technology for entry into level 5.

- A person having Matric certificate with Science subjects for entry into level 2.

# Minimum qualification for teachers

- B. Tech in RAC/Mechanical 4 Years

- B.Sc. / B.E. in Mechanical Engineering 4 Years

- D. A. E. in HVACR with 3 Years teaching experience

- Must be able to communicate effectively

Medium of instruction

English, and Urdu.

# Duration of the course:

The proposed curriculum is composed of 130 modules that will be covered in 3592 Learning hours. Duration of the course is proposed to be Three years. The total weightage for technical modules is 3600 hours. A total of 1200 hours have been reserved for allied subject i.e. Islamic studies, English, Mathematics, Physics and Chemistry.

The details of technical modules are given as under:

Level - 2 = 6 months. (Single Semester)

Level - 3 = 6 months. (Single Semester)

Level - 4 = 1 Year.     (Two Semesters)

Level - 5 = 1 Year.     (Two Semesters)

The overall distribution of contact hours and Credit Hours is given below:

Total.		3592 hours. & 359.2 Credits

The distribution of contact hours and credit hours in each level is given below:

Level - 2 = 6 months (16 weeks)

Total.		603 hours. & 60.3 Credits

Theory.	110hours (18.24%)

Practical.	493 hours (81.75%)

Level - 3 = 6 months (16 weeks)

Total.		599 hours. & 59.9 Credits

Theory.	126 hours (21 %)

Practical.	473 hours (79 %)

Level - 4 = 1 Year (16 weeks + 16 Weeks)

Total.		1200 hours. & 120 Credits

Theory.	315 hours (26.25 %)

Practical.	885 hours (73.75 %)

Level - 5 = 1 Year (16 weeks + 16 Weeks)

Total.		1207 hours. & 120.7 Credits

Theory.	491 hours (39.7 %)

Practical.	716hours (60.3 %)

# Description and structure of the course

National Qualification Certificate in HVACRTechnology Level 5

| Module Code | Name of Subjects | Category | Level | Contact Hour |  |  | Credit |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Th | Pr | Total |  |
|  | HVACR System Designer II |  |  |  |  |  |  |
| 0713E&E-46 | Contribute to the design of Commercial Refrigeration System | Technical | 5 | 10 | 66 | 76 | 7.6 |
| 0713E&E-47 | Design HVACR System and Select Components | Technical | 5 | 20 | 45 | 65 | 6.5 |
| 0713E&E-48 | Develop Specifications and Prepare Drawings for HVACR Systems | Technical | 5 | 12 | 18 | 30 | 3 |
| 0713E&E-49 | Calculate Cooling Load of Commercial Buildings | Technical | 5 | 44 | 66 | 110 | 11 |
| 0713E&E-50 | Design and Select Fan for HVACR System | Technical | 5 | 12 | 18 | 30 | 3 |
| 0713E&E-51 | Design Duct System for Commercial HVACR System | Technical | 5 | 18 | 27 | 45 | 4.5 |
| 0713E&E-52 | Design Piping for Commercial HVACR System | Technical | 5 | 18 | 27 | 45 | 4.5 |
| 0713E&E-53 | Design& Select Pumps for HVACR System | Technical | 5 | 18 | 27 | 45 | 4.5 |
| 0713E&E-61 | Make Circuit using Electronic Components | Technical | 5 | 10 | 21 | 31 | 3.1 |
| 0713E&E-62 | Make Temperature Control & Sensing Devices | Technical | 5 | 4 | 18 | 22 | 2.2 |
| 0713E&E-63 | Connect the Accessories in Control Circuits | Technical | 5 | 8 | 32 | 40 | 4 |
| 0713E&E-64 | Make Opto-Coupler Devices | Technical | 5 | 4 | 18 | 22 | 2.2 |
| 0713E&E-87 | Check and Connect Basic Controls used in HVAC | Technical | 5 | 6 | 24 | 30 | 3 |
| 0713E&E-88 | Prepare Control Circuits | Technical | 5 | 6 | 24 | 30 | 3 |
| 0713E&E-90 | Produce HVACR Control System Drawings | Technical | 5 | 12 | 18 | 30 | 3 |
| 0713E&E-91 | Adjust and Balance HVACR Controls | Technical | 5 | 8 | 12 | 20 | 2 |
| 0713E&E-92 | Operate HVAC Building Management System (BMS) | Technical | 5 | 12 | 18 | 30 | 3 |
| 0713E&E-24 | Analyze Thermodynamics performance of HVAC system | Technical | 5 | 5 | 15 | 20 | 2 |
| 0713E&E-25 | Prepare Boiler for Smooth Operation | Technical | 5 | 5 | 24 | 29 | 2.9 |
| 0713E&E-26 | Perform Water Treatment | Technical | 5 | 5 | 24 | 29 | 2.9 |
| 0713E&E-55 | Perform Water Treatment in HVACR System | Technical | 5 | 5 | 24 | 29 | 2.9 |
| 0713E&E-60 | Calculate the Quantity of Gases in a Flue Gas Sample | Technical | 5 | 5 | 15 | 20 | 2 |
| 0713E&E-78 | Operate & Maintain Absorption Air Conditioning System | Technical | 5 | 5 | 15 | 20 | 2 |
| 0713E&E-79 | Check & Inspect Air Washer System in respect of Preventive Maintenance | Technical | 5 | 5 | 12 | 17 | 1.7 |
| 0713E&E-80 | Check & Inspect Central Air Conditioning System | Technical | 5 | 5 | 12 | 17 | 1.7 |
| 0713E&E-82 | Check and Inspect HVAC Variable Refrigerant Flow (VRF)System | Technical | 5 | 5 | 12 | 17 | 1.7 |
| 0713E&E-83 | Check and Inspect Centrifugal HVAC System | Technical | 5 | 5 | 24 | 29 | 2.9 |
| 0713E&E-84 | Check and Inspect Screw Type HVAC System | Technical | 5 | 5 | 24 | 29 | 2.9 |
| 0713E&E-85 | Install, Maintain and Repair Industrial Refrigeration Systems | Technical | 5 | 5 | 12 | 17 | 1.7 |
| 0713E&E-86 | Service and Maintain Air Handling Unit (AHU) | Technical | 5 | 5 | 24 | 29 | 2.9 |
| 0713E&E-93 | Develop Entrepreneurial Skills | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-94 | Apply project information management and communications techniques | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-95 | Apply project human resources management approaches | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-96 | Direct human resources management of a project program | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-97 | Develop a project management plan | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-98 | Maintain business resources | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-99 | Develop a sales plan | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-100 | Plan and implement business-to-business marketing | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-101 | Address Customer Needs | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-102 | Manage personal finances | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-103 | Solve problems which jeopardize safety and security | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-104 | Coordinate a work team | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-105 | Lead small teams | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-106 | Plan and organize work | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-107 | Develop teams and individuals | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-108 | Apply problem solving techniques in the workplace using critical thinking | Generic | 5 | 12 | 0 | 12 | 1.2 |
| 0713E&E-109 | Manage human resource services | Generic | 5 | 12 | 0 | 12 | 1.2 |
|  |  | Total |  | 491 | 716 | 1207 | 121 |

- Detail of Modules

## Analyse Thermodynamic performance of HVACR System

Objective: This module covers the knowledge and  skills required to Prepare to analyze the thermodynamic performance of HVACR systems , analyze the thermodynamic performance of HVACR systems and Make report and act on the results of thermodynamic performance analysis

Duration:  50	Hours			                             Theory: 10Hours				                  Practice: 	40 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Prepare to analyze the thermodynamic performance of HVACR systems | Trainee will be able to: - Calculate thermodynamic properties of air - Calculate specific heat of air at constant pressure and at constant volume - Calculate enthalpy of air / gasses - Calculate internal energy of air / gasses - Calculate specific gravity of different liquids - Calculate density of air / liquids - Calculate rate of discharge of fluids | - Thermodynamic performance issues - Obtaining thermodynamic performance parameters, specifications and performance requirements appropriate to each situation - Calculate different thermodynamics parameter (density of air , discharge rate of fluid, internal energy of air/gasses, specific heat of air at constant pressure Practical Activity Calculate rate of discharge of fluids | Theory-04Hrs. Practical-13 Hrs. Total- 17 Hrs. | - Steam table - H-S chart - HVACR design software | Classroom and Lab |
| - Analyze the thermodynamic performance of HVACR systems | Trainee will be able to: - Apply thermodynamic principles to analytical solutions on refrigeration and air conditioning systems. - Obtain Parameters, specifications and performance requirements in relation to refrigeration and air conditioning systems in accordance with established procedures. - Carry out approaches to analyze thermodynamic parameters to provide the most effective solution. | - Forming effective strategies for analyzing refrigeration and air conditioning systems performance - Obtaining thermodynamic performance parameters, specifications and performance requirements appropriate to each situation Practical Activity Analyze the thermodynamic performance of HVAC/R systems | Theory-03Hrs. Practical-13 Hrs. Total- 16 Hrs. | - Personal Protective Equipment - Basic Measuring tools - Basic Marking tools | Classroom and Lab |
| - Make report and act on the results of thermodynamic performance analysis | - Evaluate to determine the effectiveness of solutions for thermodynamic issues and modify where necessary. - Make report of the analysis including details of all findings, calculations and assumptions. - Take actions regarding equipment, documents for inclusion in work/project or development records in accordance with professional standards and manufacturer’s specifications. | - Evaluating the results of the analysis - Documenting analysis details of all findings, calculations and assumptions - Record keeping and reporting Practical Activity Make report thermodynamic performance analysis | Theory-03Hrs. Practical-14 Hrs. Total- 17 Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Marking tools | Lab |

## Prepare Low Pressure Boiler for Smooth Operation

Objective: This module covers the knowledge and  skills required to perform Prepare the low-pressure boiler for operation, Operate and monitor boiler, Shut down and store boiler and Analyze and respond to abnormal performance (Trouble Shooting of Boiler

Duration:  60	Hours			                             Theory: 12Hours				                  Practice: 	48 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Prepare the low-pressure boiler for operation | Trainee will be able to: - Review operational order and check appropriate / designated / concerned / competent person where required - Identify and report health and safety hazards / maintenance requirements to appropriate personnel according to workplace reporting procedures - Identify and set quantity of steam to be generated for allocated Process - Purge the boiler according to workplace procedure - Perform pre-operational checks to confirm operational status of boiler and related equipment | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE - set quantity of steam to be generated for allocated Process - boiler according to workplace procedure Practical Activity Set measured quantities of boiler | Theory-03Hrs. Practical-12 Hrs. Total- 15 Hrs. | - Personal Protective Equipment - Boiler - Basic Measuring tools - Basic Hand tools - Basic Cutting tools | Classroom and Lab |
| - Operate and monitor boiler | Trainee will be able to: - Use equipment in line with organizational safety procedures, manufacturer’s instructions and environmental protection practices. - Apply complete pre-operational safety and pre start-up checks to ensure operational effectiveness. - Start boiler and bring safely online; communicate recent performance to appropriate personnel. - Monitor boiler operation, diagnose status and adjust to maintain safe and efficient operation. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - Working principles of boiler and its types - complete pre-operational safety and pre start-up checks to ensure operational Practical Activity Start & Operate boiler safely | Theory-03Hrs. Practical-12 Hrs. Total- 15 Hrs.. | - Boiler - Personal Protective Equipment - Basic Measuring tools - Basic Marking tools | Classroom and Lab |
| - Shut down and store boiler | Trainee will be able to: - Shut down boiler according to workplace procedures and manufacturer's recommendations - Clean boiler internally and externally according to workplace procedures and manufacturer's recommendations - Remove valves and fittings in preparation for maintenance - Store the boiler in the appropriate storage mode according to workplace procedures and manufacturer's recommendations - Store and record boiler house chemicals, in line with safety procedures and environmental protection practices. - Follow emergency shutdown procedures in cases of fire. - Complete operating log, record fuel efficiency and report to the designated personnel. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Emergency shutdown procedures in cases of fire. - operating log, record fuel efficiency and report to the designated personnel Practical Activity Shut down boiler according to workplace procedures | Theory-03Hrs. Practical-12 Hrs. Total- 15 Hrs. | - Boiler - Personal Protective Equipment - Basic Measuring tools - Basic Marking tools - Basic Cutting tools - Basic Power tools |  |
| - Analyze and respond to abnormal performance (Trouble Shooting of Boiler) | Trainee will be able to: - Analyze operating data and plant operating conditions to identify causes of abnormal performance - Act correctively in accordance with workplace procedures in response to Hazards, out-of-specification test results and/or plant performance - Implement emergency procedures as required according to workplace procedures and manufacturer's recommendations and ASHRAE US Standards. | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) Practical Activity Analyze operating data and plant operating conditions to identify causes of abnormal performance | Theory-03Hrs. Practical-12 Hrs. Total- 15 Hrs. | - Personal Protective Equipment - Basic Measuring tools - Basic Marking tools |  |

## Perform Water Treatment

Objective: This module covers the knowledge and  skills required to perform Perform chemical test of water,  Prepare for hot water treatment,  Carry out post-treatment procedures  and Perform organic and inorganic material treatment procedure

Duration:  30	Hours			                             Theory: 6Hours				                  Practice: 	24Hour

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Perform chemical test of water | Trainee will be able to: - Collect water samples from boiler, close water circuit and cooling tower - Examine sample waters with the help of chemical test kit - Compare values of required water with PH standards - Prepare report | - Identification and use of Personal Protective Equipment (PPE) - Chemicals used for the treatment of water - Properties of the different chemicals - Ratio between water and chemical - Advantages of the water treatment - Examine the water with the help of chemical test - PH value Practical Activity - Perform different test of water | Theory-01Hrs. Practical-06 Hrs. Total- 07 Hrs. | - Personal Protective Equipment - Chemical test kit - Water treatment assembly kit - Water pots for sampling | Classroom and Lab |
| - Prepare for hot water treatment | Trainee will be able to: - Confirm work instructions on hot water treatments - Confirm materials as available and ready to meet requirements - Set up equipment in according to its specifications - Prepare chemicals for hot water treatment and hydration according to specifications - Collect Waste and dispose it of according to workplace procedures | - Chemicals used for the treatment of water - Properties of the different chemicals - Ratio between water and chemical - Advantages of the water treatment - Examine the water with the help of chemical test - PH value - Work instructions on hot water treatments - Perform different test of water Practical Activity Collect Waste and dispose it of according to workplace procedures | Theory-01Hrs. Practical-06 Hrs. Total- 07 Hrs.. | - Personal Protective Equipment - Chemical test kit - Water treatment assembly kit - Water pots for sampling | Classroom and Lab |
| - Carry out post-treatment procedures | Trainee will be able to: - Collect water samples from boiler, close water circuit and cooling tower - Compare values of required water with PH standards - Collect Waste and dispose it of according to workplace procedures - Conduct work in accordance with the workplace environmental guidelines - Prepare report | - Chemicals used for the treatment of water - Properties of the different chemicals - Ratio between water and chemical - Advantages of the water treatment - Examine the water with the help of chemical test - PH value - Hardness of water and neutralization process - Eradication process of fungi - Organic and inorganic material and their properties - Record keeping and reporting Practical Activity Perform water treatment with different methods | Theory-02Hrs. Practical-06 Hrs. Total- 08 Hrs. | - Personal Protective Equipment - Chemical test kit - Water treatment assembly kit - Water pots for sampling | Classroom and Lab |
| - Perform organic and inorganic material treatment procedure | Trainee will be able to: - Perform Chlorination - Remove temporary hardness by boiling in boiler - Remove salt concentration in cooling tower by neutralization process - Insert recommended amount of chemical for eradicate the growth of fungi | - Hydration, and chlorination Hardness of water and neutralization process - Organic and inorganic material and their properties - Perform water treatment with different methods - Eradication process of fungi Practical Activity Remove salt concentration in cooling tower by neutralization process | Theory-02Hrs. Practical-06 Hrs. Total- 08 Hrs. | - Personal Protective Equipment - Chemical test kit - Water treatment assembly kit - Water pots for sampling |  |

## Service and Maintain Transport / Mobile Refrigeration Units

Objective: This module covers the knowledge and  skills required to service and maintain transport / mobile refrigeration units. Students will be expected to diagnose the defects and service / maintain in transport / mobile refrigeration units according to the nature of work at workplace. The underpinning knowledge regarding servicing and maintenance of transport / mobile refrigeration units will be sufficient to provide the basis for work.

Duration:  20 Hours			Theory:  4 Hours			Practice:  16 Hours          	        Credit Hours:  2

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Check and diagnose the defect in the freezer unit | Trainee will be able to: - Inspect unit and ascertain, record to the extent of repair needed. - Prepare list of material, equipment, manpower and items according to the requirement. - Check / observe all components of refrigerant circuit according to standard practices and manufacturer’s specifications to ensure correct performance. - Check / observe all components of the refrigerant system, electrical system and accessories according to standards practices & manufacturer’s specifications to ensure correct operation. - Test system pressure with dry nitrogen gas and locate leaks using specified equipment and recommended safety procedures. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Different types of compressors and their functions - Define pressure and temperature laws - Define temperature and its units - Read and interpret manufacturer’s manuals, specifications etc., - Basic refrigeration and air conditioning principles Refrigeration Cycle - Types of Refrigerants, their properties and applications Practical Activity: - Diagnose faults of Transport Refrigeration by using specified tools and instruments | Theory- 2 Hrs Practical- 6 Hrs Total- 8 Hrs | - Personal Protective Equipment - Basic Hand tools - Basic Electric tools - Gauge manifold - Basic Measuring tools | Class room & Lab |
| LU2. Service / repair refrigerant system of the freezer unit | Trainee will be able to: - Check internal and external electrical / electronic control systems for operations and repair / replace where necessary according to manufacturer’s instructions. - Check electronic climatic controls for smooth operation and replace where necessary according to manufacturer’s instructions. - Check freezer unit for specified /specific performance against manufacturer’s specification | - Functions of the gauge manifold and color code of hoses - Function of service valves - Working principles of the recovery machine - Refrigerant recovery process - Refer to manufacturer’s specifications/ instructions on service and maintenance of transport / mobile refrigeration units - Identify the type of refrigerants - Detection of gas leaks and repairing leaks Pressure testing in refrigerant lines Adherence to conditions of the “Environment Protection Acts “(EPA) - Coupling manifold gauge and hoses to the refrigerant lines either by piercing or using service valves - Safe handling and use of refrigerants, gauges, tools & equipment Record keeping and reporting Practical Activity: - Repair refrigerant leak in Transport Refrigeration system | Theory- 2 Hrs Practical- 10 Hrs Total- 12 Hrs | - Personal Protective Equipment - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Electric tools - Gauge manifold - Recovery Machine with accessories - Vacuum pump - Refrigerant Charging Station - Oxy-acetylene welding set with accessories - Basic Measuring tools | Class room & Lab |

## Apply principles of refrigeration in Cold Storage Technology

Objective: This module covers the knowledge and  skills required to this learning module is designed to apply principles of refrigeration cold storage technology. Students will be expected to recognize causes of food spoilage analyze food spoilage risks in supply chain and select optimum methods storage of perishable food, in cold storage technology according to the nature of work at workplace. His underpinning knowledge regarding cold storage technology will be sufficient to provide the basis for his work.

Duration:  20 Hours			Theory: 5 Hours			Practice: 15 Hours          	        Credit Hours:  2

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify causes of food spoilage | Trainee will be able to: - Obtain and implement work health and safety (WHS) and environmental requirements for a given work area - Determine causes of food spoilage from observation, testing, measurements and/or supply chain tracking - Interpret and apply relevant National / ASHRAE US standards, codes and regulations for food storage and handling - Obtain equipment and resources needed for the task in accordance with enterprise procedures | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) Practical Activity: - Recognize cause of food spoilage | Theory- 1 Hrs Practical- 4 Hrs Total- 5 Hrs | - Personal Protective Equipment - Food analyzer | Class room & Lab |
| LU2. Analyze food spoilage risks in supply chain | Trainee will be able to: - Identify critical points in the food supply chain and determine the associated risks - Identify and document risks and propose appropriate risk minimization strategies - Check proposed risk minimization strategies against relevant standards, codes and legislative requirements - Develop and Provide immediate solutions to unexpected situations of faults - Provide solution which is consistent with enterprise procedures | - Cold storage technology - Principles of refrigeration - Food storage methods - Storage temperature of different type of food - Ability to analyze food properties Practical Activity: - Adopt correct method for storage of different food items | Theory- 2 Hrs Practical- 5 Hrs Total- 7 Hrs | - Personal Protective Equipment - Food analyzer | Class room & Lab |
| LU3. Select optimum storage methods of perishable food | - Trainee will be able to: - Propose options to minimize food spoilage based on analysis of the produce type, facilities available and supply chain requirements - Select optimum solutions with respect to equipment, facilities, processing techniques and cost. - Adopt storage and handling method in accordance with enterprise procedures - Develop proper documentation of the situation and keep record for future reference and use | - Storage methods of perishable food - Define food chain - Define and can analyze food spoilage risks - Record keeping and reporting Practical Activity: - Select accurate temperature and humidity for specified items | Theory- 2 Hrs Practical- 6 Hrs Total- 8 Hrs | - Personal Protective Equipment - Food analyzer | Class room & Lab |

## Maintain and Repair Multi-Stage, Cascade & Ultra-Low Temperature Refrigeration System

Objective: This module covers the knowledge and  skills required to this learning module is designed to maintain and repair multi-stage, cascade & ultra-low temperature refrigeration system. Students will be expected to undertake preventive maintenance checks/ adjustment on multi-stage, cascade and/or ultra-cold industrial refrigeration systems and coordinate an air conditioning system in the production of food products according to the nature of work at workplace. His underpinning knowledge regarding ultra-low temperature refrigeration units will be sufficient to provide the basis for his work.

Duration:  20 Hours			Theory: 4 Hours			Practice: 16 Hours          	        Credit Hours:  2

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Undertake preventive maintenance checks / adjustment on multi- stage, cascade and/or ultra-cold industrial refrigeration systems | Trainee will be able to: - Check the temperature, pressure and properties of the multi-stage, cascade and/or ultra-cold refrigeration system for conformance to specification. - Check the noise/vibration levels of the multi- stage, cascade and/or ultra-cold refrigeration system for conformance to specification. - Perform preventative maintenance tasks according to manufacturers' specifications using refrigeration techniques / practices. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Using tools, techniques and equipment necessary to check multi-stage, cascade and/or ultra-cold industrial refrigeration systems and components for correct operation - Comparing system, sub-systems and component performance/operation against specification - Identifying faulty components and non-compliances making required adjustments to achieve specifications Practical Activity: - Maintain log sheet of unit and Inspect different parts of unit | Theory-2 Hrs Practical- 10Hrs Total- 12 Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Electric tools - Gauge manifold - Recovery Machine with accessories - Vacuum pump - Refrigerant Charging Station - Oxy-acetylene welding set with accessories | Class room & Lab |
| LU2. Coordinate an air conditioning system in the production of food products | Trainee will be able to: - Identify common forms of air conditioning systems used in the production of food products - Assess air conditioning requirements for a given situation in the production process - Identify variables on a psychrometric chart - Apply psychrometric charts for the analysis of air conditioning systems in the production process - Monitor the performance of the air conditioning system in the production process - Rectify issues with performance of air conditioner - Monitor energy efficiency to reduce costs and environmental impacts - Report problems to the designated person | - Applying safety procedures, standard operating procedures and legislative requirements to all work undertaken documenting results of the adjustments - Reading, interpreting and following information on written job instructions, specifications, standard operating procedures, charts, lists, drawings and other applicable reference documents - Procedures for reporting non-conformances procedures and sequence for performing preventative maintenance - Procedures and sequence for performing safety equipment checks specifications and process for identifying system components - Operational characteristics of the system components procedures and all legislative and regulatory requirements for safely removing the refrigerant from the system procedures for dismantling and repairing components, selecting replacement parts, reassembling and testing - Record keeping and reporting Practical Activity: - Diagnose fault in system and Repair faults | Theory- 2Hrs Practical- 6Hrs Total- 8 Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Electric tools | Class room & Lab |

## Monitor Refrigeration in Food Processing

Objective: This module covers the knowledge and  skills required to this learning module is designed to monitor refrigeration in food processing. Students will be expected to organize refrigeration and air conditioning system in the production of food item in food processing according to the nature of work at workplace. His underpinning knowledge regarding food processing refrigeration will be sufficient to provide the basis for his work.

Duration:  30 Hours			Theory: 6 Hours			Practice: 24 Hours          	        Credit Hours:  3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Organize a refrigeration system in the production of food items | Trainee will be able to: - Identify refrigerants and their required properties - Monitor performance of the refrigeration system in the production process - Analyze performance of a refrigeration system according to HVAC standards and manufacturers specifications. - Identify and evaluate ways to improve the performance of the refrigeration system | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Using tools, techniques and equipment necessary to check refrigeration and air conditioning systems and components for correct operation - Comparing system, sub-systems and component performance/operation against specification - Identifying faulty components and non-compliances making required adjustments to achieve specifications - Applying safety procedures, standard operating procedures and legislative requirements to all work undertaken documenting results of the adjustments - Reading, interpreting and following information on written job instructions, specifications, standard operating procedures, charts, lists, drawings and other applicable reference documents - Procedures for reporting non-conformances procedures and sequence for performing preventative maintenance Practical Activity: - Recognize & select refrigeration system - Analyze performance of a refrigeration system for food processing | Theory- 3 Hrs Practical- 15 Hrs Total- 18 Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Electric tools - Gauge manifold - Recovery Machine with accessories - Vacuum pump - Refrigerant Charging Station - Oxy-acetylene welding set with accessories | Class room & Lab |
| LU2. Organize an air conditioning system in the production of food items | Trainee will be able to: - Identify common forms of air conditioning systems used in the production of food products - Assess air conditioning requirements for a given situation in the production process - Identify variables on a psychrometric chart - Apply psychrometric charts for the analysis of air conditioning systems in the production process - Monitor the performance of the air conditioning system in the production process - Rectify issues with performance of air conditioner - Monitor energy efficiency to reduce costs and environmental impacts - Report problems to the designated person | - Procedures and sequence for performing safety equipment checks specifications and process for identifying system components - Operational characteristics of the system components procedures and all legislative and regulatory requirements for safely removing the refrigerant from the system procedures for dismantling and repairing components, selecting replacement parts, reassembling and testing - Record keeping and reporting Practical Activity: - Identify & Rectify issues regarding food processing | Theory- 3 Hrs Practical- 9 Hrs Total- 12 Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Electric tools | Class room & Lab |

## Perform Refrigerant Recovery

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to Couple the recovery unit to the equipment and to  Recover Refrigerant,

Duration:  10 Hours			Theory:03	Hours				Practice: 	07Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Couple the recovery unit to the equipment, | Trainee will be able to: - Identify type of refrigerant to be recovered according to available information. - Select appropriate system for connection of charging hoses, either with piercing valve or charging valve according to requirements. - Ensure recovery unit to be free of any other type of refrigerant. - Transfer refrigerant in unit to a separate recovery cylinder; ensure that no refrigerant escapes to atmosphere. - Connect gauge manifold to system, according to standard color codes of hoses of manifold gauge. - Couple recovery unit to equipment, following standard procedure for connections. - Connect overfill protection device and ensure safety of operation. | - Recovery of refrigerants using recovery machines and allied accessories. - Coupling manifold gauge and hoses to the refrigerant lines either by piercing or using service valves - Types of Refrigerants, their properties and applications - Functions of the gauge manifold and color code of hoses - Function of service valves - Working principles of the recovery machine Practical Activity: - Perform Connection of gauge manifold to system, according to standard color codes of hoses of manifold gauge. - Couple recovery unit to equipment, following standard procedure for connections. | Theory-2 Hrs. Practical-3 Hrs. Total- 5 Hrs. | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Electric tools - Gauge manifold with hoses - Piercing valve - Recovery unit | Class Room and workshop |
| - Recover Refrigerant | Trainee will be able to: - Start recovery unit, monitor process and ensure full recovery of Refrigerant. - Stop recovery unit - Disconnect system according to standard procedure - Ensure no refrigerant escapes to atmosphere | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - Working principles of the recovery machine - Refrigerant recovery process - Safe handling and use of refrigerants, pressure gauges, tools & equipment Practical Activity: - Perform the Transfer of refrigerant in unit to a separate recovery cylinder; ensure that no refrigerant escapes to atmosphere. | Theory-1 Hrs. Practical-4 Hrs. Total- 5 Hrs. | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Electric tools - Gauge manifold with hoses - Piercing valve - Recovery unit | Class Room and workshop |

## Install Residential Air Conditioner

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge for the Installation  of Window Air Conditioner,

Duration:  40 Hours			Theory:06	Hours				Practice: 	34 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Install Window Air Conditioner , | - Trainee will be able to: - Select tools, equipment and related accessories according to job requirements - Mark the location on the wall where Window Air Conditioner to be installed according to Unit specifications and client requirements - Make opening at the marked area on the wall - Fix Iron / wooden frame in the opening firmly and insert in it the Air Conditioner cover according to the instructional manual and standards - Install the Air conditioner in the framed opening with standard slope so that condensate water drops outside - Cover / Seal side air gaps of opening with insulation material - Fix the fancy wooden border / frame around the Air conditioner grill as per client’s requirement - Fix the Air Conditioner condensate drainpipe and put it into main sewerage line - Install power supply with circuit breaker near the Air Conditioner - Remove all packing material - Cardboard, Styrofoam, Tape and Plastic Film from the site after the installation - Switch on the Air Conditioner and check Air Conditioner performance as per capacity and specifications | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989Basic load calculation for cooling / heating. - Basic load calculation for cooling / heating - Fundamental knowledge of HVACR, Electric and Electronics - Techniques for installation of Window Air conditioner - Electrical / HVAC layout plans/wiring diagrams. - Types of electrical wires and cables, including underground cables, their ratings and its applications - Basic Masonry and Carpentry applications - Gas welding (Soldering and Brazing) - Types of Insulation and their applications Practical Activity: Perform the following - Electrical / HVAC layout plans and wiring - Basic Masonry and Carpentry work - installation of Window Air conditioner - Insulation of side crakes and Gapes | Theory-3 Hrs. Practical-15 Hrs. Total- 18 Hrs. | - Measuring tools ,Measuring Tape ,Tri square - AVO meter - Sprit level - Drill Machine - Screw driver set | Class Room and workshop |
| - Install Split Air Conditioner | Trainee will be able to: - Select tools, equipment and related accessories according to job requirements - Select and mark the areas on the walls where Indoor and Outdoor units are to be installed according to specifications and client requirements - Perform physical inspection of indoor and outdoor unit according to unit specifications - Make opening for the refrigerant pipes, condensate pipe and control wires to pass through - Mount the Indoor unit wall mounting plate according to manufacturer specifications and install the Indoor unit on it - Prepare base for the fixing of Outdoor unit according to manufacturer specifications and fix the Outdoor unit there - Make electric supply connection at outer unit. - Connect the refrigerant pipes amongst/ to both indoor and outdoor units, supply and control wires according to manufacturer manual - Add additional refrigerant for additional piping according to manufacturer recommendations - Make oil trap in copper pipe as per site requirement Perform leak test, evacuation procedure, charge refrigerant and open the service valves - Insulate the joints and refrigerant pipes according to standards and manufacturer installation manual - Remove all packing material - Cardboard, Styrofoam, Tape and Plastic film - Switch on the Air Conditioner and check performance as per capacity and specifications | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989Basic load calculation for cooling / heating. - Basic load calculation for cooling / heating - Fundamental knowledge of HVACR, Electric and Electronics - Techniques for installation of Window / Split (DC Inverter) - Technical Operations of all types of split air conditioners - Electrical / HVAC layout plans/wiring diagrams. - Types of electrical wires and cables, including underground cables, their ratings and its applications - Methods of Copper Tube cutting / Reaming / Bending /Swaging / Flaring / Brazing / Jointing / fixing - Basic Masonry and Carpentry applications - Gas welding (Soldering and Brazing) - Types of Insulation and their applications - Methods of Pressurizing/ Evacuation / Purging / Refrigerant charging Practical Activity: - Mark location according to specifications and standards - Perform electric connections to joint indoor unit and outdoor unit - Prepare the base for condensing unit - Install the indoor / outdoor unit - Purge refrigerant and charge the unit | Theory-4 Hrs. Practical-18 Hrs. Total- 22 Hrs. | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - AVO meter - Adjustable Screw Wrench - Combination Plier - Nose Plier Set - Locking Plier - Copper tube cutter - Electric Hand Drill Machine | Class Room and workshop |

## Repair Refrigerator, Deep Freezer, Display Unit, Bottle Cooler and Water Cooler

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to repair refrigerators, deep freezers, display units, bottle coolers and water coolers. Students will be expected to repair refrigerators, deep freezers, display units, bottle coolers and water coolers,

Duration:  70 Hours			Theory:20	Hours				Practice: 	50Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Check and identify defects in refrigerators, deep freezers, display units, bottle coolers and water coolers | Trainee will be able to: - Check unit for the extent of repair needed ascertain and recorded. - Enlist equipment / items, material main power and accessories as required for job. - Check all components of the electrical / electronic circuit according to standard / practices and manufacturers specifications to ensure correct performance. - Check all components of the refrigerant circuit according to standard / practices and manufactures specifications to ensure correct performance. - Check all components of the Air-flow system according to standards / practices and manufactures specifications to ensure correct performance. - Check outer cover / chassis for corrosion etc. - Test system pressure with dry nitrogen and locate gas leaks by using specified equipment following safety procedures | - Types of Refrigerants, their properties and applications - Functions of the gauge manifold and color code of hoses - Function of service valves - Working principles of the recovery machine Practical Activity: - Perform Connection of gauge manifold to system, according to standard color codes of hoses of manifold gauge. - Couple recovery unit to equipment, following standard procedure for connections. | Theory-10 Hrs. Practical-25 Hrs. Total- 35 Hrs. | - Measuring tools , gauge manifold - Hand tools Pl iers, screw Driver set, Adjustable spanners, Tube cutter, Fixed spanner set Ratchet - Refrigerant Recovery unit - Piercingvalve | Class Room and workshop |
| - Repair refrigerators, deep freezers, display units, bottle coolers and water coolers | Trainee will be able to: - Identify defects and repair / replace the relevant component(s). - Perform brazing and test system for leakages - Evacuate the system using vacuum pump and test according to manufacturer’s specifications - Recharge refrigerant using specified type of refrigerant and recharging equipment, to required specification following safety practices. - Check filters clean / replace if necessary. - Check corrosion in outer cover / base plate and restore required conditions. - Operate and check unit to ensure satisfactory performance according to manufacturer’s specifications | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - Working principles of the recovery machine - Refrigerant recovery process Practical Activity: - Perform the Transfer of refrigerant in unit to a separate recovery cylinder; ensure that no refrigerant escapes to atmosphere. | Theory-10 Hrs. Practical-25Hrs. Total- 35 Hrs. | - Measuring tools , gauge manifold - Hand tools Pliers, screw Driver set, Adjustable spanners, Tube cutter ,Fixed spanner set Ratchet Refrigerant Recovery unit Piercing valve | Class Room and workshop |

## Repair and Service Residential Air Conditioner

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge todiagnose / repair / service residential Air conditioners at workplace in accordance with the manufacturer’s specifications / guidelines and the knowledge regarding safety rules, personal protective equipment, and international standards for repairing / servicing of Residential Air conditioners to provide you the basis for student work,

Duration:  60 Hours			Theory:12	Hours				Practice: 	48Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Diagnose Faults in Residential Air Conditioner | Trainee will be able to: - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Check for obvious problem to determine which component or system is causing the problem - Select tools, equipment and related accessories according to requirements and standards. - Check power supply, electric wiring, electric / electronic components and refrigerant pressure to determine the exact problem by using AVO meter / Gauge manifold / flow chart as recommended by manufacturer and record the results - Eliminate the causes of the problem according to the manufacturer’s manual and standards. - Isolate and recheck the causes of the problem and rectify the fault - Start the Air conditioner and recheck the unit as specified in the manufacturer’s manual and record the results | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - Fundamental knowledge of HVACR, Electric and Electronics - Techniques for repairing of Window / Split air conditioners - Technical Operations of split air conditioners - Techniques of Diagnose and Troubleshooting of Residential Air conditioners - Familiar with Residential Air conditioners error codes and solution - Types of Motors used in Residential Air conditioners Practical Activity: - Diagnose faults of Air Conditioner by using specified tools and instruments | Theory-3 Hrs. Practical-12 Hrs. Total- 15 Hrs. | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Marking tools - Basic Electric tools - Power tools - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Digital Clamp-On Meter Digital Multi Meter | Class Room and workshop |
| - Repair Window / Split Air Conditioner | Trainee will be able to: - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Select tools, equipment and related accessories according to job requirements - Disconnect the Air conditioner from electric supply and follow the manual instructions for rectification - Rectify the faults as per diagnosed, repair / replace the components, as necessary - Switch on the Air conditioner to check the performance of electrical/ electronic and mechanical components as specified in the manufacturer’s manual and record the results | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - Techniques of Diagnose and Troubleshooting of Residential Air conditioners - Techniques for repairing of Window / Split air conditioners - Methods of Pressurizing/ Evacuation / Purging / Refrigerant charging - Types of Refrigerant, its properties, recovery and reclaiming - Record keeping and reporting. Practical Activity: - Repair refrigerant leak in Air Conditioner - Replace the compressor of Air conditioner - Recharging of refrigerant - Replace the printed circuit board (PCB) of split air conditioner | Theory-3 Hrs. Practical-12 Hrs. Total- 15 Hrs. | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Portable Refrigerant Charging Station - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Tube Cutter - Digital Optical Tachometer - Micron Pressure Gauge - Digital Pressure Gauges Set (High &Combine) - Pinch-Off Plier - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type) - Megohmmeter (0 - 1000 Volts) - Laser Temperature Measuring Device Nose Plier Set - Digital Clamp-On Ampere Meter - Digital Multi Meter | Class Room and workshop |
| LU3. Service Window Air conditioners | - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Select tools, equipment and related accessories according to job requirements - Start the Air conditioner, check and record performance by using specified test instruments - Disconnect the Air conditioner from electric supply and remove Air conditioner from the cover - Secure the electric / electronic components with polythene sheet - Clean / wash the all mechanical parts of Window Air conditioner with specified cleaning agents / detergent by using pressure pump. - Fix the Air conditioner in the cover, connect with electric supply, check and record performance | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - Fundamental knowledge of HVACR, Electric and Electronics - Standard procedures of Service and lubrication Window Air conditioners - Record keeping and reporting Practical Activity: Perform water cleaning service on window Air Conditioners according to the standard procedure | Theory-3 Hrs. Practical-12 Hrs. Total- 15 Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Portable Refrigerant Charging Station - Digital Air Flow / Velocity Meter - Water Pressure Gun for Service - Electronic Leak Detector - Tube Cutter - Digital Optical Tachometer - Micron Pressure Gauge - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type) - Laser Temperature Measuring Device - Nose Plier Set - Digital Clamp-On Ampere Meter - Digital Multi Meter - Screwdriver Set | Class Room and workshop |
| LU4.Service Split Air Conditioner | - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Select tools, equipment and related accessories according to job requirements - Start the Air conditioner, check and record performance by using specified test instruments - Pump down the split type Air conditioner and dismantle the both indoor and condensing unit - Clean the components of Air conditioner with specified cleaning agents/tools & material. - Re-Install the indoor & outdoor unit, connect with refrigerant pipes, control wires and open the service valves - Switch on the Air conditioner, check and record performance | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - Fundamental knowledge of HVACR, Electric and Electronics - Standard procedures of Service and lubrication of split Air conditioners - Record keeping and reporting Practical Activity: - Pump down the split air conditioner - Perform water cleaning service on split Air Conditioners according to the standard procedure | Theory-3 Hrs. Practical-12 Hrs. Total- 15 Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Portable Refrigerant Charging Station - Digital Air Flow / Velocity Meter - Water Pressure Gun for Service - Electronic Leak Detector - Tube Cutter - Digital Optical Tachometer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type) - Digital Clamp-On Ampere Meter - Digital Multi Meter - Screwdriver Set | Class Room and workshop |

## Overhaul the compressors

Objective: This module covers the knowledge and  skills required to to overhaul the compressors in accordance with the manufacturer’s specifications / guidelines.

Duration:  20 Hours			Theory:05	Hours				Practice: 	15 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Prepare to dismantle compressor, | Trainee will be able to: - Determine job requirements from workplace instructions - Control and interpret refrigerant gases during installation, servicing or de-commissioning of air conditioners source - Source and interpret dismantling information - Analyze dismantling options and select most appropriate to the circumstances - Identify hazards associated with the work and manage the risks - Select dismantling tools and equipment and check for serviceability | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - Fundamental knowledge of HVACR, Electric and Electronics - Types of Lubricants and their properties - Compressor types/ Specifications and applications - Gas welding (Soldering and Brazing) Practical Activity: - Select dismantling tools and equipment - Remove compressor’s Electrical and Mechanical connections | Theory-1 Hrs. Practical-3 Hrs. Total- 4 Hrs. | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Electric tools - Portable Refrigerant Charging Station | Class Room and workshop |
| - Dismantle and evaluate compressor and components | - Dismantle compressor in a logical sequence according to manufacturer, workplace procedures, safety & environmental requirements and without affecting unnecessary damage to components or systems - Clean components for evaluation according to workplace procedures, safety and environmental requirements - Measure and Compare components with manufacturer specifications and serviceability is determine - Determine component repair methods - Identify unserviceable parts and replacement parts sourced | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - Fundamental knowledge of HVACR, Electric and Electronics - Techniques for Dismantling of compressors Practical Activity: - Dismantle compressor - Identify unserviceable parts and replacement parts sourced | Theory-1 Hrs. Practical-3 Hrs. Total- 4 Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Portable Refrigerant Charging Station - Electronic Leak Detector - Tube Cutter - Micron Pressure Gauge - Digital Pressure Gauges Set (High &Combine) - Electric Hand Grinder - Digital Multi Meter - Electric Hand Drills - Screwdriver Set | Class Room and workshop |
| - Carry out overhaul | - Source and interpret overhaul information - Analyze overhaul options and select those most appropriate to the circumstances - Select and check overhaul tools and equipment for serviceability - Machine the components repair / replace as required - Carryout adjustments according to manufacturer specifications, workplace procedures, safety and | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental knowledge of HVACR, Electric and Electronics - Techniques for overhauling of compressors - Compressor types/ Specifications and applications - Gas welding (Soldering and Brazing) Practical Activity: - Servicing of compressor - Cleaning of compressor | Theory-1 Hrs. Practical-3 Hrs. Total- 4 Hrs. | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Electric tools - Electric Hand Grinder - Digital Multi Meter - Electric Hand Drills - Screwdriver Set | Class Room and workshop |
| - Assemble compressor and components | Trainee will be able to: - Assemble compressor according to manufacturer specifications, workplace procedures, and safety & environmental requirements - Measure tolerance and clearances against manufacturer specifications and make necessary adjustments - Complete assembly of compressor within workplace timeframes and without causing damage to other components or systems - Carryout post-assembly testing according to workplace procedures, safety & environmental requirements - Detect and rectify problem(s) as have been introduced during the assembly process | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental knowledge of HVACR, Electric and Electronics - Techniques for Assembling of compressors - Compressor types/ Specifications and applications - Gas welding (Soldering and Brazing) Practical Activity: - Assemble compressor according to requirements - Measure tolerance and clearances | Theory-1 Hrs. Practical-3 Hrs. Total- 4 Hrs. | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Electric tools - Electric Hand Grinder - Digital Multi Meter - Electric Hand Drills - Screwdriver Set | Class Room and workshop |
| - Complete work processes | - Ensure final inspection to make work according to workplace expectations and ready compressor for use or storage - Clean work area, dispose of waste and non-recyclable materials and store tools and equipment or identify any faulty electrical equipment tagged and isolated according to workplace procedures - Process workplace documentation according to workplace procedures | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental knowledge of HVACR, Electric and Electronics - Record keeping and reporting Practical Activity: - Analyze compressor performance - Clean work station dispose of waste . - Process workplace documentation | Theory-1 Hrs. Practical-3 Hrs. Total- 4 Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Screwdriver Set Report formats and record book |  |

## Repair and Service Residential Refrigeration Units

Objective: This module covers the knowledge and  skills required to diagnose / repair / service residential refrigeration units at workplace in accordance with international standards for repairing / servicing of residential refrigeration units .

Duration:  30 Hours			Theory:6	Hours				Practice: 	24 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Check and identify defects in refrigerators, deep freezers, display units, bottle coolers and water coolers | Trainee will be able to: - Check unit for the extent of repair needed ascertain and recorded. - Enlist equipment / items, material main power and accessories as required for job. - Check all components of the electrical / electronic circuit according to standard / practices and manufacturers specifications to ensure correct performance. - Check all components of the refrigerant circuit according to standard / practices and manufactures specifications to ensure correct performance. - Check all components of the Air-flow system according to standards / practices and manufactures specifications to ensure correct performance. - Check outer cover / chassis for corrosion etc. - Test system pressure with dry nitrogen and locate gas leaks by using specified equipment following safety procedures. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental knowledge of HVACR, Electric and Electronics - Step by step techniques for Diagnosing the faults in Refrigerators / Freezers / Water Coolers and Water Dispensers - Technical Operations of Non-Frost refrigerators - Types of electrical wires and cables, their ratings and applications Practical Activity: - Diagnose faults of Refrigeration unit by using specified tools and instruments. | Theory-3 Hrs. Practical-12 Hrs. Total- 15 Hrs. | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Tube Cutter - Digital Optical Tachometer - Micron Pressure Gauge - Digital Pressure Gauges Set (High &Combine) - Megger meter (0 - 1000 Volts) - Laser Temperature Measuring Device Nose Plier Set - Electric Hand Grinder - Digital Clamp-On Ampere Meter - Digital Multi Meter - Hot Air Gun - Digital Capacitor Analyzer - Hand Electric Blower - Digital Humidity Meter - Digital Psychrometer (Hygrometer) - Pulley Wheel Puller - Screwdriver - Allen Key Set - Locking Plier | Class Room and workshop |
| - Repair refrigerators, deep freezers, display units, bottle coolers and water coolers | - Identify defects and repair / replace the relevant component(s). - Perform brazing and test system for leakages - Evacuate the system using vacuum pump and test according to manufacturer’s specifications - Recharge refrigerant using specified type of refrigerant and recharging equipment, to required specification following safety practices. - Check filters clean / replace if necessary. - Check corrosion in outer cover / base plate and restore required conditions. - Operate and check unit to ensure satisfactory performance according to manufacturer’s specifications | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental knowledge of HVACR, Electric and Electronics - Techniques for repairing of Refrigerators / Freezers / Water Coolers and Water Dispensers Practical Activity: - Check & Replace electrical accessories of unit - Check & Replace the mechanical parts & accessories of the unit - Charge the refrigerant in unit | Theory-3 Hrs. Practical-12 Hrs. Total- 15 Hrs. | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Portable Refrigerant Charging Station - Digital Air Flow / Velocity Meter - Water Pressure Gun for Service - Electronic Leak Detector - Tube Cutter - Digital Optical Tachometer - Micron Pressure Gauge - Digital Pressure Gauges Set (High &Combine) - Pinch-Off Plier - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type) - Megger meter (0 - 1000 Volts) - Laser Temperature Measuring Device Nose Plier Set - Electric Hand Grinder - Soldering Iron - Digital Clamp-On Ampere Meter - Digital Multi Meter - Electric Hand Drills - Hot Air Gun - Digital Capacitor Analyzer - Hand Electric Blower - Digital Humidity Meter - Pulley Wheel Puller - Screwdriver Set - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Gas Welding Set with All Accessories - Allen Key Set - Locking Plier | Class Room and workshop |

## Test, recover, evacuate and charge refrigeration system

Objective: This module covers the knowledge and  skills required to this learning module is designed to test, recover and charge refrigeration system at workplace in accordance with the manufacturer’s specifications / guidelines.

Duration:  70 Hours			Theory:	13 Hours				Practice: 	57 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Assess refrigeration system operation | Trainee will be able to: - Apply refrigeration system operating principles and terminology to assessment activities. - Obtain all relevant information and interpret correctly prior to the commencement of work on the refrigeration system. - Undertake refrigeration system checks safely in accordance with standard operating procedures, relevant codes and regulations. - Apply appropriate operating procedures as required. - Determine pressures and temperatures correctly and recorded. - Rectify faults | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - Fundamental knowledge of HVACR, Electric and Electronics - Techniques for repairing of Window / Split air conditioners - Technical Operations of split air conditioners - Electric circuit diagrams. - Copper piping layout - Types of electrical wires and cables, including underground cables, their ratings and its applications - Techniques of Diagnose and Troubleshooting of Residential Air conditioners - Familiar with Residential Air conditioners error codes and solution - Types of Motors used in Residential Air conditioners - Types of Lubricants and their properties - Capable to replace PCB Card - Compressor types/ Specifications and applications - Methods of Copper Tube cutting / Bending /Swaging / Flaring / Brazing / Jointing / fixing - Gas welding (Soldering and Brazing) - Types of Insulation and their applications - Methods of Pressurizing/ Evacuation / Purging / Refrigerant charging - Types of Refrigerant, its properties, recovery and reclaiming - Record keeping and reporting Practical Activity: - Assess refrigeration system operation - Record performance and make report | Theory-5 Hrs. Practical-18 Hrs. Total- 23Hrs. | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Portable Refrigerant Charging Station - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Tube Cutter - Digital Optical Tachometer - Micron Pressure Gauge - Digital Pressure Gauges Set (High &Combine) - Megohmmeter (0 - 1000 Volts) - Laser Temperature Measuring Device Nose Plier Set - Digital Clamp-On Ampere Meter - Digital Multi Meter - Electric Hand Drills - Digital Capacitor Analyzer - Digital Humidity Meter - Digital Psychrometer (Hygrometer) - Pulley Wheel Puller - Screwdriver Set - Allen Key Set - Locking Plier | Class Room and workshop |
| - Recover refrigerant and evacuate system | Trainee will be able to: - Recover the refrigerant from the system in accordance with standard operating procedures, codes and regulations. - Contain the refrigerant recovered from the refrigeration system in accordance with the relevant codes and regulations of ASHRAE. - Evacuate the refrigeration system in accordance with standard operating procedures, codes and regulations | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - Fundamental knowledge of HVACR, Electric and Electronics - Techniques to Recover refrigerant and to evacuate system Technical Operations of split air conditioners - Electric circuit diagrams. - Compressor types/ Specifications and applications - Methods of Copper Tube cutting / Bending /Swaging / Flaring / Brazing / Jointing / fixing - Gas welding (Soldering and Brazing) - Types of Insulation and their applications - Methods of Pressurizing/ Evacuation / Purging / Refrigerant charging - Types of Refrigerant, its properties, recovery and reclaiming - Record keeping and reporting Practical Activity: - Recover refrigerant - Leak testing & Repair leaks - Evacuate system | Theory-4 Hrs. Practical-21 Hrs. Total- 25 Hrs. | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Portable Refrigerant Charging Station - Electronic Leak Detector - Tube Cutter - Micron Pressure Gauge - Digital Pressure Gauges Set (High &Combine) - Screwdriver Set - Allen Key Set - Locking Plier | Class Room and workshop |
| - Charge the refrigeration system | - Charge the refrigeration system with the correct refrigerant in accordance with standard operating procedures. - Add the appropriate lubricating oil to the refrigeration system in accordance with standard operating procedures. - Check the refrigeration system for leaks. | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - Fundamental knowledge of HVACR, Electric and Electronics - Methods of Pressurizing/ Evacuation / Purging / Refrigerant charging - Types of Refrigerant, its properties, recovery and reclaiming - Record keeping and reporting Practical Activity: - Purge and charge refrigerant | Theory-4 Hrs. Practical-18 Hrs. Total- 22 Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Electric tools - Portable Refrigerant Charging Station - Electronic Leak Detector - Tube Cutter - Micron Pressure Gauge - Digital Pressure Gauges Set (High &Combine) - Screwdriver Set - Allen Key Set - Locking Plier | Class Room and workshop |

## Calculate Fundamental Properties of Gasses

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to calculate the basic properties of gasses, quantity of heat in gasses, calculate & convert temperature scale, pressure volume and temperature relationship of gasses. Students will be expected to calculate properties of gasses according to the nature of work at workplace. His underpinning knowledge regarding calculation of properties of gasses will be sufficient to provide the basis for his work.

Duration:  40	Hours			                             Theory: 8	Hours				                  Practice: 	32 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Calculate the basic properties of gasses. | Trainee will be able to: - Convert other system of units into S.I units. - Calculate pressure of gases. - Calculate energy, density and specific volume of gases. - Calculate volume and velocity of gases. - Calculate vapor density of gases | - Identification and use of Personal Protective Equipment (PPE) - Hazards that are most likely to cause harm to health and safety - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - States of Matter - SI units, pressure, energy, density and specific volume of gases - Work, area, volume and velocity of gases - Density of gases, sensible, latent and total heat - Absolute temperature and pressure of gases - Boyles’s and Charles’s law - Gay-Lussac law and General gas law - Solving problems on sensible and latent heat - Solving problem - Record keeping and reporting Practical Activity: - Perform engine compression test (Dry test and wet test) and engine vacuum test - Identified different parts of petrol engine | Theory-2 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Sling Psychrometer - Psychrometer Chart - Lead Pencil - Foot rule - Eraser - Sharpener - Compound Gauge - High Pressure Gauge - Thermometer | Class Room and workshop |
| - Calculate the quantity of heat in gases. | Trainee will be able to: - Calculate sensible heat. - Calculate latent heat - Calculate total heat | - Identification and use of Personal Protective Equipment (PPE) - Hazards that are most likely to cause harm to health and safety with HVAC tools - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - SI units, pressure, energy, density and specific volume of gases - Work, area, volume and velocity of gases - Density of gases, - Heat in Substance - Sensible, latent and total heat - Absolute temperature and pressure of gases - Solving problems on sensible and latent heat - Solving problem - Record keeping and reporting Practical Activity: - Perform engine compression test (Dry test and wet test) and engine vacuum test - Identified different parts of diesel engine | Theory-2 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Sling Psychrometer - Psychrometer Chart - Lead Pencil - Foot rule - Eraser - Sharpener - Compound Gauge - High Pressure Gauge - Thermometer | Class Room and workshop |
| - Calculate and convert the temperature scale. | Trainee will be able to: - Convert the Units of temperature into different systems. - Convert the Units of pressure into different systems. - Calculate the absolute temperature and pressure. | - Identification and use of Personal Protective Equipment (PPE) - Hazards that are most likely to cause harm to health and safety with HVAC tools - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - SI units, pressure, energy, density and specific volume of gases - Work, area, volume and velocity of gases - Density of gases, sensible, latent and total heat - Temperature & Their Scales - Absolute temperature and pressure of gases - Solving problems Converting Scales of Temperature. - Record keeping and reporting | Theory-2 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Sling Psychrometer - Psychrometer Chart - Lead Pencil - Foot rule - Eraser - Sharpener - Compound Gauge - High Pressure Gauge - Thermometer |  |
| - Pressure, volume and temperature relationship of gases. | Trainee will be able to: - Calculate Boyle’s law. - Calculate Charles’s law. - Calculate properties of Gay-Lussac law - Calculate general gas (equation) law. | - Identification and use of Personal Protective Equipment (PPE) - Hazards that are most likely to cause harm to health and safety with HVAC tools - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - SI units, pressure, energy, density and specific volume of gases - Work, area, volume and velocity of gases - Density of gases, sensible, latent and total heat - Absolute temperature and pressure of gases - Boyles’s and Charles’s law - Gay-Lussac law and General gas law - Solving problems on sensible and latent heat - Solving problem Boyles’s, Charles’s and Gay-Lussac and General gas law - Record keeping and reporting | Theory-2 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Sling Psychrometer - Psychrometer Chart - Lead Pencil - Foot rule - Eraser - Sharpener - Compound Gauge - High Pressure Gauge - Thermometer |  |

## Calculate Psychrometric Processes of Air

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to identify and evaluate cool & heat Psychrometric processes of air. Students will be expected to calculate and evaluate Psychrometric processes according to the nature of work at workplace. His underpinning knowledge regarding calculation and evaluation of Psychrometric process will be sufficient to provide the basis for his work.

Duration:  70	Hours			                             Theory: 9	Hours				                  Practice: 	61 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify cool Psychrometric processes of air | Trainee will be able to: - Identify and mark the sensible cooling process on Psychrometric chart as per given reading. - Identify and mark the cooling and humidification process on Psychrometric chart as per given reading. - Identify and mark the cooling and dehumidification process on Psychrometric chart as per given reading. - Identify and mark the evaporative cooling process on Psychrometric chart as per given reading. - Identify and mark the air mixing process on Psychrometric chart as per given reading. | - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Psychrometric chart - Sensible Cooling, Practical Activity: - Perform engine compression test (Dry test and wet test) and engine vacuum test - Identified different parts of petrol engine | Theory-2 Hrs. Practical-18 Hrs. Total- 20 Hrs. | - Sling Psychrometer - Psychrometer Chart - Lead Pencil - Foot rule - Eraser - Sharpener - Compound Gauge - High Pressure Gauge - Thermometer | Class Room and workshop |
| LU2. Calculate the quantity of heat in gases. | Trainee will be able to: - Identify and mark the Sensible heating process on Psychrometric chart as per given reading. - Identify and mark the heating and humidification process on Psychrometric chart as per given reading. - Identify and mark the heating and dehumidification process on Psychrometric chart as per given reading. - Identify and mark the air mixing process on Psychrometric chart as per given reading. | - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Psychrometric chart - Sensible Cooling, Sensible Heating, Practical Activity: - Perform engine compression test (Dry test and wet test) and engine vacuum test - Identified different parts of diesel engine | Theory-4 Hrs. Practical-26 Hrs. Total- 30 Hrs. | - Sling Psychrometer - Psychrometer Chart - Lead Pencil - Foot rule - Eraser - Sharpener - Compound Gauge - High Pressure Gauge - Thermometer | Class Room and workshop |
| LU3. Evaluate Psychrometric properties. | Trainee will be able to: - Calculate sensible heating and cooling properties. - Calculate cooling and dehumidification properties. - Calculate heating humidification properties. - Calculate evaporative cooling properties. - Calculate air mixing properties. | - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Psychrometric chart - Sensible Cooling, Sensible Heating, humidification and dehumidification - Air mixing process - Heating and humidification - Heating and dehumidification - Calculation of evaporative cooling process - Cooling and Humidification (Evaporative Cooling) - Cooling and Dehumidification (Summer Cooling) | Theory-3 Hrs. Practical-17 Hrs. Total- 20 Hrs. | - Sling Psychrometer - Psychrometer Chart - Lead Pencil - Foot rule - Eraser - Sharpener - Compound Gauge - High Pressure Gauge - Thermometer | Class Room and workshop |

## Calculate Psychrometric Properties of System Air

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to draw and calculate Psychrometric properties of system air. Students will be expected to calculate Psychrometric properties of system air according to the nature of work at workplace. His underpinning knowledge regarding calculation of Psychrometric properties of system air will be sufficient to provide the basis for his work.

Duration:  80	Hours			                             Theory: 10 Hours				                  Practice: 	70 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Calculate the Psychrometric properties of air. | Trainee will be able to: - Calculate the relative humidity - Calculate the specific humidity - Calculate the specific enthalpy - Calculate the enthalpy - Calculate the specific volume - Calculate the volume of mixture per kg of dry air | - Identification and use of Personal Protective Equipment (PPE) - Hazards that are most likely to cause harm to health and safety with HVAC tools - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Relative and specific humidity - Enthalpy, specific volume and specific enthalpy - Volume of mixture per kg of dry air - Dry bulb temperature and wet bulb temperature - Define humidification and de humidification - Saturation and dew point temperature - Calculation of enthalpy deviation and specific volume - Heating and cooling processes of air - Sensible heat factor / ratio - Bypass return air - Bypass factor - Content factor - Degree day - Use of Psychrometric chart Practical Activity: - Perform engine compression test (Dry test and wet test) and engine vacuum test - Identified different parts of petrol engine | Theory-2 Hrs. Practical-18 Hrs. Total- 20 Hrs. | - Sling Psychrometer - Psychrometer Chart - Lead Pencil - Foot rule - Eraser - Sharpener - Compound Gauge - High Pressure Gauge - Thermometer | Class Room and workshop |
| LU2. Draw Psychrometric properties of air | Trainee will be able to: - Draw dry bulb temperature line on Psychrometric chart. - Draw wet bulb temperature line on Psychrometric chart. - Draw dew point temperature line on Psychrometric chart. - Draw relative humidity curve on Psychrometric chart. - Draw specific humidity / humidity ration line on Psychrometric chart. - Draw saturation curve on Psychrometric chart. - Draw enthalpy line on Psychrometric chart. - Determine enthalpy deviation on Psychrometric chart. - Determine specific volume line on Psychrometric chart. | - Identification and use of Personal Protective Equipment (PPE) - Hazards that are most likely to cause harm to health and safety with HVAC tools - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Relative and specific humidity - Enthalpy, specific volume and specific enthalpy - Volume of mixture per kg of dry air - Dry bulb temperature and wet bulb temperature - Define humidification and de humidification - Saturation and dew point temperature - Calculation of enthalpy deviation and specific volume - Heating and cooling processes of air - Use of Psychromatric Chart Practical Activity: - Perform engine compression test (Dry test and wet test) and engine vacuum test - Identified different parts of diesel engine | Theory-4 Hrs. Practical-26 Hrs. Total- 30 Hrs. | - Sling Psychrometer - Psychrometer Chart - Lead Pencil - Foot rule - Eraser - Sharpener - Compound Gauge - High Pressure Gauge - Thermometer | Class Room and workshop |
| LU3. Calculate the properties of system air | Trainee will be able to: - Calculate properties of air in heating or cooling process - Calculate the latent heat - Calculate the sensible heat - Calculate sensible heat factor - Calculate the properties of bypass return air - Calculate the properties of air in a duct | - Identification and use of Personal Protective Equipment (PPE) - Hazards that are most likely to cause harm to health and safety with HVAC tools - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Relative and specific humidity - Enthalpy, specific volume and specific enthalpy - Volume of mixture per kg of dry air - Dry bulb temperature and wet bulb temperature - Define humidification and de humidification - Saturation and dew point temperature - Calculation of enthalpy deviation and specific volume - Heating and cooling processes of air - Sensible heat factor / ratio - Plot Lines on Psycrometric Chart - Evaluate Properties on Air | Theory-4 Hrs. Practical-26 Hrs. Total- 30 Hrs. | - Sling Psychrometer - Psychrometer Chart - Lead Pencil - Foot rule - Eraser - Sharpener - Compound Gauge - High Pressure Gauge - Thermometer | Class Room and workshop |

## Analyze Psychrometric Performance of HVAC Systems

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to analyze Psychrometric performance of HVAC systems. Students will be expected to analyze the Psychrometric performance according to the nature of work at workplace. His underpinning knowledge regarding Psychrometric performance will be enough to provide the basis for his work.

Duration: 70	Hours			                             Theory: 10 Hours				                  Practice: 	60 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare to analyze the Psychrometric performance of HVACR System | Trainee will be able to: - Measure indoor room temperature - Measure atmospheric temperature - Measure specific heat of air at constant pressure - Measure mass of available room air | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Psychrometric principals / parameters in respect of HVACR like Wet Bulb temperature, Dry Bulb temperatures, PH values etc. - Effective strategies for analyzing refrigeration and air conditioning systems performance - Psychometric performance parameters, specifications and performance requirements appropriate to each situation. - Documenting analysis details of all findings, calculations and assumptions. - Record keeping and reporting Practical Activity: - Perform engine compression test (Dry test and wet test) and engine vacuum test - Identified different parts of petrol engine | Theory-2 Hrs. Practical-18 Hrs. Total- 20 Hrs. | - Sling Psychrometer - Psychrometer Chart - Lead Pencil - Foot rule - Eraser - Sharpener - Compound Gauge - High Pressure Gauge - Thermometer | Class Room and workshop |
| LU2. Analyze the Psychrometric performance of HVACR systems | Trainee will be able to: - Calculate mass flow rate of air - Calculate volume flow rate of air - Calculate temperature of supply air - Calculate temperature of return air - Calculate cooling load of given room | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Psychrometric principals / parameters in respect of HVACR like Wet Bulb temperature, Dry Bulb temperatures, PH values etc. - Effective strategies for analyzing refrigeration and air conditioning systems performance - Psychometric performance parameters, specifications and performance requirements appropriate to each situation. - Results of the analysis - Documenting analysis details of all findings, calculations and assumptions. - Record keeping and reporting Practical Activity: - Perform engine compression test (Dry test and wet test) and engine vacuum test - Identified different parts of diesel engine | Theory-3 Hrs. Practical-27 Hrs. Total- 30 Hrs. | - Sling Psychrometer - Psychrometer Chart - Lead Pencil - Foot rule - Eraser - Sharpener - Compound Gauge - High Pressure Gauge - Thermometer | Class Room and workshop |
| LU3. Report and act on the results of Psychrometric performance analysis. | Trainee will be able to: - Evaluate to determine their effectiveness of solutions for Psychrometric issues and modify where necessary. - Develop report of the analysis including details of all findings, calculations - Report analysis to the concerned personnel to establish appropriate action to be taken based on findings. | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Psychrometric principals / parameters in respect of HVACR like Wet Bulb temperature, Dry Bulb temperatures, PH values etc. - Effective strategies for analyzing refrigeration and air conditioning systems performance - Psychometric performance parameters, specifications and performance requirements appropriate to each situation. - Results of the analysis - Documenting analysis details of all findings, calculations and assumptions. - Documenting justification of actions to be implemented in accordance with professional standards. - Dealing with unplanned events by drawing on essential knowledge and skills to provide appropriate solutions incorporated in the holistic assessment with the above listed items - Record keeping and reporting | Theory-5 Hrs. Practical-25 Hrs. Total- 30 Hrs. | - Sling Psychrometer - Psychrometer Chart - Lead Pencil - Foot rule - Eraser - Sharpener - Compound Gauge - High Pressure Gauge - Thermometer | Class Room and workshop |

## Develop Geometrical Solids

Objective: This module covers the knowledge and  skills required to this learning module is designed to draw mechanical lines and surfaces, sketches of piping Joints and ducts, draw cone and transition pieces and symbolic representation.

Duration: 60	Hours			                            Theory: 6	Hours				                  Practice: 	54 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Draw Mechanical lines and surfaces | Trainee will be able to: - Draw straight lines and curved lines - Draw inclined and curved surfaces by parallel line and radial line method - Development of a cone by triangular method - Development of a cylinder by radial line method | - Fundamentals units i.e. arcs, circles and ellipse - Development by a radial line method - Development by a parallel line method - Development by a triangular method Practical Activity: - Draw required lines & shapes | Theory-2 Hrs. Practical-15 Hrs. Total- 17 Hrs. | - T-square - Set square - Compass - Eraser - Pencil - Sharpener - Drawing board | Class Room and drawing hall |
| - Draw sketches of piping Joints | Trainee will be able to: - Draw different types of joints - Draw Development of tea joint of a round pipe - Draw line of intersection for intersecting pipe | - Pipe and duct joint - Complete detail of intersecting pipes Practical Activity: - Make sketch for complex drawings | Theory-1 Hrs. Practical-12 Hrs. Total- 13 Hrs . | - T-square - Set square - Compass - Eraser - Pencil - Sharpener4 - Drawing board | Class Room and drawing hall |
| - Draw sketches of Ducts, cone and transition pieces | - Draw different types of ducts - Draw truncated cone and pipe - Draw transition pieces used in pipes and ducts - Draw the development of rectangular duct - Draw the development of square duct - Draw development of truncated cone | - Pipe and duct joint - Frustum of a cone Practical activity - Draw drawings for joints | Theory-2 Hrs. Practical-15 Hrs. Total- 17 Hrs | - T-square - Set square - Compass - Eraser - Pencil - Sharpener4 - Drawing board |  |
| - Draw Symbolic Representation | - Draw symbols of HAVC components - Draw symbols of HAVC equipment - Draw sectioning symbols of different materials used in mechanical drawing | - Symbols of HVAC components - Symbols of HVAC equipment - Sectioning symbols of various mechanical materials Practical activity - Draw required sectioning symbols of given materials | Theory-1 Hrs. Practical-12 Hrs. Total- 13 Hrs |  |  |

## Draw Projection of Pipes

Objective:

This module covers the knowledge and skills required to this learning module is designed to learn about drawing orthographic projection, draw single-and double-line piping and electrical symbols.

Duration: 30	Hours			                             Theory: 3	Hours				                  Practice: 	27 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Draw orthographic projection. | Trainee will be able to: - Draw orthographic views of a square pipe - Draw orthographic views of a round pipe - Draw isometric view of square pipe - Draw isometric view of round pipe | - Orthographic drawing - Isometric drawing Practical Activity: - Draw different views of pipe | Theory-1 Hrs. Practical-9 Hrs. Total- 10 Hrs. | - T-square - Set square - Compass - Eraser - Pencil - Sharpener - Drawing board | Class Room and drawing hall |
| - Draw single- and double- line piping | Trainee will be able to: - Draw orthographic view of single line piping - Draw orthographic view of double line piping - Draw isometric view of single line piping - Draw isometric view of double line piping | - Isometric drawing - Single line piping - Double line piping Practical Activity: - Draw single line & double line piping system | Theory-1 Hrs. Practical-9 Hrs. Total- 10 Hrs. | - T-square - Set square - Compass - Eraser - Pencil - Sharpener4 - Drawing board | Class Room and drawing hall |
| - Draw electrical symbols | - Draw complete drawing of electrical accessories - Draw working drawing of electrical accessories - Draw the symbolic representation of electrical accessories along with drawing | - Electrical symbols Practical activity - Draw required symbols of required accessories | Theory-1 Hrs. Practical-9 Hrs. Total- 10 Hrs. | - T-square - Set square - Compass - Eraser - Pencil - Sharpener4 - Drawing board |  |

## Draw Building Drawings

Objective:

This module covers the knowledge and skills required to this learning module is designed to draw building accessories drawings and draw building sectioning drawings.

Duration: 50	Hours			                             Theory: 5 Hours				                  Practice: 	45 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Draw building accessories drawings | Trainee will be able to: - Draw accessories of building - Draw complete drawing of a building showing doors, windows and arches in it - Draw symbols of accessories used in building - Show section of a building viewing walls section and doors windows and arches etc. | - Details of door, windows and arches - Symbols used in architectural drawing Practical Activity: - Draw symbols of required accessories used in building | Theory-2.5Hrs. Practical-24 Hrs. Total- 26.5 Hrs. | - T-square - Set square - Compass - Eraser - Pencil - Sharpener - Drawing board | Class Room and drawing hall |
| - Draw building sectioning drawings | Trainee will be able to: - Draw different types of building according to design and use - Draw different views of a building like perspective view and single point view - Draw plan, front and side elevation of a building | - Different design in building - Plan, front and side elevation of a building Practical Activity: - Draw sectioning views of required parts - Draw relevant symbols | Theory-2.5 Hrs. Practical-21 Hrs. Total- 23.5 Hrs. | - T-square - Set square - Compass - Eraser - Pencil - Sharpener4 - Drawing board | Class Room and drawing hall |

## Prepare Computer Added Drawings File (Auto CAD)

Objective:

This module covers the knowledge and skills required to this learning module is designed to learn drawing requirements and Identify key features of CAD software.

Duration: 110	Hours			                            Theory: 8 Hours				                  Practice: 	102 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Confirm drawing requirements and access software and setup for drawing work | Trainee will be able to: - Open software and navigate organizational filing and library system - Identify organizational symbols, codes and standards to be applied in drafting work and how these are accessed and applied - Set up working environment - Review available information relevant to project and work requirements, identify and address further information needs - Identify workflow and procedures for work supervision | - Apply unit setting - Apply limit setting - Apply user coordinate system - Apply workspace setting - Apply object snap setting Practical Activity: - Operate computer confidently & Select type of CAD software - Understand drawing completely | Theory-4 Hrs. Practical-24 Hrs. Total- 28 Hrs. | - PC with accessories | Class Room and Computer Lab |
| - Identify key features of CAD software. | Trainee will be able to: - Select type of CAD software used for detail drafting, their key features and suitability for producing specific drawing outcomes - Select type of CAD software used for design drafting, their key features and suitability for producing specific drawing outcomes use with suitable commands like that arc, circle Poly line Rectangle Spline and text etc. - Identify differences in CAD process to generate 2-D drawings and 3-D models, and reasons for each presentation - Identify differences in CAD process to generate single and multiple view drawings, and reasons for each presentation - Identify CAD software used in the organization and confirm compatibility with other software programs and peripheral equipment - Identify software features for linked specifications, catalogues or materials ordering. | - Angle and lines in Auto CAD - Differentiate between absolute, relative and polar system - DIMSTYLE and MTEXT commands - HATCHING concepts in AutoCAD - Differentiate between CHAMFER and FILLET command - Types of Array - OFFSET, CIRCLE and ROTATE short commands - Zooming options - Tools palettes window - Design center - Scale and paper sizes - Modify dimension style and text size according to paper size - Backup file Practical Activity: - Use right commands - Convert said drawing into CAD | Theory-4 Hrs. Practical-78 Hrs. Total- 82 Hrs. | - PC with accessories | Class Room and Computer Lab |

## Contribute to the Design of Commercial Refrigeration system

Objective: This module covers the knowledge and  skills required to determine optimum system design for a given application, design system and validate system performance.

Duration:  50	Hours			                             Theory: 8	Hours				                  Practice: 	42 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Determine optimum system design for a given application | Trainee will be able to: - Consult appropriate personnel to determine system specifications and obtain final confirmation - Plan design development work to meet scheduled timelines in consultation with others involved on the worksite its main components | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Selecting appropriate system components - Applying relevant standards and regulatory requirements to the design task - Documenting technical information and designs - Interpreting and applying manufacturers’ data, tables and specifications Practical Activity: - Visit the lab and surroundings to the select appropriate HVAC system for specific application and defend the selection | Theory-2 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |
| - Design system | Trainee will be able to: - Design system considering safety, regulatory requirements, relevant standards, system specifications and budgetary constraints - Determine selected equipment required for the systems and locations in accordance with the design specifications and enterprise procedures - Check system design draft for compliance with the design brief, regulatory requirements and environmental standards as per ASHRAE standards | - Selection of appropriate system components - Applying relevant standards and regulatory requirements to the design task - Documenting technical information and designs - Interpreting and applying manufacturers’ data, tables and specifications - Using relevant software tools effectively - Interpreting drawings and specifications - Standards and codes relevant to commercial refrigeration systems Practical Activity: - Design a system to perform required task | Theory-6 Hrs. Practical-24 Hrs. Total- 30Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |
| - Validate system performance | Trainee will be able to: - Establish operating criteria for expected ambient conditions - Determine and validate likely operating characteristics for a given refrigeration load against the design specifications and standards - Adjust the functional design and remap operating characteristics to achieve optimal system performance - Program the control system to meet the operational requirements - Document the designed system and its validation according to enterprise procedures | - Calculation of capacity in heat exchangers - Commercial refrigeration systems feature and components; applications system requirements operating conditions and criteria - Refrigerants, refrigeration cycle, evaporators, condensers, compressors, liquid expansion devices - Record keeping and reporting Practical Activity: - Validate the system to perform required task | Theory-0 Hrs. Practical-10 Hrs. Total- 10Hrs | - HVAC Design Soft wares - HVAC apparatus | workshop |

## Design HVAC System and Select Components

Objective: This module covers the knowledge and  skills required to determine optimum system design for a given application, design system and validate system performance.

Duration:  50	Hours			                             Theory: 20	Hours				                  Practice: 	30 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Prepare to design commercial refrigeration systems | Trainee will be able to: - Determine the extent and nature of the refrigeration system from design specifications. - Consult Work supervisor or customers to determine which functions of the system are to be used and seek the parameter of each and written confirmation. - Plan design development work to meet scheduled timelines in consultation with others involved on the work site | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Standards and codes relevant to commercial refrigeration systems - Using relevant software tools effectively - Design parameters for single-story buildings (e.g., offices, restaurants, hotels, bars) - Building purpose, location, orientation and shape - Zoning and building use - Design features, engineering and selection procedures for direct expansion air conditioning systems: - • Practical Activity: - Collect data and calculate heat load | Theory 6 Hrs. Practical-10 Hrs. Total- 16 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |
| - Design commercial refrigeration systems. | Trainee will be able to: - Apply knowledge of refrigeration and food storage technology, refrigeration system components and piping, performance standards and compliance methods to develop the system design - Incorporate functional and budgetary considerations in the installation design. - Select equipment required for the system in accordance with the design specifications and established requirements. - Document location of components of the system to ensure correct operation of system functions. - Check system design draft for compliance with the design brief and regulatory requirements. - Document system design for submission to appropriate person(s) for approval. - Provide solutions to unplanned situation consistent with organization’s policy | - Split systems and package units - Free blow and ducted fan coil units - Cooling, heat pump and electric heating - Implement Occupational Health and Safety workplace procedures and practices including the use of risk control measures as specified in the performance criteria and range statement - Apply sustainable energy principles and practices as specified in the performance criteria and range statement - Demonstrate an appropriate level of skills enabling employment - Practical Activity - Select HVAC system and also select accessories | Theory-8 Hrs. Practical-10Hrs. Total- 18 Hrs. | • HVAC Design Soft wares | Class Room and workshop |
| - Obtain approval for engineering computer applications design | Trainee will be able to: - Present and explain system design to client representative and/or another relevant person(s). - Negotiate requests for alterations to the design with relevant person(s) within the constraints of organization's policy. - Document final design and approval obtained from appropriate person(s). - Monitor quality of work against personal performance agreement and/or establishment | - Conduct work observing the relevant Anti-Discrimination legislation, regulations, polices and workplace procedures - Select accessories - Practical Activity: - Record keeping and reporting | Theory-6 Hrs. Practical-10 Hrs. Total- 16 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |

## Develop specifications and prepare drawings for HVAC Systems

Objective: This module covers the knowledge and  skills required to prepare to develop specifications and prepare drawings, develop specifications and prepare drawings, and obtain approval for specifications and drawings.

Duration:  30 Hours			                             Theory: 12	Hours				                  Practice: 	18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Prepare to develop specifications and prepare drawings | Trainee will be able to: - Identify, obtain and understand OHS processes and procedures for a given work area - Establish the extent of the project from design brief and/or other relevant documentation and from discussions with concerned expert person(s). - Consult appropriate personnel to ensure the work is coordinated effectively with others involved in the work - Obtain Software tools and equipment as needed for the work in accordance with established procedures | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) Practical Activity: - Collect data and Calculate heat load | Theory-4 Hrs. Practical-6 Hrs. Total- 10 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |
| - Develop specifications and prepare drawings | Trainee will be able to: - Establish and select sources of components and materials needed for the project for their availability, suitability for purpose and cost in accordance with organization policies and procedures. - Develop specifications that include the necessary performance requirements for components and system. - Seek and obtain risk management strategies for the project for incorporating in the specification. - Use appropriate software tools to develop specifications and produce drawing based on standard protocols. - Review project specifications and drawings against all inputs and adjust to rectify any anomalies. - Document Project specifications and drawings in accordance with organization policies and procedures. - Provide solutions to unplanned situation consistent with organization’s policy. - Monitor quality of work against personal performance agreement and/or established organizational or professional standards | - Evidence shall show an understanding of air conditioning drawing, applying safe working practices and relevant Standards, Codes and Regulations to an extent indicated by the following aspects: - Architectural and mechanical drafting conventions encompassing: Fire, hydraulic, electrical layout diagrams, - Sketching of pipework circuits and mechanical services, - Drawing standards and symbols, - Working, detail and assembly drawings, - Ductwork layouts and conventions, - Pipework layouts and conventions, Practical Activity: - Present data on CAD | Theory-4 Hrs. Practical-6 Hrs. Total- 10 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |
| - Obtain approval for specifications and drawings. | Trainee will be able to: - Present project specifications and drawings and discuss with person(s) of higher authority. - Negotiate alterations to the project specifications and drawings resulting from the presentation / discussion with person(s) of higher authority within the constraints of organization’s policy. - Document final project specifications and drawings and obtain approval from appropriate person(s). | - Extent of the drawing work accurately - Determining appropriate types of drawings and their layouts correctly including appropriate technical data parameters in the drawings - Checking and correcting drawings accurately - Filing copies of completed drawings securely - Record keeping and reporting Practical Activity: - Draw drawings by using CAD | Theory-4 Hrs. Practical-6 Hrs. Total- 10Hrs | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |

## Calculate Cooling Load of Commercial Buildings

Objective: This module covers the knowledge and  skills required to extract data from drawings, calculate cooling load, and develop Computer Aided Design (CAD).

Duration:  110 	Hours			                             Theory: 44	Hours				                  Practice: 	66 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Extract Data from Drawings | Trainee will be able to: - Read and interpret construction plans, schematics, and blueprints for new construction projects. understand the building Geometry - Finalize and Freeze indoor Design Condition with the consent of Client. Consult relevant International ASHRAE Standards - Assess and analyze the environmental and structural information of the building | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Understand the Significance of Reduction of heat gain from Glass and other Building Materials. - HVAC CAD design Practical Activity: - Visit the lab and surroundings to the select appropriate HVAC system for specific application and defend the selection | Theory-12 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |
| - Calculate Cooling Load | Trainee will be able to: - Select and operate HVAC load Calculation Software or Manually - Create Spaces in Software - Calculate ventilation requirements based on the types of systems needed. - Identify or Determine the Function/Activity of space for occupants Heat Dissemination. - Determine the total cooling load of the building’s air-conditioning system - Calculate the heat generation due to conduction from peripheral structures of the building (including external and internal walls, roof and windows) - Calculate the heat generation due to penetration of sunlight through windows - Calculate the heat generation due to indoor heat sources (including equipment, lighting and human bodies) - Calculate the cooling load caused by infiltration and ventilation - Determine the total cooling load of the building’s air-conditioning system - Estimate and calculate the total cooling load of the building’s air-conditioning system on computer software | - Impact of different types of refrigeration systems on energy saving. - Working principles and selection criteria for different types of air-conditioning and refrigeration energy-saving equipment. - Various types of energy-saving methods for air-conditioning systems, including: - Energy-saving methods for air-handling units - Energy-saving methods for air-conditioning water systems - Energy-saving methods for variable air-volume (VAV) air-conditioning systems - Energy-saving methods for heat recovery of air-conditioning system - Impact of Testing, adjusting and Balancing (TAB) for HVAC System. - Record keeping and reporting Practical Activity: | Theory-6 Hrs. Practical-24 Hrs. Total- 30Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |
| - Develop Computer Aided Design (CAD) | Trainee will be able to: - Operate AutoCAD or any other CAD software (AutoCAD and Intel CAD). - Make/Draft Drawing in CAD. Understand the techniques and methods of using computer to draw complicated mechanical engineering drawings - Set the CAD layers and Annotation. | - Make/Draft Drawing in CAD. Understand the techniques and methods of using computer to draw complicated mechanical engineering drawings. Practical Activity: | Theory-30 Hrs. Practical-42 Hrs. Total- 72Hrs | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |

## Design and Select Fans for HVAC system

Objective: This module covers the knowledge and  skills required to select fan, select air-handling equipment

Duration:  30 	Hours			                             Theory: 12	Hours				                  Practice: 	18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Select Fan | Trainee will be able to: - Identify the Fan Arrangements (SMACNA) Fan Arrangement 1 to 12 - Read and Interpret Fan Performance and Fan Curves - Find the Fan specifications from Equipment Schedule/Design Document | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Different types of electric motors - Significance of Fan Laws - Basic Knowledge of Terminology such as Air flow, pressure head, power, efficiency ESP, TSP, VP etc. - Define working principles of different types of electric motors Practical Activity: - Use SMACNA standards And also obtain specifications of air flow & HVAC system | Theory-6 Hrs. Practical-9 Hrs. Total- 15 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |
| - Select Air-handling equipment | Trainee will be able to: - Determine the type and arrangement of air-handling unit according to uses and building conditions - Determine the type and arrangement of fan coil unit, and its intake of fresh air according to uses and building conditions - Perform audit checks for the surface air cooler of the selected air-conditioning plant to ensure that the unit plant the design requirements - Select suitable air filters according to requirements - Select suitable air purifiers according to requirements | - Basic Knowledge of Terminology such as Air flow, pressure head, power, efficiency ESP, TSP, VP etc. - Working principles and construction of centrifugal fans and recognize different Fan Types. - Define pressure and temperature laws - Define temperature and its units - Use of Ohm meter, Voltmeter and Ampere meter - Record keeping and reporting Practical Activity: - Select capacity & type of fan according to specification And also select accessories for fan arrangement | Theory-6 Hrs. Practical-9 Hrs. Total- 15 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |

## Design Piping for Commercial HVAC System

Objective: This module covers the knowledge and  skills required to design hydronic system, and design pipe network.

Duration:  40 	Hours			                             Theory: 16	Hours				                  Practice: 	24 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Design Hydronic System | Trainee will be able to: - Understand the Basics of Hydronic System - Differentiate the Types of Hydronic Systems (Open Loop and Close Loop) - Identify the Components of Hydronic System such as Pumps, Expansion/Compression Tank, Air Separator, De-Coupler, Chemical Feeding Pumps, Cooling Towers, AHU's, FCU's, Chillers, Radiators, Hot Water Generator, Control Valves etc. | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Basics of Hydronic System - All types and arrangements of the "Hydronic Piping Circuits Arrangement /Types" - Different types of electric motors - Working principles of different types of electric motors - Ohm meter, Voltmeter and Ampere meter - Record keeping and reporting Practical Activity: - Design Hydronic system | Theory-8 Hrs. Practical-12 Hrs. Total- 20 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |
| - Design system Design Pipe Network | Trainee will be able to: - Understand the difference and working principle of open circuit and close circuit for design purpose. - Calculate the Piping system head. - Calculate Total flow rate of piping system. - Determine the pipe size for required Flow rate and Pressure Loss using pipe sizing chart/software. - Make best route for Hydronic Piping with co-ordination of other discipline | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Basics of Hydronic System - All types and arrangements of the "Hydronic Piping Circuits Arrangement /Types" - Different types of electric motors - Working principles of different types of electric motors - Ohm meter, Voltmeter and Ampere meter - Record keeping and reporting Practical Activity: - Calculate water flow rate | Theory-8 Hrs. Practical-12 Hrs. Total- 20 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |

## Design & Select Pumps for HVAC system

Objective: This module covers the knowledge and  skills required to understand pumps basics and Select Size and type of Pump

Duration:  40 	Hours			                             Theory: 16	Hours				                  Practice: 	24 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Understand Pumps Basics | Trainee will be able to: - Identify the Pump Types used for Hydronic System (End-Suction Pumps, Split Case Pumps, and In-line Pumps), identify the parts of Pumps. - Select suitable centrifugal water pumps with understanding of performance curves of pumps - Determine the operating point of centrifugal water pumps with reference to the pump performance curves and piping performance curves | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Working Principle of Centrifugal Pumps. - Characteristics of centrifugal water pumps, including: Definition of flow Rate, lift, power, efficiency, rotational speed, Duty Point, BHP, NPSH, Required Horsepower, BEP Practical Activity: - Select accessories to connect pumps | Theory-8 Hrs. Practical-12 Hrs. Total- 20 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |
| - Select Size and type of Pump | Trainee will be able to: - Read and Interpret Pump Laws, Pump Performance Curves, System Curve - Calculate the Head Loss of Hydronic System. - Construct or Draw System curve before pump selection, furthermore, able to differentiate System Curve and Pump performance Curve. | - Working principles and characteristics of primary pump and secondary pump chilled water systems - Difference in Static Balancing and Dynamic Balancing of Pumps with Motors on Mount. - Ohm meter, Voltmeter and Ampere meter - Record keeping and reporting Practical Activity: - Design & Select pump sizes | Theory-8 Hrs. Practical-12 Hrs. Total- 20 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |

## Design Duct system for Commercial HVAC system

Objective: This module covers the knowledge and  skills required to develop duct design (Air Distribution Network), and develop air-distribution devices.

Duration:  45 Hours			                             Theory: 18	Hours				                  Practice: 	27 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Develop Duct Design (Air Distribution Network) | Trainee will be able to: - Identify different types of Ducts (Round, Rectangular, Spiral, Oval etc.) - Make Duct route considering building geometry and Coordinating with other disciplines. - Determine the Size of Air duct as per Space Air Distribution (determined by Cooling/Heating load Calculations). - Calculate Air Velocity and Cross-sectional Area of the Duct - Calculate Total "Air flow Rate" and "Pressure drop" for Fan Sizing. - Study Duct Standards such as SMACNA or Equivalent. | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Working principles of different types of electric motors - Pressure, temperature and its units - Significance of Fan Laws - Basic Knowledge of Terminology such as Air flow, pressure head, power, efficiency ESP, TSP, VP etc. - Working principles and construction of centrifugal fans, and recognize different Fan Types Practical Activity: - Use SMACNA standards of duct designing - Obtain specifications of air flow & HVAC system - Calculate Total Air Flow Rate and Pressure drop | Theory-8 Hrs. Practical-12 Hrs. Total- 20 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |
| - Develop Air-Distribution Devices | Trainee will be able to: - Interpret the selection catalogues of Air Distribution Devices. - Determine the type of air distribution and the air flow pattern according to the design and requirements of the building - Select the appropriate "Air-Distribution Devices" such as Diffusers, Grills, Register and VCDs. | - Duct material and its types according to construction - Types of duct insulation - Record keeping and reporting Practical Activity: - Select size & type of duct according to specification - Select air distribution accessories for selected duct system | Theory-8 Hrs. Practical-12 Hrs. Total- 12 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |

## Attenuate Noise and Vibration Encounter in HVAC Applications

Objective: This module covers the knowledge and  skills required to prepare to determine noise and vibration encountered in HVAC applications, determine noise and vibration encountered in HVAC applications.

Duration:  30 Hours			                             Theory: 6	Hours				                  Practice: 	24 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Prepare to determine noise and vibration encountered in HVAC applications | Trainee will be able to: - Obtain the nature of the problem from documentation or from work supervisor to establish the scope of work to be undertaken. - Establish procedures, sources of equipment and products that may be required for the work accordingly - Carry out tools, equipment and testing devices needed to the work are obtained and check for correct operation and safety | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Noise and vibration measurements - Record keeping and reporting Practical Activity: - Suggestion regarding unexpected situations safely | Theory-2 Hrs. Practical-6 Hrs. Total- 8 Hrs. | - Personal Computer - Charts of Noise Criteria Standards | Class Room and workshop |
| - Determine noise and vibration encountered in HVAC applications | Trainee will be able to: - Select methods to determine noise and vibration measurements encountered in HVAC/R application - Deal unexpected situations safely with the approval of an authorized person. - Take measures without damage to apparatus, circuits, the surrounding environment or services and using sustainable energy practices with the minimum waste and rework. | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Noise and vibration measurements - Record keeping and reporting Practical Activity: - Select alternative approach to determine Noise & Vibration | Theory-2 Hrs. Practical-9 Hrs. Total- 11 Hrs. | - Personal Computer - Charts of Noise Criteria Standards | Class Room and workshop |
| - Document noise and vibration measurements in HVAC applications. | Trainee will be able to: - Determine noise and vibration to justify alternative approach - Document the work completion and an appropriate person or persons notified in accordance with established procedures. | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Noise and vibration measurements - Record keeping and reporting Practical Activity: - Select alternative approach to determine Noise & Vibration | Theory-2 Hrs. Practical-9 Hrs. Total- 11 Hrs | - Personal Computer - Charts of Noise Criteria Standards | Class Room and workshop |

## Perform Water Treatment in HVAC System

Objective: This module cover the knowledge and skills required to Prepare the water treatment process for operation, Operate and monitor the water treatment process , Analyze and respond to abnormal performance, Hand over water treatment system, Shut down the water treatment system

Duration: 40 Hours						Theory: 10 Hours				Practice: 30 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1.Prepare the water treatment process for operation | Trainee will be able to: - Confirm chemicals and test equipment readiness for use - Confirm services are available and ready for operation - Select, fit and use personal protective equipment according to workplace safety procedures - Conduct pre-operational checks according to operating procedures - Calibrate instrumentation and test equipment according to operating specifications - Identify and report health and safety hazards and maintenance requirements according to workplace safety procedures | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - Water treatment functions - Monitoring, testing and adjustment of water treatment - PH value of the water - Cleaning of water systems Practical Activity: - Collect samples of water | Theory- 02Hrs Practical-06Hrs Total-08 Hrs | - Personal Protective Equipment - PH meter - Water cleaning system | Classroom and Lab |
| LU2. Operate and monitor the water treatment process | Trainee will be able to: - Start the water treatment system according to operating procedures - Confirm operating condition is maintained within operating requirements - Monitor, test and adjust wastewater quality according to operating procedures - Operate first flush systems during rainfall events - Ensure the work area is maintained to workplace cleaning standards | - Water treatment functions - Monitoring, testing and adjustment of water treatment - PH value of the water - Cleaning of water systems Practical Activity: - Perform water treatment with different methods | Theory- 02Hrs Practical-06Hrs Total-08 Hrs | - Personal Protective Equipment - PH meter - Water cleaning system | Lab |
| LU3 Analyze and respond to abnormal performance | Trainee will be able to: - Analyze water condition and plant operating conditions according to workplace procedures and manufacturer s guidelines - Take corrective action in response to hazards, out-of-specification test results and / plant performance - Implement emergency procedures according to workplace safety procedures | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - Water treatment functions - Monitoring, testing and adjustment of water treatment | Theory- 02Hrs Practical-06Hrs Total-08 Hrs | - Personal Protective Equipment - Basic tool Kit - PH meter - Water cleaning system | Lab |
| LU4. Hand over water treatment system | Trainee will be able to: - Maintain workplace records according to workplace procedures - Carry out handover according to workplace procedures Ensure operators are aware of system status and related equipment at completion of handover | - Monitoring, testing and adjustment of water treatment - PH value of the water - Corrosion and its eradication process - Record keeping and reporting Practical Activity: - Perform different test of water | Theory- 02Hrs Practical-06Hrs Total-08 Hrs | - Basic tool Kit | Lab |
| LU5..Shut down the water treatment system | Trainee will be able to: - Safely shut down the system according to operating procedures - Prepare the system for storage in shutdown mode according to operating procedures - Identify and report operational maintenance requirements according to workplace procedures | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) Practical Activity: Prepare the system for storage in shutdown mode according to operating procedures | Theory- 02Hrs Practical-06Hrs Total-08 Hrs | - Basic tool Kit - Water cleaning system | Lab |

## Analyse the operation of HVAC Air and Hydronic system

Objective: This module cover the knowledge and skills required to  Prepare to analyze the operation of HVAC air and hydronic systems, Analyze the operation of HVAC air and hydronic systems, Document and develop report on the results of the operation of HVAC/R systems analysis and actions taken.

Duration: 40 Hours					Theory: 07 Hours					Practice: 33Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare to analyze the operation of HVAC air and hydronic systems | - Identify, obtain and understand OHS processes and procedures for a given work area - Follow established OHS risk control measures and procedures in preparation for the work. - Determine the extent of operating analysis from performance specifications and situation reports and in consultations with relevant persons Plan activities to meet scheduled timelines in consultation with others involved in the work - Plan effective strategies to ensure solution development and carry out implementation efficiently. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - Basics of Hydronic System - All types and arrangements of the "Hydronic Piping Circuits Arrangement /Types" - Effective strategies to ensure solution development Practical Activity: - Operate HVAC air and hydronic systems | Theory- 03Hrs Practical- 11Hrs Total-14 Hrs | - Personal Protective Equipment - Personal Computer | Classroom and Lab |
| LU2. Analyze the operation of HVAC air and hydronic systems | - Follow OHS risk control measures and procedures for carrying out the work - Apply knowledge of HVAC air and hydronic systems operating parameters to analytical solutions of refrigeration and air conditioning systems - Obtain parameters, specifications and performance requirements in relation to HVAC air and hydronic systems in accordance with established procedures - Carry out approaches to analyzing operating parameters to provide the most effective solution. Deal with unplanned/ unforeseen events safely and effectively consistent with regulatory requirements and enterprise policy - Monitor quality of work against personal performance agreement and/or established organizational or professional standards | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - Basics of Hydronic System - All types and arrangements of the "Hydronic Piping Circuits Arrangement /Types" - Effective strategies to ensure solution development - Carry out implementation efficiently regarding hydronic system Practical Activity: Make the hydronic piping circuits | Theory- 02Hrs Practical-11 Hrs Total- 13Hrs | - Personal Computer | Lab |
| LU3. Document and develop report on the results of the operation of HVAC/R systems analysis and actions taken. | Trainee will be able to: - Evaluate results of system operating analysis to determine whether performance requirements are being met or otherwise. Document analysis including details of all findings, calculations and assumptions. Report analysis to concerned expert personnel to establish appropriate action to be taken based on findings. - Document justification for findings and any actions to be undertaken in relation to the equipment for inclusion in work/project or development records in accordance with professional standards. | - Effective strategies to ensure solution development - Carry out implementation efficiently regarding hydronic system - Evaluation parameters of hydronic system - Record keeping and reporting Practical Activity: Analyze obtained data and make report | Theory-02 Hrs Practical- 11Hrs Total- 13Hrs | - Personal Protective Equipment - Personal Computer | Lab |

## Calculate Quantity of Heat Transfer for Different Applications

Objective: This module covers the knowledge and  skills required to calculate temperature change, select appropriate heating and cooling mechanism, determine heating required to suit process conditions, and conduct energy balance over process components

Duration:  20 	Hours			                             Theory: 5	Hours				                  Practice: 	15 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Calculate temperature change | Trainee will be able to: - Calculate temperature change caused by heating/cooling pipes & ducts - Calculate change in heat content caused by different heat transferred factors - Calculate temperature change caused by insulation | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Pressure, Temperature and its units Practical Activity: - Calculate the heat transfer by thermometers | Theory-1 Hrs. Practical-3 Hrs. Total- 4 Hrs. | - Personal Protective Equipment - Basic tool Kit | Class Room and workshop |
| - Select appropriate heating and cooling mechanism | Trainee will be able to: - Compare rates of heat transfer/overall heat transfer coefficients for major methods of heating and cooling - Determine appropriate methods of varying/controlling rates of heat transfer in HVAC systems - Calculate heat transfer rates under a range of designed conditions | - Heat transfer and methods of heat transfer - Load calculations Practical Activity: - Calculate quantity of transferred heat by all modes | Theory-2 Hrs. Practical-3 Hrs. Total- 5 Hrs. | - Basic tool Kit - Digital Air Flow / Velocity Meter | Class Room and workshop |
| - Determine heating required to suit process conditions | Trainee will be able to: - Determine heating requirements to obtain correct viscosity for processing - Select appropriate heat transfer mechanism(s) to achieve desired conditions - Select appropriate mechanism to control the flow of heat transfer | - Heat transfer and methods of heat transfer - Effects of temperature changes - Interpret the relation between pressure and temperature Practical Activity: | Theory-1 Hrs. Practical-3 Hrs. Total- 4 Hrs. | - Digital Optical Tachometer | Class Room and workshop |
| - Conduct energy balance over process components | Trainee will be able to: - Determine overall heating load for process components - Determine overall cooling load for process components - Determine the adequacy (or otherwise) of the process/plant heating/cooling system to cope with this | - Record keeping and reporting Practical Activity: Calculate heat transfer by using Energy method equation | Theory-1 Hrs. Practical-6Hrs. Total- 7 Hrs. | - Electronic Leak Detector | Class Room and workshop |

## Plot Refrigeration Cycle on PH Chart

Objective: This module covers the knowledge and  skills required to calculate refrigeration process of actual refrigeration cycle  and calculate effects of change in condensing temperature on cycle efficiency.

Duration:  20 Hours			                             Theory: 5	Hours				                  Practice: 	15 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Calculate refrigeration process of actual refrigeration cycle | Trainee will be able to: - Draw refrigeration cycle on PH chart. - Calculate refrigerating effect. - Calculate coefficient of performance. - Calculate the mass flow rate. - Calculate the system capacity. - Calculate the heat of compression | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - PH chart - Read and interpret PH chart Practical Activity: - Draw relevant lines of refrigeration cycle | Theory-3 Hrs. Practical-6 Hrs. Total- 9 Hrs. | - T-square - Drafting machine - French Curves - Rulers - Compass | Class Room and workshop |
| - Calculate effects of change in condensing temperature on cycle efficiency | Trainee will be able to: - Draw refrigeration cycle on PH chart. - Calculate refrigerating effect. - Calculate coefficient of performance. - Calculate the mass flow rate. - Calculate the system capacity. - Calculate the heat of compression. - Compare such properties with theoretical refrigeration cycle | - Draw refrigeration cycle on PH chart - Calculate system capacity through PH chart - Coefficient of performance - Refrigerating effect and system capacity - Heat of compression and mass flow rate - Record keeping and reporting Practical Activity: - Calculate enthalpies - Calculate Refrigerating effect | Theory-2 Hrs. Practical-9 Hrs. Total- 11 Hrs. | - T-square - Drafting machine - French Curves - Rulers - Compass | Class Room and workshop |

## Calculate Different Process on PH Chart

Objective: This module covers the knowledge and  skills required to identify and interpret PH chart, draw refrigeration cycle of PH chart, and analyze the cycle performance.

Duration:  40 Hours			                             Theory: 7	Hours				                  Practice: 	33 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Identify and interpret PH chart | Trainee will be able to: - Identify the PH chart. - Identify the line & curves of ph. chart with their readings. - Differentiate phases of ph. chart. - Draw the different refrigeration process on ph. chart. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - PH chart - Read and interpret PH chart Practical Activity: - Draw relevant lines of refrigeration cycle - Draw condensing process for specified refrigerant. | Theory-2 Hrs. Practical-9 Hrs. Total- 11 Hrs. | - T-square - Drafting machine - French Curves - Rulers - Compass | Class Room and workshop |
| - Draw refrigeration cycle of PH chart. | Trainee will be able to: - Draw condensing process for specified refrigerant. - Draw expansion process for specified refrigerant. - Draw vaporization process for specified refrigerant. - Draw compression process for specified refrigerant. - Complete the diagram according to given pressure & temperature. - Calculate the properties of air after observing enthalpies at different point | - Draw refrigeration cycle on PH chart Practical Activity: - Draw condensing process for specified refrigerant. - Draw expansion process for specified refrigerant. | Theory-3 Hrs. Practical-15 Hrs. Total- 18 Hrs. | - T-square - Drafting machine - French Curves - Rulers - Compass | Class Room and workshop |
| - Analyze the cycle performance | Trainee will be able to: - Calculate refrigerating effect - Calculate coefficient of performance - Calculate the mass flow rate of refrigerant in the system. - Calculate the compressor capacity | - Calculate system capacity through PH chart - Coefficient of performance - Refrigerating effect and system capacity - Heat of compression and mass flow rate - Record keeping and reporting Practical Activity: - Calculate enthalpies - Calculate Refrigerating effect | Theory-02 Hrs. Practical-9 Hrs. Total- 11 Hrs. | - PH Chart - T-square - Drafting machine - French Curves - Rulers - Compass | Class Room and workshop |

## Calculate the Quantity of Gasses in a flue gas Sample

Objective: This module covers the knowledge and  skills required to identify and use flue gases and estimate flue gases quantity

Duration:  20 	Hours			                             Theory: 5	Hours				                  Practice: 	15 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Identify and use flue gases | Trainee will be able to: - Identify the properties of gases. - Identify the properties of flue gases. - Use air and gases. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) Practical Activity: - Use oars apparatus - Calculate composition of gases in ores apparatus | Theory-3 Hrs. Practical-9 Hrs. Total- 12 Hrs. | - Personal Computer - HVAC Design Soft wares | Class Room and workshop |
| - Estimate flue gases quantity | Trainee will be able to: - Identify and operate Ores apparatus. - Identify the percentage of different gasses in flue gas. - Convert the content of the different element of mol. - Calculate the air according to the stoichiometric reaction. - Calculation of excess air. - Convert flue gases to mol. | - Flue gasses and flue gasses calculations - Identification and use of Ores apparatus - Stoichiometric reaction - Elements of mol and conversion of flue gases into mol Record keeping and reporting Practical Activity: - Calculate quantity of Excess air | Theory-2 Hrs. Practical-6 Hrs. Total- 8 Hrs. | • HVAC Design Soft wares - Personal computer | Class Room and workshop |

## Make Circuits Using Electronic Components.

Objective: After the completion of this module, the Trainee will be able to Make rectifier circuit, Make common emitter (CE) amplifier circuit, Make DC motor speed control circuit, Make AC power control circuit, Make time delay circuit

Duration:  20 Hours			Theory:  05 Hours			Practice:  15 Hours          	        Credit Hours:  2

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Make rectifier circuit. | Trainee will be able to: - Connect two diodes; make an "L" of their two ends marked with the white bands (cathodes). - Connect the remaining two diodes, this time with their ends having no bands (anodes) - Connect both sets of diodes according to the circuit diagram. - Verify the results that the circuit is converting complete cycle of AC supply into DC supply | - N Type and P-Type material. - PN junction - Forward biasing - Reverse biasing - Rectification Practical Activity: Construct full wave bridge rectifier and draw its input and output wave shape using Oscilloscope. | Theory- 01 Hrs Practical- 03 Hrs Total- 04 Hrs | - Diodes - Transformer - Breadboard - Connecting leads | Classroom & Lab |
| LU2. Make common emitter (CE) amplifier circuit | Trainee will be able to: - Connect the transistors according to circuit diagram. - Connect amplifier circuit to the power supply - Measure the input voltage (f=1 kHz). - Verify the output is 4Vpp at 1 kHz as compare to input. | - Types of transistor. - Biasing of transistor. - Amplification - Phase reversal. - Amplification Practical Activity: Construct common emitter amplifier using transistor and calculate its gain. | Theory- 01 Hrs Practical- 03 Hrs Total- 04 Hrs | - Transistor - Power supply - Signal generator - Breadboard - Oscilloscope - Connecting leads. | Classroom & Lab |
| LU3. Make DC motor speed control circuit | Trainee will be able to: - Connect the silicon-controlled rectifier (SCR) according to circuit diagram - Connect the dc motor with controlling circuit. - Connect the circuit to power supply. - Check and verify the circuit that speed of dc motor controlled properly | - Introduction to SCR - Effect of triggering - Difference between rectification and controlled rectification - Speed control parameters of DC motor. - Speed control methods of DC motor. Practical Activity: Implement speed control circuit to control the speed of DC motor. Change the triggering angle and note the effect on speed of DC motor | Theory- 01 Hrs Practical- 03 Hrs Total- 04 Hrs | - DC motor - SCR - Diodes - DC supply - Variable resistors - Connecting leads | Classroom & Lab |
| LU4. Make AC power control circuit. | Trainee will be able to: - Connect the diac & triac according to circuit diagram. - Connect circuit to power source (AC supply). - Trigger the circuit at different positions of AC wave form - Check and verify the results that circuit is controlling AC power supply properly. | - Introduction to DIAC - Introduction to TRIAC - Effect of triggering Practical Activity: Implement Fan dimmer circuit to control the speed of fan. Change the triggering angle and note the effect on speed of Fan | Theory- 01 Hrs Practical- 03 Hrs Total- 04 Hrs | - DIAC - TRIAC - Capacitor - Resistor - Fan - Connecting lead. | Classroom & Lab |
| LU5. Make time delay circuit. | Trainee will be able to: - Connect the uni junction transistor (UJT) and SCR according to circuit diagram. - Connect the circuit to power supply and adjust the power supply to 12V dc. - Trigger the SCR through UJT to operational the circuit. - Verify that by increase in resistance should change the time delay period longer. - Verify that by decrease in resistance should change the time delay period shorter | - Construction of UJT - RC time constant - Switching behavior of UJT - Inter base resistance - SCR Practical Activity: Construct UJT relaxation oscillator, Change the resistance and note the effect on its output. | Theory- 01 Hrs Practical- 03 Hrs Total- 04 Hrs | - UJT - SCR - Resistors - Rheostat - Capacitor - Connecting leads - DC supply | Classroom & Lab |

## Make Temperature Control & Sensing Devices

Objective: After the completion of this module, the Trainee will be able to Make a temperature control device, Make a temperature sensing device

Duration:  20 Hours			Theory:  04 Hours			Practice:  16 Hours          	        Credit Hours: 02

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Make a temperature control device | Trainee will be able to: - Strip back the outer insulation of wires. - Bend the wire to make a contact point and weld them - Measure & verify the output of thermocouple at open circuit that readings must be above 17 to 18 mill volts. - Measure & verify the output of thermocouple at close circuit that readings must be up to 8 to 9 mill volts | - See Back effect - Construction of Thermocouple - Connecting leads - Galvanometer Practical Activity: Construct a thermocouple, apply heat at hot-junction and measure the output voltage at its cold junction. | Theory- 02 Hrs Practical- 08 Hrs Total- 10 Hrs | - Thermocouple - Heating source - Digital voltmeter. | Classroom & Lab |
| LU2. Make a temperature sensing device | Trainee will be able to: - Connect the thermistor according to circuit diagram. - Connect the power supply to op- amp and apply 15 V and apply +5 V to the sensor. - Measure the output voltage using a digital voltmeter (DVM) - Checked and verified resistance verses temperature characteristics. - Verify the thermistor sense cold water, tap water, and hot water combinations to obtain a range between 15 to 60 centigrade | - Introduction to thermistor - Working of thermistor - Operational amplifier Practical Activity: Construct fire alarm circuit, apply heat on sensor and note the effect on buzzer. | Theory- 02 Hrs Practical- 08 Hrs Total- 10 Hrs | - Thermistor - Operational amplifier - Heating source - Connecting leads - Voltmeter | Classroom & Lab |

## Connect the Accessories in Control Circuits

Objective: After the completion of this module, the Trainee will be able to Connect electronic relays, timers in circuits, Connect electro-pneumatic & mechanical controller

Duration:  40 Hours			Theory:  08 Hours			Practice:  32 Hours          	        Credit Hours:  04

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Connect electronic relays, timers in circuits. | Trainee will be able to: - Connect dc time delay relay according to circuit diagram. - Check & verify its time delay function. - Connect AC resistance sensitive relay according to circuit diagram. - Check & verify its resistance sensitivity function. - Connect heat sensitive relay according to circuit diagram. - Check & verify heat sensitivity function. - Connect sequence timer according to circuit diagram. - Check & verify its function | - Introduction to timer - Introduction to Relay - Time delay action - Sequential circuit Practical Activity: Implement electronic relay with time delay circuit | Theory- 04 Hrs Practical- 16 Hrs Total- 20 Hrs | - Time delay circuit - Sequential timer - Heat sensitive relay. - Connecting leads | Classroom & Lab |
| LU2. Connect electro-pneumatic & mechanical controller | Trainee will be able to: - Connect electro-pneumatic controller according to circuit diagram. - Check & verify its pneumatic function. - Connect electro-mechanical controller according to circuit diagram. - Check & verify its function | - Introduction to pneumatics - Introduction to electro pneumatics - Transformer - Solenoid valve - sensors Practical Activity: Construct a Single solenoid valve with a spring return (reset) | Theory- 04 Hrs Practical- 16 Hrs Total- 20 Hrs | - DC power supply - Switches - Relays - Solenoid valves - Sensors - Connecting leads | Classroom & Lab |

## Make Opto-Coupler Devices

Objective: After the completion of this module, the Trainee will be able to Make illumination Control, Make a counter, Make a pin-hole detector, Make flame failure Control

Duration:  20 Hours			Theory:  04 Hours			Practice:  16 Hours          	        Credit Hours:  02

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Make illumination Control | Trainee will be able to: - Draw the Circuit of illumination control. - Select the components for illumination control. - Place the components for illumination control on bread board. - Fall the light on sensor and verify the functionality of circuit. | - Purpose of illumination control. - Application of illumination control. Practical Activity: Construct illumination Control circuit and verify its functionality. | Theory- 01 Hrs Practical- 04 Hrs Total- 05 Hrs | - IC LM358 – 1 - Resistor 10KΩ – 1 - Potentiometer 10KΩ – 1 - 5V Relay Module – 1 - Small LED Strip - 9V Battery - LDR – 1 - Connecting Wires - Breadboard | Classroom & Lab |
| LU2. Make a counter | Trainee will be able to: - Connect increment and reset to an OR gate. - Connect the increment button to each AND gate. - Connect AND gate each output to one S input on each RS flip-flop - Connect the reset button to every R input on each RS flip-flop. - Connect the single OR gate output to the clock input on each RS flip-flop - Connect each or gate’s output to one of the numerical display inputs. - Connect RS flip-flop’s Q output, to one input of the first XOR gate, and one input of the first AND gate. - Connect RS flip-flops output to an input of the previous XOR gate, an input of the next XOR gate, and the input of the next AND gate Connect - Connect RS flip-flop to the last XOR gate, and one to each of the OR gates | - Flip flop - Toggling function of JK or T flipflop - Oscillation. - Preset and rest function. Practical Activity: Construct 4bit asynchronous counter, apply the pulses to counter and note the changes of output code of counter. | Theory- 01 Hrs Practical- 04 Hrs Total- 05 Hrs | - JK flip flop. - Square wave generator - Connecting lead. - Seven segment display - Seven segment decoder. | Classroom & Lab |
| LU3. Make a pin-hole detector | Trainee will be able to: - Connect the components according to circuit diagram. - Connect the circuit low voltage power supply. - Check automatic sensitivity calibration and voltage - Measure insulated coatings less than 500 µm or 20 milli meter on conductive substrates | - Working principle of pinhole detector. - Applications of pinhole detector. Practical Activity: Check cracks and damaged areas on non-conductive coatings on conductive substrates using pinhole detector. | Theory- 01 Hrs Practical- 04 Hrs Total- 05 Hrs | - Pinhole detector - Material under test. - Power supply. | Classroom & Lab |
| LU4. Make flame failure Control | Trainee will be able to: - Connect flame failure detector according to circuit diagram - Install the detector to burner. - Connect the device to power supply. - Verify that detector stopping flow of gas to the burner | - Knowledge about flame failure control. - Thermocouple - Application of Flame failure control. Practical Activity: Verify the function of flame failure Control | Theory- 01 Hrs Practical- 04 Hrs Total- 05 Hrs |  | Classroom & Lab |

## Install Commercial Refrigeration System.

Objective: After the completion of this competency standard, the Trainee will be able to install different types and sizes of walk in coolers / freezers / ice making machines / electric water coolers / chilled water tanks at workplace in accordance with the organization’s / clients’ guidelines. This unit covers the knowledge regarding safety rules, personal protective equipment, and international standards for installing Refrigeration units to provide you the basis for your work.

Duration:  30Hours			Theory: 3 Hours			Practice: 27 Hours          	 Credit Hours: 3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Install Walk in Cooler / Freezer | Trainee will be able to: - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Select tools, equipment and related accessories according to job requirements - Prepare insulated room for preserving the food on lowest temperature as per drawing and requirements - Prepare steel structure for installation of evaporator assembly and condensing unit following manufacturer’s specifications - Prepare the place and leveled it, to fix the evaporator and condensing unit firmly according to manufacturer’s specifications - Layout piping and control wiring from indoor to outdoor unit according to instructional manual - Perform leak test, evacuation and charge the refrigerant according to unit specifications and standards, before commissioning - Connect the electric supply and check the performance | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ohm meter, Voltmeter and Ampere meter use - Refrigeration and its types - Commercial refrigeration - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Compressors and functions of compressors - Air purge valves, fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Read and understand drawings - Make foundations and hangers - Install components of refrigeration system - Make water drain connections - Install anti freezing/defrosting and water level protection system | Theory-1Hrs Practical-9Hrs Total-10Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Classroom Training Workshop Lab/ Field Visit |
| LU2. Install Ice Making Machine | Trainee will be able to: - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Select tools, equipment and related accessories according to job requirements - Fix the machine on potable water supply by following manufacturer’s specifications - Measure the clearance on each side to be sure it meets the standards set by the manufacturer - Make water drain connections in order to empty purged and melt water as per manual instructions and client requirements - Install shut of valve on water supply near the machine according to unit specifications - Make electric supply, switched on and check performance according to machine specification by using specific instruments | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ohm meter, Voltmeter and Ampere meter use - Refrigeration and its types - Commercial refrigeration - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Compressors and functions of compressors - Air purge valves, fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Read and understand drawings - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install anti freezing/defrosting and water level protection system | Theory-1Hrs Practical-9Hrs Total-10Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Class Room Training Workshop |
| LU3. Install Electric Water Cooler / Chilled Water Tank | - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Select tools, equipment and related accessories according to job requirements - Fix the cooler / tank on potable water supply by following manufacturer’s specifications and client requirements - Measure the clearance on each side to be sure it meets the standards set by the manufacturer - Make water drain connections adjacent to the water supply as per manual instructions / location - Fix minimum water level protection &interlocking with refrigeration unit to prevent empty freezing - Make power supply as per manual instructions. - Operate and check performance | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ohm meter, Voltmeter and Ampere meter use - Refrigeration and its types - Commercial refrigeration - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Compressors and functions of compressors - Air purge valves, fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Read and understand drawings - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install anti freezing/defrosting and water level protection system | Theory-1Hrs Practical-9Hrs Total-10Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Classroom Lab/ Field Visit |

## Install, Maintain & Repair Industrial Refrigeration System.

Objective: After the completion of this competency standard, the Trainee will be able to install, maintain and repair different types and sizes of cold rooms/ freezer rooms/ ice plants using specified tools & test instruments and material and referring to manufacturer’s specifications while ensuring safe working conditions and the safe use of tools, equipment and material.

Duration: 30 Hours			Theory:  3Hours			Practice: 27 Hours          	 Credit Hours:  3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify the selected design of industrial refrigeration system. | Trainee will be able to: - Identify location as per the design. - Select system specifications, check to ensure matching with selected design of the unit. - Prepare a list of equipment/items and material required for the job. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration, And Air Conditioning Engineers (ASHRAE) - Different types of electric motors - Working principles of different types of electric motors - Refrigeration and its types - Commercial refrigeration - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Compressors and functions of compressors - Air purge valves, fans and its types - Vibration and abnormal noises of electrical devices and machinery Record keeping and reporting Practical Activity: - Read and understand drawings - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install anti freezing/defrosting and water level protection system - Fault finding & Trouble shooting - Leak testing & Charge refrigerant in refrigeration system - Replace different parts | Theory-1Hr Practical-9Hrs Total-10Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Classroom Training Workshop |
| LU2. Install industrial refrigeration system | Trainee will be able to: - Select components of system according to requirements for the installation. - Prepare Floor and level to install industrial refrigeration system according to layout plans. - Install industrial refrigeration system according to specifications following manufacturer’s specification. - Install refrigeration equipment including piping & electrical wiring following standard practices and safety procedures. - Check and test system before commissioning, as per specifications and manufacturer’s instructions, and under the supervision of the engineer. - Record commissioning data indicating system pressures, electrical data, humidity & temperatures outside & inside cold room and filed for future use. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration, And Air Conditioning Engineers (ASHRAE) - Different types of electric motors - Working principles of different types of electric motors - Refrigeration and its types - Commercial refrigeration - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Compressors and functions of compressors - Air purge valves, fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Read and understand drawings - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install anti freezing/defrosting and water level protection system - Fault finding & Trouble shooting - Leak testing & Charge refrigerant in refrigeration system - Replace different parts | Theory-1Hr Practical-9Hrs Total-10Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Training Workshop Lab/ Field Visit |
| LU3. Maintain / repair industrial refrigeration system. | - Check cold room / freezer room / ice plant and repair / maintenance if necessary - Enlist equipment / items, material and accessories as required for the job. - Check all components of the electrical / electronic circuits according to standard practice and manufacturers specifications to ensure correct performance and defects rectified. - Check and ensure performance of all electro - mechanical safety & control devices according to manufacturer’s specifications. - Check all mechanical devices such as drive belts etc. for correct performance according to manufacturer’s specifications. - Check all components of the refrigeration circuit and rectify defects for correct performance according to manufacturer’s specifications. - Check Defrost heaters, drain line, Pan heaters, fan delays, de frost timers, defrost termination devices and temperature controllers, service / replace where necessary to ensure proper functioning. - Check Body mounts and restore to the required condition - Test system pressure and repair gas leaks by using specified test instruments. - Evacuate system by using vacuum pump and charge gas by weight method using specified equipment according to specifications. - Operate, check and test plant, to ensure satisfactory performance according to manufacturer’s specifications. - Re-commission and hand over the plant, according to manufactures specifications, following safety procedures, under the supervision of the superior and record readings / data obtained during commissioning of the plant and check against manufacturers specifications. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration, And Air Conditioning Engineers (ASHRAE) - Different types of electric motors - Working principles of different types of electric motors - Refrigeration and its types - Commercial refrigeration - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Compressors and functions of compressors - Air purge valves, fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Read and understand drawings - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install anti freezing/defrosting and water level protection system - Fault finding & Trouble shooting - Leak testing & Charge refrigerant in refrigeration system - Replace different parts | Theory-1Hr Practical-9Hrs Total-10Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Training Workshop Lab/ Field Visit |

## Install, Maintain & Repair Commercial Refrigeration System.

Objective: After the completion of this competency standard, the Trainee will be able to

Duration:  20Hours			Theory:  2Hours			Practice:  18Hours          	 Credit Hours:  2

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Diagnose Faults in Refrigeration Units. | Trainee will be able to: - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Check for obvious problem to determine which component or system is causing the problem - Select tools, equipment and related accessories according to requirements and standards. - Check the power supply, electric wiring, electric / electronic components and refrigerant pressure to determine the exact problem by using flow chart as recommended by manufacturer and record the results - Eliminate the causes of the problem according to the manufacturer’s manual and standards. - Isolate and recheck the causes of the problem and correct the fault - Start the Refrigeration unit and recheck the unit as specified in the manufacturer’s manual and record the results | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration, And Air Conditioning Engineers (ASHRAE) - Different types of electric motors - Working principles of different types of electric motors - Ohm meter, Voltmeter and Ampere meter use - Refrigeration and its types - Commercial refrigeration - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Compressors and functions of compressors - Air purge valves, fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Read and understand drawings - check foundations and hangers - check components of refrigeration system - check plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - check anti freezing/defrosting and water level protection system - Fault finding & Trouble shooting - check Leak testing & Charge refrigerant in refrigeration system - check different parts | Theory-1Hr Practical-9Hrs Total-10Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar mmeter (0 - 1000 Volt) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Classroom Training Workshop |
| LU2. Repair Refrigeration Units | Trainee will be able to: - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Select tools, equipment and related accessories according to requirements and standards - Disconnect the Refrigerator from electric supply and follow the manual instructions for rectification - Rectify the fault as per diagnosed with the help of repair / replace the components - Switched on Refrigerator to check the performance of electrical/ electronic and mechanical components as specified in the manufacturer’s manual and record the results | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration, And Air Conditioning Engineers (ASHRAE) - Different types of electric motors - Working principles of different types of electric motors - Ohm meter, Voltmeter and Ampere meter use - Refrigeration and its types - Commercial refrigeration - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Compressors and functions of compressors - Air purge valves, fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Read and understand drawings - Check and maintain water drain connections - Check and maintain anti freezing/defrosting and water level protection system - Fault finding & Trouble shooting - Leak testing & Charge refrigerant in refrigeration system - Replace different parts | Theory-1Hr Practical-9Hrs Total-10Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Class Room Training Workshop |

## Install, Maintain & Repair Package Type Air Conditioning System.

Objective: After the completion of this competency standard, the Trainee will be able to repair package type Air Conditioners. It includes preparing unit, tools and workplace, checking and identifying defects and repairing of package type air conditioners to provide you the basis for your work.

Duration: 20 Hours			Theory: 4 Hours			Practice: 16 Hours          	 Credit Hours:  2

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare package type Air Conditioner for service and maintenance | Trainee will be able to: - Observe safe work practices and personal protective equipment (PPE) worn as required for the work to perform. - Identify necessary tools and equipment in line with job requirements - Select necessary materials as per job requirement - Clean and assemble materials for package type Air conditioner as per work standard. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration, And Air Conditioning Engineers (ASHRAE) - Different types of electric motors - Working principles of different types of electric motors - Types of split air conditioners and package type air conditioners - Refrigeration and its types - Commercial refrigeration - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Compressors and functions of compressors - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Mark location for unit - Check air conditioner and make electrical connections - Check plumbing assembly for condenser water and drain - Fault finding & Trouble shooting in unit - Leak testing & Charge refrigerant in air conditioner - Replace different parts of air conditioner | Theory-1Hr Practical-4Hrs Total-5Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Training Workshop Lab/ Field Visit |
| LU2. Check and Identify faults | Trainee will be able to: - Observe systematic pre-testing procedure in accordance with manufacturer’s instruction - Identify system defects / faults symptoms are using appropriate tools and equipment - Check different feature by using recommended testing procedure - Check components of Electrical Circuit of Package type air conditioner by using recommended testing procedure | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration, And Air Conditioning Engineers (ASHRAE) - Different types of electric motors - Working principles of different types of electric motors - Types of split air conditioners and package type air conditioners - Refrigeration and its types - Commercial refrigeration - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Compressors and functions of compressors - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Mark location for unit - Check and maintain air conditioner and make electrical connections - Check and maintain plumbing assembly for condenser water and drain - Fault finding & Trouble shooting in unit - Leak testing & Charge refrigerant in air conditioner - Replace different parts of air conditioner | Theory-1Hr Practical-4Hrs Total-5Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Training Workshop Lab/ Field Visit |
| LU3. Service / Maintain of package type air conditioner | - Replace defective components of refrigeration system with identical or recommended appropriate equivalent ratings - Perform control settings/adjustments in conformity with service-manual specifications - Clean air filter and evaporator fins with cleaning agent - Evacuate the system by using high vacuum pump. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration, And Air Conditioning Engineers (ASHRAE) - Different types of electric motors - Working principles of different types of electric motors - Types of split air conditioners and package type air conditioners - Refrigeration and its types - Commercial refrigeration - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Compressors and functions of compressors - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Mark location for unit - Check and maintain air conditioner and make electrical connections - Check and maintain plumbing assembly for condenser water and drain - Fault finding & Trouble shooting in unit - Leak testing & Charge refrigerant in air conditioner - Check and maintain different parts of air conditioner | Theory-1Hr Practical-4Hrs Total-5Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Training Workshop Lab/ Field Visit |
| LU4. Clean and store of tools and equipment | - Maintain and clean tools and equipment as per instruction - Clean workplace in accordance with environmental requirements - Store tools and equipment safely inappropriate location according to standard workshop procedure | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration, And Air Conditioning Engineers (ASHRAE) - Filters, strainers and lubrication oils - Record keeping and reporting Practical Activity: - Mark location for unit - clean air conditioner and make electrical connections - clean plumbing assembly for condenser water and drain - clean different parts of air conditioner | Theory-1Hr Practical-4Hrs Total-5Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Training Workshop Lab/ Field Visit |

## Install Central Air Conditioning System.

Objective: After the completion of this competency standard, the Trainee will be able to install Package type unit / VRF / VRV / Absorption Chiller system at workplace in accordance with the organization’s / client’s guidelines under the supervision of HVAC Engineer. This unit covers the knowledge regarding safety rules, personal protective equipment, and international standards for the installation of central air conditioning system to provide you the basis for student work.

Duration: 30 Hours			Theory: 9 Hours			Practice: 21 Hours          	 Credit Hours:  3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Install Package Unit | Trainee will be able to: - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Select tools, equipment and related accessories according to job requirements - Mark the location and area according to layout plan and manufacturer’s specifications - Prepare foundation as per drawing, place, adjust and level the Package unit by giving attention to safety precautions - Connect Package unit with duct through flexible connection - Connect the power supply and control wires attached with Building Management (BMS) system - Switch on the supply and check the performance according to manufacturer’s instructions and standards | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - HVACR, Electric and Electronics fundamentals - Techniques for installation of central Air conditioners - Fundamental and Technical Operations of VRF / VRV system - Electrical / HVAC layout plans/wiring diagrams. - Electrical control wires, cables, including underground cables, their ratings and its applications - Methods of Copper Tube cutting / Bending /Swaging / Flaring / Brazing / Y-Jointing / fixing - Basic Masonry and Carpentry applications - Welding types and techniques - Types of Insulation and their applications - Types of AHU, FCU, Chillers, Cooling towers, Compressor, Condenser and pump types and their applications - Types of Refrigerant, its properties, recovery and reclaiming - Procedure regarding commissioning the central HVAC systems - Record keeping and reporting Practical Activity: - Read and understand drawings - Mark locations according to specification - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install AHU and FCU - Balancing the system (Air / Water) | Theory-1 Hr Practical- 3Hrs Total-4Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Training Workshop Lab/ Field Visit |
| LU2. Install Variable Refrigerant Flow (VRF) / Variable Refrigerant Volume (VRV) System | Trainee will be able to: - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Select tools, equipment and related accessories according to job requirements - Prepare foundation as per drawing, place, adjust and level the system by giving attention to safety precautions - Prepare piping, weld braze them according to unit specifications and layout drawings - Install indoor units according to layout diagrams, client requirements and manufacturer’s instruction manual. - Fix Shut-off valves with service ports on every indoor unit - Check leaks by applying pressure method before the joint’s insulation, repair leaks, if any - Insulate the copper pipe joints according to manufacturer’s instructions and standards | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - HVACR, Electric and Electronics fundamentals - Techniques for installation of central Air conditioners - Fundamental and Technical Operations of VRF / VRV system - Electrical / HVAC layout plans/wiring diagrams. - Electrical control wires, cables, including underground cables, their ratings and its applications - Methods of Copper Tube cutting / Bending /Swaging / Flaring / Brazing / Y-Jointing / fixing - Basic Masonry and Carpentry applications - Welding types and techniques - Types of Insulation and their applications - Types of AHU, FCU, Chillers, Cooling towers, Compressor, Condenser and pump types and their applications - Types of Refrigerant, its properties, recovery and reclaiming - Procedure regarding commissioning the central HVAC systems - Record keeping and reporting Practical Activity: - Read and understand drawings - Mark locations according to specification - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install AHU and FCU - Balancing the system (Air / Water) : | Theory-1 Hr Practical- 3Hrs Total-4Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Training Workshop Lab/ Field Visit |
| LU3.Install Water Chiller System | - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Select tools, equipment and related accessories according to job requirements - Mark the location and area according to layout plan - Prepare foundation as per drawing, place, adjust and level the chiller by giving attention to safety precautions - Install Air Handling Units (AHU) at different locations inside the building according to drawing - Install seamless high-pressure MS Pipe from chiller to Air Handling Units inside the building. - Fabricate and install G.I sheet ducting inside the building as per drawing. - Install Water Cooling Tower outside the building / roof (Only for water cooled condenser). - Install building management system (BMS) as per design - Establish the electric power supply system for the chiller & air handling units and cooling tower as per Requirements & Standards. - Perform Air Balancing test, Pressure test, Smoke test, etc. - Switch on the system and check performance. | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - HVACR, Electric and Electronics fundamentals - Techniques for installation of central Air conditioners - Fundamental and Technical Operations of VRF / VRV system - Electrical / HVAC layout plans/wiring diagrams. - Electrical control wires, cables, including underground cables, their ratings and its applications - Methods of Copper Tube cutting / Bending /Swaging / Flaring / Brazing / Y-Jointing / fixing - Basic Masonry and Carpentry applications - Welding types and techniques - Types of Insulation and their applications - Types of AHU, FCU, Chillers, Cooling towers, Compressor, Condenser and pump types and their applications - Types of Refrigerant, its properties, recovery and reclaiming - Procedure regarding commissioning the central HVAC systems - Record keeping and reporting Practical Activity: - Read and understand drawings - Mark locations according to specification - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install AHU and FCU - Balancing the system (Air / Water) | Theory-1 Hr Practical- 3Hrs Total-4Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Training Workshop Lab/ Field Visit |
| LU4. Carry out Commissioning | - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Select tools, equipment and related accessories according to job requirements - Start the condenser and chilled water pump for water circulation in the system - Start the chiller and take reading of all parameters regarding pressure and electric power, check unusual vibrations / noises etc., if any. - Perform Air Balancing test to check the air distribution according to design requirements - Start AHU’s, FCU’s and Humidifiers/ Dehumidifiers for air circulation at the required areas. - Check the system performance. | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - HVACR, Electric and Electronics fundamentals - Techniques for installation of central Air conditioners - Fundamental and Technical Operations of VRF / VRV system - Electrical / HVAC layout plans/wiring diagrams. - Electrical control wires, cables, including underground cables, their ratings and its applications - Methods of Copper Tube cutting / Bending /Swaging / Flaring / Brazing / Y-Jointing / fixing - Basic Masonry and Carpentry applications - Welding types and techniques - Types of Insulation and their applications - Types of AHU, FCU, Chillers, Cooling towers, Compressor, Condenser and pump types and their applications - Types of Refrigerant, its properties, recovery and reclaiming - Procedure regarding commissioning the central HVAC systems - Record keeping and reporting Practical Activity: - Read and understand drawings - Mark locations according to specification - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install AHU and FCU - Balancing the system (Air / Water) Practical Activity: - Read and understand drawings - Mark locations according to specification - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install AHU and FCU - Balancing the system (Air / Water) | Theory-1 Hr Practical- 1 Hr Total-2Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Training Workshop Lab/ Field Visit |
| LU 5. Install the Water Chiller Plant. | - Check and ensure availability of required electrical power supply - Check Air Conditioner and ensure its suitability according to requirement - Layout plan and manufacturer’s specifications/instructions referred to, and location of installation identified - Prepare a list of items and material and number of labor hours required for the estimated job. - Check & test required Floor / foundation level and firmness - Transfer Unit to required location giving attention to safety precautions - Mount, adjust and level unit at pre-identified location - Install piping & connections for chilled water & condenser water - Install Stop valve &commissioning valve (DRV) in condenser, evaporator, thermometer wells and pressure tap according to specification - Install Condenser and chilled water pumps with double regulator valve (DRV) Variable Frequency Drive (VFD)according to specification - Install Electrical wiring and control panels/switchgear according to specifications | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - HVACR, Electric and Electronics fundamentals - Techniques for installation of central Air conditioners - Fundamental and Technical Operations of VRF / VRV system - Electrical / HVAC layout plans/wiring diagrams. - Electrical control wires, cables, including underground cables, their ratings and its applications - Methods of Copper Tube cutting / Bending /Swaging / Flaring / Brazing / Y-Jointing / fixing - Basic Masonry and Carpentry applications - Welding types and techniques - Types of Insulation and their applications - Types of AHU, FCU, Chillers, Cooling towers, Compressor, Condenser and pump types and their applications - Types of Refrigerant, its properties, recovery and reclaiming - Procedure regarding commissioning the central HVAC systems - Record keeping and reporting Practical Activity: - Read and understand drawings - Mark locations according to specification - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install AHU and FCU - Balancing the system (Air / Water) Practical Activity: - Read and understand drawings - Mark locations according to specification - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install AHU and FCU - Balancing the system (Air / Water) | Theory-1 Hr Practical- 3Hrs Total-4Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Training Workshop Lab/ Field Visit |
| LU 6. Install Cooling Tower | - Inspect Cooling Tower verify, confirm its suitability layout plan and manufacturer’s specifications/instructions refer to, and location for installation - Check & test Floor / foundation required level and confirm firmness - Transfer Unit to required location ensuring safety precautions - Mount Unit at pre-identified location, adjust and level - Install Cooling tower basin and level Fill packs, Cooling tower motor & fan - Connect Water pipes to cooling tower as necessary - Connect Electrical wiring to cooling tower - Test Cooling tower for satisfactory performance and make adjustments, where necessary | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - HVACR, Electric and Electronics fundamentals - Techniques for installation of central Air conditioners - Fundamental and Technical Operations of VRF / VRV system - Electrical / HVAC layout plans/wiring diagrams. - Electrical control wires, cables, including underground cables, their ratings and its applications - Methods of Copper Tube cutting / Bending /Swaging / Flaring / Brazing / Y-Jointing / fixing - Basic Masonry and Carpentry applications - Welding types and techniques - Types of Insulation and their applications - Types of AHU, FCU, Chillers, Cooling towers, Compressor, Condenser and pump types and their applications - Types of Refrigerant, its properties, recovery and reclaiming - Procedure regarding commissioning the central HVAC systems - Record keeping and reporting Practical Activity: - Read and understand drawings - Mark locations according to specification - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install AHU and FCU - Balancing the system (Air / Water) | Theory-1 Hr Practical- 1Hr Total-2Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Training Workshop Lab/ Field Visit |
| LU 7. Install Air handling Equipment | - Install Air handling equipment according to specification at the specified location (Fan) reheat coil to maintain R.H. controller (relative Humidity) as required. - Connect Electrical supply, piping and duct lines using specifies accessories and tools. (DRV/ motorized valve with temperature control) | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - HVACR, Electric and Electronics fundamentals - Techniques for installation of central Air conditioners - Fundamental and Technical Operations of VRF / VRV system - Electrical / HVAC layout plans/wiring diagrams. - Electrical control wires, cables, including underground cables, their ratings and its applications - Methods of Copper Tube cutting / Bending /Swaging / Flaring / Brazing / Y-Jointing / fixing - Basic Masonry and Carpentry applications - Welding types and techniques - Types of Insulation and their applications - Types of AHU, FCU, Chillers, Cooling towers, Compressor, Condenser and pump types and their applications - Types of Refrigerant, its properties, recovery and reclaiming - Procedure regarding commissioning the central HVAC systems - Record keeping and reporting Practical Activity: - Read and understand drawings - Mark locations according to specification - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly , - Make water drain connections - Install AHU and FCU - Balancing the system (Air / Water) | Theory-1 Hr Practical- 1Hrs Total-2Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device | Training Workshop Lab/ Field Visit |
| LU 8. Install Ducts | - Read & interpret Drawings and specifications for installing ducts - Locate and mark places where ducts are to be laid, according to specifications - Install Brackets / supports for mounting of ducts as necessary Mount Ducts, level and adjust, as necessary - Install Fire dampers and air volume dampers in ducts as per drawings - Insulate heat ducts according to manufacturer’s specifications - Do final connections of ducts to air handling plant as per manufacturer’s instructions - Check and ensure availability of required electrical power supply - Energize air side equipment of system and check defects in air side, plan, as necessary | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - HVACR, Electric and Electronics fundamentals - Techniques for installation of central Air conditioners - Fundamental and Technical Operations of VRF / VRV system - Electrical / HVAC layout plans/wiring diagrams. - Electrical control wires, cables, including underground cables, their ratings and its applications - Methods of Copper Tube cutting / Bending /Swaging / Flaring / Brazing / Y-Jointing / fixing - Basic Masonry and Carpentry applications - Welding types and techniques - Types of Insulation and their applications - Types of AHU, FCU, Chillers, Cooling towers, Compressor, Condenser and pump types and their applications - Types of Refrigerant, its properties, recovery and reclaiming - Procedure regarding commissioning the central HVAC systems - Record keeping and reporting Practical Activity: - Read and understand drawings - Mark locations according to specification - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install AHU and FCU - Balancing the system (Air / Water) | Theory-1 Hr Practical- 3Hrs Total-4Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device - Laser Temperature Measuring Device | Training Workshop Lab/ Field Visit |
| LU 9. Assist testing &commissioning the Air Conditioning system | - Check condensing medium equipment such as air-cooled condensers /cooling towers and pumps - Energize crank case heaters of main plant for specified number of hours according to manufacturer’s specifications, and switch on main air-conditioning equipment. - Take readings of electrical power taken and check electrical safety gear, unusual noises & vibrations - Check and repair leak (if any) of refrigerant circuit in air conditioning system - Operate and check system for satisfactory performance - Record performance of the equipment | - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - HVACR, Electric and Electronics fundamentals - Techniques for installation of central Air conditioners - Fundamental and Technical Operations of VRF / VRV system - Electrical / HVAC layout plans/wiring diagrams. - Electrical control wires, cables, including underground cables, their ratings and its applications - Methods of Copper Tube cutting / Bending /Swaging / Flaring / Brazing / Y-Jointing / fixing - Basic Masonry and Carpentry applications - Welding types and techniques - Types of Insulation and their applications - Types of AHU, FCU, Chillers, Cooling towers, Compressor, Condenser and pump types and their applications - Types of Refrigerant, its properties, recovery and reclaiming - Procedure regarding commissioning the central HVAC systems - Record keeping and reporting Practical Activity: - Read and understand drawings - Mark locations according to specification - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install AHU and FCU - Balancing the system (Air / Water) | Theory-1 Hr Practical- 3Hrs Total-4Hrs |  | Training Workshop Lab/ Field Visit |

## Repair and Service Central Air Conditioning System.

Objective: After the completion of this competency standard, the Trainee will be able to diagnose / repair / service central air conditioning system at workplace in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding safety rules, personal protective equipment, and international standards for repairing / servicing of central air conditioning units to provide you the basis for student work.

Duration: 60  Hours			Theory:  8Hours			Practice: 52 Hours          	 Credit Hours:  6

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Diagnose Fault in Central Air Conditioning System | Trainee will be able to: - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Check for obvious problem to determine which component or system is causing the problem - Select tools, equipment and related accessories according to requirements and standards. - Arrange drawings and manuals of the equipment to be attended for fault diagnose - Check the power supply, electric wiring, electric / electronic components and refrigerant pressure to determine the exact problem and record the results - Eliminate the causes of the problem according to the manufacturer’s manual and standards. - Start the air conditioning unit and recheck as specified in the manufacturer’s manual and record the results | - Regulations of American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - HVACR and Electrical / Electronic components - Technical Operations of Chillers, Cooling Tower, Pumps, AHUs & FCUs - Types of electrical controls, wires and cables, including underground cables, their ratings and its applications - Techniques of Diagnose and Troubleshooting of central Air conditioning systems - Central Air conditioners error codes and solution - Types of Motors used in central Air conditioners - Types of controls and their functions used in central air conditioning systems - Uses & handle the micron gauge for deep vacuum measuring - Gas welding (Soldering and Brazing) - Types of Insulation and their applications - Compressor, Condenser, Evaporator types and applications - Types of Refrigerant, its properties, recovery and reclaiming - Record keeping and reporting Practical Activity: - Diagnose faults of central Air Conditioning Systems by using specified tools and instruments - Repair refrigerant leaks - Replace the motors and other parts & Accessories - Replace the controls - Replace water pump - Replace motorized actuators | Theory-2Hrs Practical-13Hrs Total-15Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device | Training Workshop Lab/ Field Visit |
| LU2. Repairing of Air Handling Unit (AHU) / Fan Coil Unit (FCU) | Trainee will be able to: - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Select tools, equipment and related accessories according to job requirements - System shut down and follow the manual instructions for rectification - Rectify the faults as per diagnosed, repair / replace the components, as necessary - Switch on the system to check the performance of electrical / mechanical components as specified in the manufacturer’s manual and record the results | - Regulations of American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - HVACR and Electrical / Electronic components - Technical Operations of Chillers, Cooling Tower, Pumps, AHUs & FCUs - Types of electrical controls, wires and cables, including underground cables, their ratings and its applications - Techniques of Diagnose and Troubleshooting of central Air conditioning systems - Central Air conditioners error codes and solution - Types of Motors used in central Air conditioners - Types of controls and their functions used in central air conditioning systems - Uses & handle the micron gauge for deep vacuum measuring - Gas welding (Soldering and Brazing) - Types of Insulation and their applications - Compressor, Condenser, Evaporator types and applications - Types of Refrigerant, its properties, recovery and reclaiming - Record keeping and reporting Practical Activity: - Diagnose faults of central Air Conditioning Systems by using specified tools and instruments - Repair refrigerant leaks - Replace the motors and other parts & Accessories - Replace the controls - Replace water pump - Replace motorized actuators | Theory-2Hrs Practical-13Hrs Total-15Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device | Training Workshop Lab/ Field Visit |
| LU3. Maintain Cooling Tower | - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Select tools, equipment and related accessories according to job requirements - System shut down and follow the manual instructions for rectification - Check Air purge valve and water level of cooling tower - Check the fan assembly, to check the bearings and motor abnormalities according to manufacturer’s specifications and HVAC standards. - Check the float valves and strainers to maintain water level - Perform chemical treatment to prevent the sludge / scaling problems according to manufacturer’s specifications and HVAC standards. - Condenser / chilled water pumps start and check their performance according to their specifications, service / repair, if necessary - Clean the sprinkler assembly, water pan from leaves, mud, and scale, if any. - Rectify the fault and restart the cooling tower unit. | - Regulations of American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - HVACR and Electrical / Electronic components - Technical Operations of Chillers, Cooling Tower, Pumps, AHUs & FCUs - Types of electrical controls, wires and cables, including underground cables, their ratings and its applications - Techniques of Diagnose and Troubleshooting of central Air conditioning systems - Central Air conditioners error codes and solution - Types of Motors used in central Air conditioners - Types of controls and their functions used in central air conditioning systems - Uses & handle the micron gauge for deep vacuum measuring - Gas welding (Soldering and Brazing) - Types of Insulation and their applications - Compressor, Condenser, Evaporator types and applications - Types of Refrigerant, its properties, recovery and reclaiming - Record keeping and reporting Practical Activity: - Diagnose faults of central Air Conditioning Systems by using specified tools and instruments - Repair refrigerant leaks - Replace the motors and other parts & Accessories - Replace the controls - Replace water pump - Replace motorized actuators | Theory-2Hrs Practical-13Hrs Total-15Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device | Training Workshop Lab/ Field Visit |
| LU4. Repair Control System | - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Select tools, equipment and related accessories according to job requirements - System shut down and follow the manual instructions for rectification - Arrange drawings and manuals of the equipment to be attended for fault diagnose - Check the details of fault / errors on computer screen to rectify the same - Eliminate the causes of the problem according to the manufacturer’s manual and standards. - Isolate and recheck the causes of the problem and correct the fault - Start the air conditioning unit and recheck as specified in the manufacturer’s manual and record the results | - Regulations of American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - HVACR and Electrical / Electronic components - Technical Operations of Chillers, Cooling Tower, Pumps, AHUs & FCUs - Types of electrical controls, wires and cables, including underground cables, their ratings and its applications - Techniques of Diagnose and Troubleshooting of central Air conditioning systems - Central Air conditioners error codes and solution - Types of Motors used in central Air conditioners - Types of controls and their functions used in central air conditioning systems - Uses & handle the micron gauge for deep vacuum measuring - Gas welding (Soldering and Brazing) - Types of Insulation and their applications - Compressor, Condenser, Evaporator types and applications - Types of Refrigerant, its properties, recovery and reclaiming - Record keeping and reporting Practical Activity: - Diagnose faults of central Air Conditioning Systems by using specified tools and instruments - Repair refrigerant leaks - Replace the motors and other parts & Accessories - Replace the controls - Replace water pump - Replace motorized actuators | Theory-2Hrs Practical-13Hrs Total-15Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm - Tube Benders (Spring Type and Pulley Bender Type - Laser Distance Measuring Device | Training Workshop Lab/ Field Visit |

## Service and Maintain Ceiling Mounted Cassette Type Air Conditioner

Objective: After the completion of this competency standard, the Trainee will be able to repair Cassette type Air Conditioners using specified tools, test & measuring instruments. It includes preparing unit, tools and workplace, checking and identifying defects and repairing of cassette type air conditioning units to provide you the basis for student work.

Duration:20  Hours			Theory: 4 Hours			Practice:16  Hours          	 Credit Hours:  2

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare for service and maintenance Cassette type Air Conditioner | Trainee will be able to: - Observe safe work practices and personal protective equipment (PPE) worn as required for the work to be performed. - Identify necessary tools and equipment in line with job requirements - Select necessary materials as per job requirement - Clean and assemble materials for package type Air conditioner as per work standards | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Different types of electric motors - Working principles of different types of electric motors - Ohm meter, Voltmeter and Ampere meter use - Record keeping and reporting Practical Activity: - Diagnose faults of Ceiling Mounted Cassette Type Air Conditioner by using specified tools and instruments - Repair refrigerant leaks - Replace the motors and other electric parts & Accessories - Clean drains | Theory- 1Hr Practical-4Hrs Total-5Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Class Room Training Workshop |
| LU2. Check and Identify fault . | Trainee will be able to: - Observe systematic Test and Checking in accordance with manufacturer’s instruction. - Check components of the Air-flow system according to manufactures specifications to ensure correct performance - Test system pressure with dry nitrogen using specified equipment following safety procedures. - Check motor terminals using specified testing procedures - Check motor settings/adjustments in conformity with service-manual specifications. - Check components of refrigeration and electrical / electronic circuit according to standard procedures. - Identify system defects/fault symptoms and document using appropriate tools and equipment. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Different types of electric motors - Working principles of different types of electric motors - Ohm meter, Voltmeter and Ampere meter use - Record keeping and reporting Practical Activity: - Diagnose faults of Ceiling Mounted Cassette Type Air Conditioner by using specified tools and instruments - Repair refrigerant leaks - Replace the motors and other electric parts & Accessories - Clean drains | Theory- 1Hr Practical-4Hrs Total-5Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Class Room Training Workshop |
| LU3. Servicing / Maintenance of package type air conditioner | - Replace defective components with identical or recommended appropriate equivalent ratings - Perform control settings/adjustments in conformity with service-manual specifications - Clean air filter and evaporator fins with approved cleaning agent - Evacuate system by using high vacuum pump and charge required refrigerant (if needed) according to manufacturer instructions. - Charge refrigerant using specified type of refrigerant by charging equipment to required specification following safety practices. - Perform cleaning of unit in accordance with standard procedures - Operate and check unit to ensure satisfactory performance according to manufactures specifications | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Different types of electric motors - Working principles of different types of electric motors - Ohm meter, Voltmeter and Ampere meter use - Record keeping and reporting Practical Activity: - Diagnose faults of Ceiling Mounted Cassette Type Air Conditioner by using specified tools and instruments - Repair refrigerant leaks - Replace the motors and other electric parts & Accessories - Clean drains | Theory- 1Hr Practical-4Hrs Total-5Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Class Room Training Workshop |
| LU4. Clean and store of tools and equipment | - Clean and maintain tools and equipment as per instruction manual - Clean workplace in accordance with environmental requirement - Store tools and equipment safely inappropriate location according to standard workshop procedure. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Record keeping and reporting Practical Activity: - Diagnose faults of Ceiling Mounted Cassette Type Air Conditioner by using specified tools and instruments - Repair refrigerant leaks - Replace the motors and other electric parts & Accessories - Clean drains | Theory- 1Hr Practical-4Hrs Total-5Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Class Room Training Workshop |

## Service and Maintain Cooling Tower.

Objective: After the completion of this competency standard, the Trainee will be able to understand, operate & maintain cooling towers/evaporative condenser used in hydronic systems of HVAC units. His underpinning knowledge regarding servicing and maintenance of cooling tower will be sufficient to provide the basis for his work.

Duration: 30 Hours			Theory: 6 Hours			Practice: 24 Hours          	 Credit Hours:  3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Undertake preventive maintenance checks | Trainee will be able to: - Understand the legislative requirements. - Identify the system components. - Inspect and test the operational function of each component. - Assess the correct operation of each component against specification. - Test and visual inspection with appropriate test equipment are carried out according to refrigeration principles, procedures and safety requirements. - Preventative maintenance tasks are performed to manufacturers' specifications using refrigeration techniques and practices. - Remove the fills.. | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - HVACR, Electrical and Electronics control - Technical Operations and operation of Control - Terminology of cooling towers - Sling Psychrometer and measure the properties of air through Psychrometric chart - Measuring instruments/equipment, specifications and procedures for checking temperature(s)/humidity/air flow - Terminology operation and field testing of centrifugal water pumps - Operation of water valves including bypass valve either mechanical or electrical operation - Procedures for testing of fan motors V-belts - Measuring instruments/equipment, specifications and procedures for checking component noise and vibration levels - Procedures for reporting non-conformances - Procedures and sequence for performing preventative maintenance on refrigeration and air conditioning systems - Specifications, operational characteristics and process for identifying system components - Process for localizing and confirming faulty components - Procedures and all legislative and regulatory requirements for safely removing the refrigerant and charging the system - Procedures for dismantling, repairing, reassembling and testing components - Procedure for removal/recharging refrigerant Practical Activity: - Check & Visually inspect the tower - Replace fills (Filling Material) - Replace fan motor and float valve - Calculate tower range & approach - Calculate PH value of tower water - Perform make up water and bleed off process | Theory-2Hrs Practical-4Hrs Total-6Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit | Training Workshop Lab/ Field Visit |
| LU2. Undertake fault finding on cooling tower/evaporative condenser water systems components | Trainee will be able to: - Identify the system components correctly. - Assess the correct operation of each component against specification. - Understand the characteristics and operation of each component. - Calculate the tower approach - Calculate the tower range. - Calculate the Ph value of tower water. | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - HVACR, Electrical and Electronics control - Technical Operations and operation of Control - Terminology of cooling towers - Sling Psychrometer and measure the properties of air through Psychrometric chart - Measuring instruments/equipment, specifications and procedures for checking temperature(s)/humidity/air flow - Terminology operation and field testing of centrifugal water pumps - Operation of water valves including bypass valve either mechanical or electrical operation - Procedures for testing of fan motors V-belts - Measuring instruments/equipment, specifications and procedures for checking component noise and vibration levels - Procedures for reporting non-conformances - Procedures and sequence for performing preventative maintenance on refrigeration and air conditioning systems - Specifications, operational characteristics and process for identifying system components - Process for localizing and confirming faulty components - Procedures and all legislative and regulatory requirements for safely removing the refrigerant and charging the system - Procedures for dismantling, repairing, reassembling and testing components - Procedure for removal/recharging refrigerant - Procedures for selecting replacement parts - Procedures for completing maintenance records/service reports - Record keeping and reporting. Practical Activity: - Check & Visually inspect the tower - Replace fills (Filling Material) - Replace fan motor and float valve - Calculate tower range & approach - Calculate PH value of tower water - Perform make up water and bleed off process | Theory-2Hrs Practical-4Hrs Total-6Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) Flaring and Swaging Tool Kit | Training Workshop Lab/ Field Visit |
| LU3. Repair/replace cooling tower/evaporative condenser components | - Inspect and test of faulty components are localised, and malfunction is confirmed by using refrigeration principles, procedures and safety requirements. - Dismantle and repair the faulty components to manufactures' specifications as required. - Replace parts selected from manufacturers' or other catalogues according to required specifications. - Recover refrigerant by following refrigeration principles and procedures to all relevant standards, codes and safety standards | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - HVACR, Electrical and Electronics control - Technical Operations and operation of Control - Terminology of cooling towers - Sling Psychrometer and measure the properties of air through Psychrometric chart - Measuring instruments/equipment, specifications and procedures for checking temperature(s)/humidity/air flow - Terminology operation and field testing of centrifugal water pumps - Operation of water valves including bypass valve either mechanical or electrical operation - Procedures for testing of fan motors V-belts - Measuring instruments/equipment, specifications and procedures for checking component noise and vibration levels - Procedures for reporting non-conformances - Procedures and sequence for performing preventative maintenance on refrigeration and air conditioning systems - Specifications, operational characteristics and process for identifying system components - Process for localizing and confirming faulty components - Procedures and all legislative and regulatory requirements for safely removing the refrigerant and charging the system - Procedures for dismantling, repairing, reassembling and testing components - Procedure for removal/recharging refrigerant - Procedures for selecting replacement parts - Procedures for completing maintenance records/service reports - Record keeping and reporting Practical Activity: - Check & Visually inspect the tower - Replace fills (Filling Material) - Replace fan motor and float valve - Calculate tower range & approach - Calculate PH value of tower water - Perform make up water and bleed off process | Theory-2Hrs Practical-4Hrs Total-6Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit | Training Workshop Lab/ Field Visit |
| LU4. Recheck the system after repair/ servicing. | - Test for correct operation against specification. - Charge refrigerant to system, following refrigeration principles and procedures to all relevant standards, codes and safety standards. - Use refrigeration principles and system application, correct operation of the equipment is verified. - Maintenance records/service reports are completed by appropriate designated means | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - HVACR, Electrical and Electronics control - Technical Operations and operation of Control - Terminology of cooling towers - Sling Psychrometer and measure the properties of air through Psychrometric chart - Measuring instruments/equipment, specifications and procedures for checking temperature(s)/humidity/air flow - Terminology operation and field testing of centrifugal water pumps - Operation of water valves including bypass valve either mechanical or electrical operation - Procedures for testing of fan motors V-belts - Measuring instruments/equipment, specifications and procedures for checking component noise and vibration levels - Procedures for reporting non-conformances - Procedures and sequence for performing preventative maintenance on refrigeration and air conditioning systems - Specifications, operational characteristics and process for identifying system components - Process for localizing and confirming faulty components - Procedures and all legislative and regulatory requirements for safely removing the refrigerant and charging the system - Procedures for dismantling, repairing, reassembling and testing components - Procedure for removal/recharging refrigerant - Procedures for selecting replacement parts - Procedures for completing maintenance records/service reports - Record keeping and reporting Practical Activity: - Check & Visually inspect the tower - Replace fills (Filling Material) - Replace fan motor and float valve - Calculate tower range & approach - Calculate PH value of tower water - Perform make up water and bleed off process | Theory-2Hrs Practical-4Hrs Total-6Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) Flaring and Swaging Tool Kit | Training Workshop Lab/ Field Visit |

## Perform Preventive Maintenance.

Objective: After the completion of this competency standard, the Trainee will be able to calibrate and carry out maintenance of refrigeration / air conditioning system skills at workplace in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding safety rules, personal protective equipment, and international standards for calibrating / maintenance of refrigeration / air conditioning units to provide you the basis for student work.

Duration: 30 Hours			Theory: 6 Hours			Practice:  24Hours          	 Credit Hours:  3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Calibrate and use the Measuring Instruments | Trainee will be able to: - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Shut down the system if necessary and dismantle measuring instruments - Select and arrange tools, equipment and related accessories according to job requirements / sequence of operation - Calibrate the instruments following the manufacturer’s instructions - Reinstall measuring instruments and start the system to check the performance of calibrated instrument as specified by the manufacturer’s - Record the output result of measuring instrument for future reference Follow HVACR standards to complete the job | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - HVACR, Electrical and Electronics control - Technical Operations of Control - Types of electrical wires and cables, their ratings and its applications - Purpose / Advantages of preventive maintenance - Techniques of Diagnose and Troubleshooting of controls - Controls error codes and solution - Types of controls and their functions used in central air conditioning systems - Procedure to replace PCB cards and controls - Methods of calibration of different measurement instruments - Record keeping and reporting Practical Activity: - Prepare maintenance schedule and log sheets - Replace specific parts - Prepare reports (Report writing) | Theory-3Hrs Practical12Hrs Total-15Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Training Workshop Lab/ Field Visit |
| LU2. Carry out Maintenance | Trainee will be able to: - Adopt Occupational Safety and Health (OSH) procedures to avoid hazards and accidents at workplace. - Pump down / Shut down the system if necessary - Select and arrange tools, equipment and material according to job requirements / sequence of operation - Check different machines with measuring instruments for temperature, vibration and noise, etc. to operate the plant at design efficiency - Carry out weekly / monthly / annual maintenance according to schedule - Check and record the performance of system after maintenance Follow HVACR standards to complete the job | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - HVACR, Electrical and Electronics control - Technical Operations of Control - Types of electrical wires and cables, their ratings and its applications - Purpose / Advantages of preventive maintenance - Techniques of Diagnose and Troubleshooting of controls - Controls error codes and solution - Types of controls and their functions used in central air conditioning systems - Procedure to replace PCB cards and controls - Methods of calibration of different measurement instruments - Record keeping and reporting Practical Activity: - Prepare maintenance schedule and log sheets - Replace specific parts - Prepare reports (Report writing) | Theory-3Hrs Practical12Hrs Total-15Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit Vacuum Pump 2-Stage, 6cfm | Training Workshop Lab/ Field Visit |

## Diagnose faults in complex HVAC control system

Objective: After the completion of this competency standard, the Trainee will be able to diagnosing and rectifying faults in complex HVAC / refrigeration control systems. Your underpinning knowledge regarding interpreting technical data, applying knowledge of complex HVACR control systems operating parameters to logical fault-finding processes, implementing fault rectification, safety and functional testing and reporting work activities and outcomes will be enough to provide the basis for student work.

Duration: 30 Hours			Theory: 3 Hours			Practice:  27Hours          	 Credit Hours:  3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare to diagnose and rectify faults. | Trainee will be able to: - Follow OHS procedures for a given work area - Establish OHS risk control measures and procedures and follow in preparation for the work. - Determine the extent of faults from reports and other documentation and from discussion with appropriate personnel. - Consult appropriate personnel to ensure the work is coordinated effectively with others involved on the work site. Obtain Tools, equipment and testing devices needed to diagnose faults in accordance with established procedures and check for correct operation and safety. | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental of HVACR, Electrical and Electronics control - Technical Operations of Control - Types of electrical wires and cables, their ratings and its applications - Purpose / Advantages of preventive maintenance - Techniques of Diagnose and Troubleshooting of controls - Controls error codes and solution - Types of controls and their functions used in central air conditioning systems - Procedure to replace PCB cards and controls - Methods of calibration of different measurement instruments - Record keeping and reporting Practical Activity: - Check & Visually inspect the tower - Measure pressure & temperature at different points of HVAC system - Observe behavior of control and decide its condition | Theory-1Hr Practical-9Hrs Total-10Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Classroom Training Workshop Lab/ Field Visit |
| LU2. Complete and report fault diagnosis and rectification activities | Trainee will be able to: - Follow OHS work completion risk control measures and procedures - Make work site safe in accordance with established safety procedures. - Document rectification of faults in accordance with established procedures. - Notify appropriate person / persons, in accordance with established procedures, that the system faults to rectification. | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental of HVACR, Electrical and Electronics control - Technical Operations of Control - Types of electrical wires and cables, their ratings and its applications - Purpose / Advantages of preventive maintenance - Techniques of Diagnose and Troubleshooting of controls - Controls error codes and solution - Types of controls and their functions used in central air conditioning systems - Procedure to replace PCB cards and controls - Methods of calibration of different measurement instruments - Record keeping and reporting Practical Activity: - Check & Visually inspect the tower - Measure pressure & temperature at different points of HVAC system - Observe behavior of control and decide its condition | Theory-1Hr Practical-9Hrs Total-10Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Classroom Training Workshop Lab/ Field Visit |
| LU3 Complete and report fault diagnosis and rectification activities. | Trainee will be able to: - Follow OHS work completion risk control measures and procedures - Make work site safe in accordance with established safety procedures. - Document rectification of faults in accordance with established procedures. - Notify appropriate person / persons, in accordance with established procedures, that the system faults to rectification. | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental of HVACR, Electrical and Electronics control - Technical Operations of Control - Types of electrical wires and cables, their ratings and its applications - Purpose / Advantages of preventive maintenance - Techniques of Diagnose and Troubleshooting of controls - Controls error codes and solution - Types of controls and their functions used in central air conditioning systems - Procedure to replace PCB cards and controls - Methods of calibration of different measurement instruments - Record keeping and reporting Practical Activity: - Check & Visually inspect the tower - Measure pressure & temperature at different points of HVAC system - Observe behavior of control and decide its condition | Theory-1Hr Practical-9Hrs Total-10Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Classroom Training Workshop Lab/ Field Visit |

## Service and Maintain Automobile Air Conditioner.

Objective: After the completion of this competency standard, the Trainee will be able to maintain and service automotive air conditioning Systems. Your underpinning knowledge regarding identification / confirmation of work requirement, Preparation for work, servicing of air conditioning systems, completion of work finalization processes, including clean-up and documentation will be enough to provide the basis for student work.

Duration: 30 Hours			Theory: 4 Hours			Practice:  26Hours          	 Credit Hours:  3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare for maintenance of car air conditioning system | Trainee will be able to: - Observe safe work practices and personal protective equipment (PPE) worn as required for the work performed. - Identify and collect necessary tools and equipment in accordance with work requirement. - Collect necessary materials in accordance with work requirement. - Identify and prepare Technical and/or calibration requirements for servicing sourced and support equipment Handle the refrigerants when observed dangers | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental of HVACR, Electrical and Electronics control - Technical Operations of Control - Types of electrical wires and cables, their ratings and its applications - Purpose / Advantages of preventive maintenance - Techniques of Diagnose and Troubleshooting of controls - Controls error codes and solution - Types of controls and their functions used in central air conditioning systems - Procedure to replace PCB cards and controls - Methods of calibration of different measurement instruments - Record keeping and reporting Practical Activity: - Diagnose faults of Automobile Air Conditioner by using specified tools and instruments - Repair refrigerant leak in Automobile Air Conditioner - Replace the compressor and other accessories of unit - Recharge refrigerant - Replace belts | Theory-1Hr Practical-6Hrs Total-7Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Classroom Training Workshop Lab/ Field Visit |
| LU2. Conduct test to identify fault. | - Trainee will be able to: - Check air conditioning system components using appropriate tools and techniques. - Check amount of refrigerant as per instruction manual - Detect damaged components and related electric wiring /ECU operating system according to the standard procedures. - Complete the test without causing damage to any work-place property and vehicle. - Identify faults/defects for repairing/servicing action based on checking. | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental of HVACR, Electrical and Electronics control - Technical Operations of Control - Types of electrical wires and cables, their ratings and its applications - Purpose / Advantages of preventive maintenance - Techniques of Diagnose and Troubleshooting of controls - Controls error codes and solution - Types of controls and their functions used in car air conditioning systems - Procedure to replace PCB cards and controls - Methods of calibration of different measurement instruments - Record keeping and reporting Practical Activity: - Diagnose faults of Automobile Air Conditioner by using specified tools and instruments - Repair refrigerant leak in Automobile Air Conditioner - Replace the compressor and other accessories of unit - Recharge refrigerant Replace belts | Theory-1Hr Practical-12Hrs Total-13Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Class Room Training Workshop Lab/ Field Visit |
| LU3. Repair/service Automobile Air Conditioner components | - Perform system testing and air conditioning service procedures determined. - Service the system and components carried out in accordance with manufacturer’s instruction without causing damage to any component or system - Replace components of AC system are performing based on faults with identical components. - Recover refrigerant according to safe manner. - Evacuate the system using high vacuum pump - Charging the Refrigerant is performed in accordance with standard procedure. - Final testing of auto air conditioning system is carried out to ensure the performance up to the unit standard mentioned in the manual. | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental of HVACR, Electrical and Electronics control - Technical Operations of Control - Types of electrical wires and cables, their ratings and its applications - Purpose / Advantages of preventive maintenance - Techniques of Diagnose and Troubleshooting of controls - Controls error codes and solution - Types of controls and their functions used in carl air conditioning systems - Procedure to replace PCB cards and controls - Methods of calibration of different measurement instruments - Record keeping and reporting Practical Activity: - Diagnose faults of Automobile Air Conditioner by using specified tools and instruments - Repair refrigerant leak in Automobile Air Conditioner - Replace the compressor and other accessories of unit - Recharge refrigerant Replace belts | Theory-1Hr Practical-5Hrs Total-6Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm |  |
| LU4. Clean and store equipment | - Perform cleaning of equipment in accordance with workplace expectation - Dispose-off waste materials in accordance with workplace requirements. - Store tools and equipment safely in appropriate location. | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Record keeping and reporting Practical Activity: Clean the all work stations ,tools and equipments | Theory-1Hr Practical-3Hrs Total-4Hrs | - Personal Protective Equipment - Cleaning equipments |  |

## Perform Commissioning of HVAC Systems

Objective: After the completion of this competency standard, the Trainee will be able to setting-up and adjusting complex (HVAC) heating, ventilation and air conditioning systems for optimum performance. Student underpinning knowledge regarding safe working practices, system parameter testing / analysis, adjusting equipment / controls, following procedures / documenting final operating parameters and settings will be enough to provide the basis for student work.

Duration: 20 Hours			Theory: 3 Hours			Practice:  17Hours          	 Credit Hours:  2

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare to commission complex heating, ventilation and air conditioning systems | Trainee will be able to: - Identify and obtain OHS procedures for a given work area - Establish OHS risk control measures and procedures are follow in preparation for the work. - Implement safety hazards that have not previously been identified are noted and established risk control - Consult appropriate personnel to ensure the work is coordinated effectively with others involved on the work site. - Identify system operating parameters by reviewing system specifications and component technical data. - Obtain tools, equipment and testing devices needed for the work in accordance with established - Check procedures for correct operation and safety. - Check preparatory work to ensure no damage has occurred and complies with requirements. Check circuits as being isolated where necessary in strict accordance OHS requirements and procedures | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental of HVACR, Electrical and Electronics control - Technical Operations of Control - Types of electrical wires and cables, their ratings and its applications - Purpose / Advantages of commissioning - Techniques of commissioning - Types of gadgets for commissioning used in central air conditioning systems - Methods of calibration of different measurement instruments - Record keeping and reporting Practical Activity: - Use gadgets for commissioning of central air conditioning equipments - Operate HVAC system in order - Measure pressure and temperature of system | Theory-1Hr Practical-9Hrs Total-10Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Classroom Training Workshop Lab/ Field Visit |
| LU2. Commission complex heating, ventilation and air conditioning systems. | Trainee will be able to: - Control OHS risk measures and procedures for carrying out the work - Connect Test / Measure devices and set in accordance with requirements for a system. - Make measurements and adjustments to equipment components and controls to provide optimum system performance in accordance with system specifications and regulatory requirements. - Make decisions for dealing with unexpected situations from discussions with appropriate persons and job specifications and requirements. - Select methods for dealing with unexpected situations based on safety and specified work outcomes. - Carry out commissioning efficiently without waste of materials or damage to apparatus, the surrounding environment or services and using sustainable energy principles. | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental of HVACR, Electrical and Electronics control - Technical Operations of Control - Types of electrical wires and cables, their ratings and its applications - Purpose / Advantages of commissioning - Techniques of commissioning - Types of gadgets for commissioning used in central air conditioning systems - Methods of calibration of different measurement instruments - Record keeping and reporting Practical Activity: - Use gadgets for commissioning of central air conditioning equipments - Operate HVAC system in order - Measure pressure and temperature of system | Theory-1Hr Practical-4Hrs Total-5Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Classroom Training Workshop Lab/ Field Visit |
| LU3 Completion and report commissioning | Trainee will be able to: - Follow OHS risk control work completion measures and procedures - Clean work site is and make safe in accordance with established procedures. - Document adjustment settings and notify an appropriate person or persons in accordance with established procedures.. | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental of HVACR, Electrical and Electronics control - Technical Operations of Control - Types of electrical wires and cables, their ratings and its applications - Purpose / Advantages of commissioning - Techniques of commissioning - Types of gadgets for commissioning used in central air conditioning systems - Methods of calibration of different measurement instruments - Record keeping and reporting Practical Activity: - Use gadgets for commissioning of central air conditioning equipments - Measure pressure and temperature of system - Make a commissioning report | Theory-1Hr Practical-4Hrs Total-5Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) | Classroom Training Workshop Lab/ Field Visit |

## Install and Commission Carbon Dioxide Refrigeration Systems, Components and Accessories

Objective: After the completion of this competency standard, the Trainee will be able to achieve effective and efficient operation of refrigeration equipment using carbon dioxide (CO2) as a refrigerant excluding self-contained systems. Student underpinning knowledge regarding safe working practice and encompasses applying specialized knowledge of refrigeration principles that apply to carbon dioxide, following design specifications, testing, locating and rectifying faults and defective components and completing the necessary installation and commissioning documentation will be sufficient to provide the basis for your work.

Duration: 20 Hours			Theory: 3 Hours			Practice:  17Hours          	 Credit Hours:  2

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare to install major components and associated equipment. | Trainee will be able to: - Follow OHS procedures for a given work area and establish OHS risk control measures and procedures in preparation for the work. - Obtain the nature of work from documentation or from work supervisor to establish the scope of work to be undertaken. - Install component and equipment appropriately sequence in accordance with job schedule. - Access sources of materials that may be required for the work in accordance with established routines and procedures - Carry out tools, equipment and testing devices needed to the work check for correct operation and safety | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental of HVACR, Electrical and Electronics control - Technical Operations of Control - Types of electrical wires and cables, their ratings and its applications - Purpose / Advantages of commissioning - Techniques of commissioning - Types of gadgets for commissioning use in Carbon Dioxide Refrigeration Systems Methods of calibration of different measurement instruments - Record keeping and reporting Practical Activity: - Use gadgets for commissioning of Carbon Dioxide Refrigeration Systems equipments - Operate Carbon Dioxide Refrigeration Systems in order - Measure pressure and temperature of system | Theory-1Hr Practical-9Hrs Total-10Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Classroom Training Workshop Lab/ Field Visit |
| LU2. Install major components and associated equipment. | Trainee will be able to: - Follow OHS procedures for a given work area and establish OHS risk control measures and procedures in preparation for the work. - Install components and equipment to comply with technical standards, job specifications / requirements with enough access to affect electrical and pipe work connections and maintenance. - Install components and equipment straight and square in the required locations and within acceptable tolerances - Conduct pressure test at a pressure compatible with carbon dioxide and in accordance with standards - Locate leaks and rectify using testing methods appropriate to the system and in accordance with industry practices - Evacuate system to the required level and clean all moisture and other contaminants in accordance with industry practices - Charge system safely with refrigerant grade carbon dioxide and compatible lubricants in accordance with industry practices - Use establish procedures to determine actual and specified range of operating conditions from measured and calculated values as they apply to carbon dioxide vapor compression and volatile secondary (liquid recirculation/cascade) systems - Discuss establish methods for dealing with unexpected situations with appropriate person(s) and document. - Deal unexpected situations with safely and with the approval of an authorized person. - Determine operating conditions without damage to apparatus, circuits, the surrounding environment / services and using sustainable energy practices. | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental of HVACR, Electrical and Electronics control - Technical Operations of Control - Types of electrical wires and cables, their ratings and its applications - Purpose / Advantages of commissioning - Techniques of commissioning - Types of gadgets for commissioning use in Carbon Dioxide Refrigeration Systems Methods of calibration of different measurement instruments - Record keeping and reporting Practical Activity: - Use gadgets for commissioning of Carbon Dioxide Refrigeration Systems equipments - Operate Carbon Dioxide Refrigeration Systems in order - Measure pressure and temperature of system | Theory-1Hr Practical-4Hrs Total-5Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Basic Cutting tools - Basic Power tools - Basic Marking tools - Basic Electric tools - Gas Welding Set with All Accessories - Nitrogen Gas Cylinder with Hose Pipe, Regulator and Back Arrestor - Tube Cutter - Electric Hand Grinder - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - HILTI Drill Machine (Piston Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Classroom Training Workshop Lab/ Field Visit |
| LU3. Complete Installation and commissioning work and document performance data | Trainee will be able to: - Follow OHS work completion risk control measures and procedures - Check installed components and to verify that installed components / equipment is documented and an appropriate person(s) notify in accordance with established procedures. - Sequence commissioning work appropriately in accordance with job specification - Consult appropriate personnel to ensure the work is coordinated effectively with others involved on the work site. - Determine the extent of the system and location of system components from site inspection / job specifications and diagrams - Determine system control settings and operating parameters from job specifications and requirements - Check pre commissioning parameters to ensure all components are in place and secure - Test / measure a live operating CO2 system in strict accordance with OHS requirements and when necessary conducted within established safety procedures. - Adjust Carbon Dioxide refrigeration system pressure controls, valves, pumps and regulators to their required settings. - Use Testing /measuring devices to observe the operation of refrigeration system and fine adjustments of controls are made as necessary. - Establish methods for dealing with unexpected situations discuss with appropriate person(s) and document. - Deal unexpected situations with safely and with the approval of an authorized person. - Perform commissioning efficiently without waste of materials or damage to apparatus and the surrounding environment or services and using sustainable energy practices - Clean work site and make safe in accordance with established procedures - Document results of commissioning including final operating parameters of the system. | - Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Fundamental of HVACR, Electrical and Electronics control - Technical Operations of Control - Types of electrical wires and cables, their ratings and its applications - Purpose / Advantages of commissioning - Techniques of commissioning - Types of gadgets for commissioning use in Carbon Dioxide Refrigeration Systems Methods of calibration of different measurement instruments - Record keeping and reporting Practical Activity: - Use gadgets for commissioning of Carbon Dioxide Refrigeration Systems equipments - Operate Carbon Dioxide Refrigeration Systems in order - Measure pressure and temperature of system - Make a commissioning report | Theory-1Hr Practical-4Hrs Total-5Hrs | - Personal Protective Equipment - Basic Measuring tools - Basic Hand tools - Digital Air Flow / Velocity Meter - Electronic Leak Detector - Spirit Level - Digital Multi Meter - Digital Clamp-On Ampere Meter - Type) - Digital Optical Tachometer - Meggar meter (0 - 1000 Volts) - Digital Capacitor Analyzer - Digital Pressure Gauges Set (High &Combine) - Flaring and Swaging Tool Kit - Vacuum Pump 2-Stage, 6cfm | Classroom Training Workshop Lab/ Field Visit |

## Operate & Maintain Absorption Air Conditioning System

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to operate and maintain Direct Fired absorption air conditioning system in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding operation and maintenance of absorption air conditioning system to provide you the basis for student work.

Duration:  30	Hours			                             Theory: 5	Hours				                  Practice: 	25 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Preventive Maintenance Requirements Refrigerant Side | Trainee will be able to: - Check solution chemical analysis (add inhibitors as needed) - Check refrigerant specific gravity - Check proper solution levels "adjust quantity & add if required' - Check proper concentration level octyl & alcohol | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Define air conditioning systems - Define absorption air conditioning system - Identification refrigerant contamination - Functions of pressure control switches - Functions of pressure Gas switches - Combustion analysis - Types of maintenance - Preventive maintenance - Record keeping and reporting Practical Activity: - Observe system behavior & Record it | Theory-1Hrs. Practical-5 Hrs. Total- 6 Hrs. | - Personal Protective Equipment - Basic tool Kit | Class Room and workshop |
| - Perform Preventive Maintenance Safety Controls | Trainee will be able to: - Check low refrigerant cut-out switch - Check chilled & condenser water flow switches. - Check hot water flow switches - Check HP1 + HP2 (20G direct fired units) high press. & temp. cut-out switches - Check correct HT1 - High temperature cut-out switch - Perform to check & rectify low solution level cut-out switch abnormality. - Perform adoption for accuracy check of thermistors T and transducers - Perform adoption of right procedure for accuracy check of Condenser T Pressure Gauge | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Define air conditioning systems - Define absorption air conditioning system - Identification refrigerant contamination - Functions of pressure control switches - Functions of pressure Gas switches - Combustion analysis - Types of Control - Safety Control - Types of maintenance - Preventive maintenance - Record keeping and reporting Practical Activity: - Follow start up and shut down order of system - Prepare Maintenance Schedule | Theory-1Hrs. Practical-5 Hrs. Total- 6 Hrs. | - Personal Protectiv Equipment - Basic tool Kit | Class Room and workshop |
| - Perform Preventive Maintenance Mechanical Parts & System | Trainee will be able to: - Inspect pump bearing and seal wear, repair / replace if necessary - Inspection pump Contactors repair / replace if necessary - Check average skin temperatures T of pumps for adoption of correct - Check amperage of purge pump for correct operating - Determine to proceed ultimate vacuum of Purge Pump - Check accuracy of manometer or Vacuum Gauge for Implementation - Check Procedure for proper operation of purge educator - Estimate submitted to superior / client and approval obtained | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Define air conditioning systems - Define absorption air conditioning system - Identification refrigerant contamination - Functions of pressure control switches - Functions of pressure Gas switches - Combustion analysis - Types of maintenance - Preventive maintenance - Mechanical Parts of Refrigeration System - Record keeping and reporting Practical Activity: - Inspect Firing order & Report - Check & replace Defective parts | Theory-1Hrs. Practical-5 Hrs. Total- 6 Hrs. | - Personal Protective Equipment - Basic tool Kit | Class Room and workshop |
| - Prepare Sequence for Chillers Piping Preventive Maintenance for Right Operation. | Trainee will be able to: - Inspect and brush to clean evaporator, absorber & Maintenance condenser tubes - Inspect and brush to clean evaporator, water Heat Exchanger Chamber & tubes. - Inspect absorber and condenser tubes (after brush cleaning) for Eddy current and boro scope - Inspect hot water heat exchanger tubes and gather requirements of Eddy current and boro scope - Check proper steam valve modulation and design steam entering / blocking situation. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Define air conditioning systems - Define absorption air conditioning system - Identification refrigerant contamination - Functions of pressure control switches - Functions of pressure Gas switches - Combustion analysis - Types of maintenance - Preventive maintenance - Understand Drawings - Knowladge of Materials used in System - Record keeping and reporting Practical Activity: - Prepare Maintenance Schedule for Piping - Check & replace Defective Pipes | Theory-1Hrs. Practical-5 Hrs. Total- 6 Hrs. | - Personal Protective Equipment - Basic tool Kit | Class Room and workshop |
| - Select Right Sequence for DFA Chillers Burners &Trains Operation. | Trainee will be able to: - Perform safety test - Spark Pick-Up - Test Power & Performance of burner fan air proving switch. - Check all Requirements of Combustion air Check to make sure that all sources remain clear and open to ensure safe operation. - Inspect for leakage through pilot and main solenoid or motorized valve(s) - Inspect for wear of main and pilot gas pressure regulators Combustion analysis ratios, combustion efficiency. - Perform test of high pressure and low-pressure gas switches - Inspection oil nozzle wear - Replace Fired Units / nozzle if necessary - Inspect for wear of oil solenoid and main oil modulating valve(s) to conduct performance test - Inspect oil pump unit with Checking for clogging of oil strainer and Leak test of piping (visual observation) - Determine and record oil consumption (Charts or Flow Meter) with performance test of oil pressure cutout switch (Refer to burner documentation) | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Define air conditioning systems - Define absorption air conditioning system - Identification refrigerant contamination - Functions of pressure control switches - Functions of pressure Gas switches - Combustion analysis - Types of maintenance - Preventive maintenance - Direct Fire Absorption (DFA) chillers - Prepare Maintenance schedules - Record keeping and reporting Practical Activity: - Check & Accurate Firing Orders - Write Report About Chiller | Theory-1Hrs. Practical-5 Hrs. Total- 6 Hrs. | - Personal Protective Equipment - Basic tool Kit | Class Room and workshop |

## Check and Inspect Air Washer System in Respect of Preventive Maintenance

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to check and inspect air washer system in respect of preventive maintenance in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding preventive maintenance of air washer system to provide you the basis for student work.

Duration:  20	Hours			                             Theory: 4	Hours				                  Practice: 	16 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Perform Preventive Maintenance of Chiller Operation | Trainee will be able to: - Check Visual Traces of Leakages on Water & Refrigerant Circuits with Sight Glass Level verifications. - Visual Traces of Oil Leakages, Sight Glass Level for Right Oil presence - Check Proper operation of oil return valve & its operation during cycle & at Part Load. - Check Sump Heater & its thermostat. Perform Water Analysis for Chilled & Condenser Side and to choose right water cleaning and softening skills. | - Hazards that are most likely to cause harm to health and safety with HVAC tools - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Air conditioning systems - Absorption air conditioning system - Identify refrigerant contamination - Functions of pressure control switches - Functions of pressure Gas switches - Combustion analysis - Types of maintenance - Preventive maintenance - Prepare Maintenance Schedule - State Sequence of Operation of chiller - Operation of Parts of Chiller - Record keeping and reporting Practical Activity: - Prepare schedule and log sheet | Theory-1Hrs. Practical-4 Hrs. Total- 5 Hrs. | - Personal Protective Equipment - Basic tool Kit - Bearing Puller - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU2. Perform Preventive Maintenance on Safety Control Performance | Trainee will be able to: - Check voltage across each electrical phase & check of any abnormality on Connection Tightness or Carbon Presence. - Check Chilled / Condenser Water Sensors & flow switches and its right values presentation on Interface Panel - Check Condenser Water Temperature& Flow Sensor / Switches and presentation on interface Panel. - Check High and Low Press. & Temp. Cutout Switches. - Adopt procedure for accuracy check of thermistors and transducers values with interface. - Adopt right Procedure for accuracy check of Condenser Pressure and Temperature Gauges - Perform Eddy current test and inspection of tubes with proper cleaning procedure implementation. | - Hazards that are most likely to cause harm to health and safety with HVAC tools - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Air conditioning systems - Absorption air conditioning system - Identify refrigerant contamination - Functions of pressure control switches - Functions of pressure Gas switches - Combustion analysis - Types of maintenance - Preventive maintenance - Direct Fire Absorption (DFA) chillers - Record keeping and reporting Practical Activity: - Observe system behavior - Replace Defective Parts | Theory-1Hrs. Practical-4 Hrs. Total- 5 Hrs. | - Personal Protective Equipment - Basic tool Kit - Bearing Puller - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU3. Perform Preventive Maintenance of Mechanical Parts & System | Trainee will be able to: - Inspect Main Bearing, Bolts and Seal wear - Inspect motor Margining & Tolerance Levels. - Adopt Correct Check for average skin temperatures of Compressor Motor & VFD Temperatures. - Check for operating amperage of Chiller on Full & Part Load Scenario. - Determine Oil Supply & Return Filter Clogging state & Replacement Procedure. - Inspect & Replace starter Coolant & Air Filters. - Check draining / Purge out Refrigerant and Oil for analysis & Lube Oil. - Perform different vibration Test for Motor, Bearing and Foundation to avoid abnormal sound & parts breaking. | - Working of Refrigeration System - Function of Different Parts of Refrigeration System - Maintenance Schedule Practical Activity: - Observe system behavior - Replace Defective Parts | Theory-1Hrs. Practical-4 Hrs. Total- 5 Hrs. | - Personal Protective Equipment - Basic tool Kit - Bearing Puller - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU4. Perform preventive Maintenance for Right Operation of HVACR system. | Trainee will be able to: - Inspect and brush clean evaporator, Condenser & Maintenance Heat Exchanger Baffles. - Inspect and brush clean evaporator, water Heat Exchanger Chamber & tubes. - Perform Eddy current and borescope tests on condenser tubes (after brush cleaning) - Check for different valve modulation and design flow entering / blocking situation | - Types of Maintenance - Preventive Maintenance - Basic Operation of Refrigeration Sysytem - Calibration of Measuring Instruments - Function of Different Parts of HVACR Systems Practical Activity: - Observe system behavior & Report - Replace Defective Parts | Theory-1Hrs. Practical-4 Hrs. Total- 5 Hrs. | - Personal Protective Equipment - Basic tool Kit - Bearing Puller - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |

## Check and Inspect Central Air Conditioning system

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to check and inspect central air conditioning system in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding checking and inspecting of central air conditioning system to provide you the basis for student work.

Duration:  20	Hours			                             Theory: 5	Hours				                  Practice: 	15 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify the central Air conditioning system for operation / maintenance | Trainee will be able to: - Check electrical source of supply and supply being within the requirements. - Check and ensure availability of continuous supply of good quality of water to the cooling tower& expansion tank. - Check Cooling tower and water treatment systems and ensure their satisfactory performance - Check Water pumps, cooling towers and condensing units for their satisfactory performance and necessary adjustments done. - Check Compressor and change oil as specified by manufacturer - Clean, service and replace Electrical controls and panels, as necessary, according to instructions of manufacturer. - Check and ensure Control devices and safety devices for operational parameters - Record and interpret Chiller different readings | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Different types of electric motors - Working principles of different types of electric motors - Electric controls and panels - Pressure and pressure laws - Temperature and its units - Ohm meter, Voltmeter and Ampere meter use - Cooling tower and its types - Working principle of cooling tower - Control devices and safety devices for operational parameters - Pumps and its types - Compressors and function of compressors - Air purge valves - Fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Observe System Performance & Report it | Theory-2Hrs. Practical-5 Hrs. Total- 7 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device | Class Room and workshop |
| LU2. Start & operate the central chilled water air conditioning system | Trainee will be able to: - Follow operational manual and other operational guidelines provided by manufacturer for operating plant. - Check air purge valve and water level of cooling tower. - Start, check and ensure Cooling tower fans operation - Check attend unusual noises and ensure correct performance of cooling tower fans. - Start Condenser cooling water pumps, check their performance and carry out servicing / repairs as necessary - Start Chilled water pumps, check their performance and carry out servicing/or repairs as necessary. - Carry out necessary servicing of air side equipment - Check start up procedure and start chiller - Take and record temperature readings at all places of air-conditioned space. - Check main plant, take readings at regular intervals and record in operational log sheets - Shut down System as recommended by the manufacturer | - Operating Procedure - Sequance of Operation Practical Activity: - Read and understand drawings - Balancing the system (Air / Water) - Observe system behavior | Theory-2 Hrs. Practical-5 Hrs. Total- 7 Hrs. | - • Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device | Class Room and workshop |
| LU3. Start & operate the chilled water central air conditioning system (with air cooled condenser) | Trainee will be able to: - Provide and interpret instructions on starting operations and other operational guidelines provided by manufacturer. - Follow steps outlined in manufacturer’s guidelines for starting and operating unit as specified. - Start condenser fans, and check their performance to ensure proper performance - Check and inform abnormal noises and vibrations in condenser fans - Start chilled water pumps, check their performance and carry out servicing / or repairs as necessary. - Carry out necessary servicing of air side equipment for correct operational parameters - Take and record temperature readings at all places of air-conditioned space. - Check main plant, take readings at regular intervals and record in operational log sheets - Pump down / stop system as recommended by the manufacture. | - Operation of Chiller - Function of Condenser Practical Activity: - Check compressor and pumps - Check & Inspect piping arrangement - Check flow of secondary refrigerant Replace filters and belts | Theory-1Hrs. Practical-5 Hrs. Total- 6 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device | Class Room and workshop |

## Install and Commission Ammonia Refrigeration System, Components & Accessories

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to install and commission ammonia refrigeration system components & accessories in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding installation and commissioning of ammonia refrigeration system to provide you the basis for student work.

Duration:  30	Hours			                             Theory: 6	Hours				                  Practice: 	24 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare to install and commission Ammonia refrigeration systems | Trainee will be able to: - Identify and obtain OHS procedures for a given work area through established routines and procedures - Follow established OHS risk control measures and procedures in preparation for the work. - Seek advice on risk control measures from the project engineer for safety hazards which have not previously been identified - Obtain the nature of work from documentation or from project engineer to establish the scope of work to be undertaken. - Seek advice from the project engineer to ensure the work is coordinated effectively with others. - Access sources of material that may be required for the work in accordance with established routines and procedures. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration, And Air Conditioning Engineers (ASHRAE) - Different types of electric motors - Working principles of different types of electric motors - Pressure, Temperature and its units - Ohm meter, Voltmeter and Ampere meter use - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Cooling tower and its types - Working principle of cooling tower - Control devices and safety devices for operational parameters - Pumps and its types - Compressors and function of compressors - Air purge valves - Fans and its types - Vibration and abnormal noises of electrical devices and machinery - Reading of Installation Drawings - Safety measures of Ammonia - Record keeping and reporting Practical Activity: - Understand system drawing - Observe installation Techniques & Report it | Theory-2 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU2. Install and Commission Ammonia refrigeration systems. | Trainee will be able to: - Follow established OHS risk control measures and procedures for carrying out the work. - Conduct measuring system operating parameters in strict accordance with OHS requirements and established safety procedures - Install major components and pipe work in compliance with all applicable Standards, Codes and Regulations - Conduct pressure testing at a pressure compatible with Ammonia and in accordance with applicable standards - Take precautions to prevent damage to components while pressure testing the system - Locate and rectify Leaks using testing methods appropriate to the system and in accordance with industry practice - Evacuate system in accordance with industry practices. - Charge system safely with Ammonia and lubricants in accordance with industry practices - Carry out preoperational on all operating and safety controls. - Commission system and make all adjustments to operating and safety controls. - Adjust and setting to all refrigerant flow metering devices and level control devices. - Take caution with temperature reduction of cool rooms and freezers. - Reduce temperatures in accordance with industry practices - Carry out maintenance procedures which include inspection and cleaning of all strainers, filters and collection of oil sample for analysis - Give training to personnel responsible for the operation and maintenance of the refrigeration system. | - Installation Techniques - Safety Measures Practical Activity: - Install components according to specification | Theory-2 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU3. Develop report on installation and commissioning of Ammonia refrigeration systems | Trainee will be able to: - Clean and make safe work site in accordance with established procedures. - Deal with contaminated refrigerant and lubricant in accordance with legislative/regulatory requirements - Document operational conditions and commissioning figures, including identification of any parameter that is not within the specified range for the system. - Mark all mechanical and electrical documentation to be "As Installed" | - Installation Plan - Report Writing - Record Keeping Practical Activity: - Understand system drawing - Install components according to specification - Operate HVAC system in order - Measure pressure and temperature of system - Observe system behavior | Theory-2 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |

## Check and Inspect HVAC Variable Refrigerant Flow (VRF) System

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to check and inspect HVAC variable refrigerant flow system in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding checking and inspection of HVAC VRF to provide you the basis for student work.

Duration:  30	Hours			                             Theory: 6	Hours				                  Practice: 	24 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Install Variable Refrigerant System & Allied Schemes. | Trainee will be able to: - Select tools, equipment and related accessories according to job requirements - Mark the location on the site where system to be installed according to Unit Size & Design Drawings meeting all design specifications and client on site requirements. - Make wall / slab opening at the marked area on the wall or floors for this installation fixtures. - Fix pipe runners & conduits in the opening and at entire area meeting drawing route - Install Copper, PVC & Electrical accessories with Proper Insulation according to the instructional manual and standards - Install the Indoor / Outdoor in the framed opening with standard slope so that condensate water drops outside. - Cover / Seal wall, Slab, ceiling to cover air gaps of opening with insulation material. - Fix the fancy decorative grills around the indoor grill as per manufacturer direction - Check leaks by applying pressure method before the joint’s insulation; repair leaks, if any | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Read & understand appropriate Copper Pipe sizes & distributors placement to meet system selection through record of shop drawings. - Select tools, equipment and related accessories according to job requirements - Pressure, Temperature and its units - Ohm meter, Voltmeter and Ampere meter use - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - VRF and explain its advantages and disadvantages - Working principle of cooling tower - Control devices and safety devices for operational parameters - Pumps and its types - Compressors and function of compressors - Air purge valves - Fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Find leaks & repair it | Theory-2 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU2. Perform Mandatory Action for Installation of Variable Refrigerant System. | Trainee will be able to: - Plan drain routes & Fix the indoor unit’s condensate drainpipe maintaining levels and put into main drain line firmly with provision of Air Vents. - Arrange power supply with circuit breaker near the Indoor Unit - make sure that all packing materials - Sheets, Styrofoam, Tape and Plastic Film, have been removed from the site after installation - Place Outdoor Unit on Civil Foundations and Bolt it properly - Interconnect Pre-Nitrogen Purged Copper Pipes & Communication between indoor & outdoor Units - Connect Main Power with outdoor units with matching circuit breakers and other safeties to energize outdoor units. - Purge the overall System, Make deep Vacuum for 24-hrs and check for any leakages or vacuum break. Make Controls energize and do jumper setting as per manufacturer instruction. - Switch on the system Heater and after 24 hrs. Turn on Compressor & Indoor Units and check system performance as per capacity and specifications. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Read & understand appropriate Copper Pipe sizes & distributors placement to meet system selection through record of shop drawings. - Select tools, equipment and related accessories according to job requirements - Pressure, Temperature and its units - Ohm meter, Voltmeter and Ampere meter use - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - VRF and explain its advantages and disadvantages - Working principle of cooling tower - Control devices and safety devices for operational parameters - Pumps and its types - Compressors and function of compressors - Air purge valves - Fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Install Piping - Install Indoor Units | Theory-2 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU3. Perform Corrective & Preventive Maintenance for Equipment, Safety Control with Right Performance outputs. | Trainee will be able to: - Check component or system condition, causing the problem - Ensure the procedure of right voltage supply across each electrical phase & check any abnormality on Connection Tightness or Carbon Presence on contacts. - Check capability of evaporator / condenser ambient sensors & switches and its right values through diagnostic tool at Interface Panel - Check condenser fan flow sensor / switches and to rectify and false error code. Check high and low pressure & temperature cutout switches. - Adopt procedure for accuracy check of thermistors and transducers values with ambient Temperature& communication with Main Panel. - Adopt right procedure for accuracy check of condenser & evaporators side pressure and temperature sensors. - Perform indoor / outdoor tubes & fins combing and periodic cleaning with proper procedure implementation - Conduct checking of programmable operating set points and safety cutouts and assure and assure their correction through outdoor main board for the application - Arrange OEM drawings and manuals for the subject equipment to be attended for diagnosing the fault - Isolate and detail check of the causes of the problem and correct the fault & Start the system to recheck as specified in the manufacturer manual and record the results. - Record & collect daily System operational logs to report any abnormal temperature and system behaviors to implement preventive inspection. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Read & understand appropriate Copper Pipe sizes & distributors placement to meet system selection through record of shop drawings. - Select tools, equipment and related accessories according to job requirements - Pressure, Temperature and its units - Ohm meter, Voltmeter and Ampere meter use - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - VRF and explain its advantages and disadvantages - Working principle of cooling tower - Control devices and safety devices for operational parameters - Pumps and its types - Compressors and function of compressors - Air purge valves - Fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Find leaks & repair it - Check & replace controls - Check & replace mechanical parts - Operate electronic circuit | Theory-2 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |

## Check and Inspect Centrifugal HVAC system

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to centrifugal HVAC system in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding checking and inspection of centrifugal HVAC system to provide you the basis for student work.

Duration:  20	Hours			                             Theory: 8	Hours				                  Practice: 	12 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Check and Inspect Chiller Operation | Trainee will be able to: - Check Visual Traces of Leakages on Water &Refrigerant Circuits with Sight Glass Level verifications. - Check Visual Traces of Oil Leakages, Sight Glass Level for Right Oil presence - Check Proper operation oil return valve & its operation during cycle & at Part Load - Check Sump Heater & its thermostat - Perform Water Analysis for Chilled & Condenser Side and to choose right water cleaning and softening skills. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Types of HVACR Chillers - Centrifugal Chiller - Installation Techniques - Study of Drawings - Preapration for Installation Practical Activity: - Find leaks & repair it - Check & replace controls | Theory-2 Hrs. Practical-4 Hrs. Total- 6 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU2. Check and Inspect Safety Control | Trainee will be able to: - Perform procedure for assessment of right voltage across each electrical phase & check of any abnormality on Connection Tightness or Carbon Presence. - Perform procedure to check Chilled / Condenser Water Sensors & flow Switches and its right values presentation on Interface Panel - Perform procedure to check Condenser Water Temperature& Flow Sensor / Switches and presentation on interface Panel - Perform procedure to check High and Low Press. & Temp. Cutout Switches. - Perform procedure adoption for accuracy check of thermistors and transducers values with interface. - Adopt Right Procedure for accuracy check of Condenser Pressure and Temperature Gauges - Perform eddy current test and inspection of tubes with proper cleaning procedure implementation. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - Study of Installation plan - Record keeping and reporting Practical Activity: - Check & replace Defective Control | Theory-2 Hrs. Practical-4 Hrs. Total- 6 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU3. Check and Inspect Mechanical Parts & System | Trainee will be able to: - Inspect Main Bearing, Bolts and Seal wear. - Inspect motor Margin& Tolerance Levels. - Adopt Correct Check for average skin temperatures of Compressor Motor & VFD Temperatures. - Check for operating amperage of Chiller on Full & Part Load Scenario. - Perform procedure to Determine Oil Supply & Return Filter Clogging state &Replacement Procedure. - Implement accuracy to inspect & Replace starter Coolant& Air Filters. - Analyze o draining / Purge our Refrigerant and Lube Oil Checkups. - Perform different vibration Test for Motor, Bearing and Foundation to avoid abnormal sound & parts breaking. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - Checking and repairing of main bearings, bolts and seal wear - Different types of electric motors - Working principles of different types of electric motors - Pressure, Temperature and its units - Ohm meter, Voltmeter and Ampere meter use - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Pumps and its types - Compressors and function of Screw compressor - Air purge valves - Fans and its types - Vibration and abnormal noises of electrical devices and machinery - Prepare Maintenance Plan - Record keeping and reporting Practical Activity: Check & adjust centrifugal pumps | Theory-2 Hrs. Practical-2 Hrs. Total- 4 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU4. Check and Inspect Chillers Piping | - Inspect and brush clean evaporator, Condenser & Maintenance Heat Exchanger Baffles. - Inspect and brush clean evaporator, water Heat Exchanger Chamber & tubes. - Inspect condenser tubes (after brush cleaning) - Check for proper different valve modulation. and design flow entering / blocking situation | - Types of Maintenance Practical Activity: - Service Condenser - Service Evaporator | Theory-2 Hrs. Practical-2Hrs. Total- 4 Hrs. |  |  |

## Check and Inspect Screw Type HVAC system

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to check and inspect screw type HVAC system in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding checking and inspection of screw type HVAC system to provide you the basis for student work.

Duration:  20	Hours			                             Theory: 8	Hours				                  Practice: 	12 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Check and Inspect Chiller Operation | Trainee will be able to: - Check Leakages on water & refrigerant circuits with sight glass level verifications. - Check oil leakages, sight glass level for right oil presence - Check Up for Proper operation oil returns valve & its operation - Check Sump Heater & its thermostat. - Perform water analysis for chilled & condenser side. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Checking and repairing of main bearings, bolts and seal wear - Different types of electric motors - Working principles of different types of electric motors - Pressure, Temperature and its units - Ohm meter, Voltmeter and Ampere meter use - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Pumps and its types - Compressors and function of Screw compressor - Air purge valves - Fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Find leaks & repair it - Check & replace controls - Check & replace mechanical parts - Check & adjust centrifugal pumps | Theory-2 Hrs. Practical-2 Hrs. Total- 4 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU2. Check and Inspect Chiller Equipment and Safety Controls | Trainee will be able to: - Procedure for assessment of right voltage across each electrical phase & check of any abnormality on Connection Tightness or Carbon Presence. - Procedure to check Chilled / Condenser Water Sensors & flow switches and its right values presentation on Interface Panel. - Procedure to check Condenser Water Temperature& Flow Sensor / Switches and presentation on interface Panel. - Procedure to check High and Low Press. &Temp. Cutout Switches. - Procedure adoption for accuracy check of thermistors and transducers values with interface. - Adoption of Right Procedure for accuracy check of Condenser Pressure and Temperature Gauges. - Ability to perform eddy current test and inspection of tubes with proper cleaning procedure implementation. - Ability to do Checking Programmable Operating Set points and Safety Cutouts. Assure they are correct and viewable through interface for the application. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Checking and repairing of main bearings, bolts and seal wear - Different types of electric motors - Working principles of different types of electric motors - Pressure, Temperature and its units - Ohm meter, Voltmeter and Ampere meter use - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Pumps and its types - Compressors and function of Screw compressor - Air purge valves - Fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Check & Replace Defective Control | Theory-2 Hrs. Practical-2 Hrs. Total- 4 Hrs | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU3. Check and Inspect Chiller Mechanical Parts & System | Trainee will be able to: - Inspect Main Bearing, Bolts and Seal wear, repair / replace if necessary - Inspect and Check Superheat on the Evaporator and the Economizer feed to the Compressor and sub cooling on condenser part. - Correct Check for average skin temperatures of Compressor Motor & VFD Temperatures. - Check operating amperage of Chiller on Full & Part Load Scenario. - Determine Oil Supply & Return Filter Clogging state &Replacement Procedure. - Inspect starter, coolant & air filters replace if necessary. - Analyze draining / Purging, Refrigerant and lubrication oil checkups. - Perform different vibration Test for Motor, Bearing and Foundation to avoid abnormal sound & parts breaking. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Checking and repairing of main bearings, bolts and seal wear - Different types of electric motors - Working principles of different types of electric motors - Pressure, Temperature and its units - Ohm meter, Voltmeter and Ampere meter use - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Pumps and its types - Compressors and function of Screw compressor - Air purge valves - Fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Observe System Performance & Report | Theory-2 Hrs. Practical-4 Hrs. Total- 6 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU4. Check and Inspect Screw Chillers Operation | Trainee will be able to: - Inspect and clean evaporator, Condenser & Maintenance Heat Exchanger Baffles. - Inspect and clean evaporator, water Heat Exchanger Chamber & tubes. - Inspect condenser tubes after brushing / cleaning - Check different valve modulation and design flow entering / blocking situation. P5. Check Glycol concentration on Low Temp or other applications where freezing may be a problem & Change of VSD Glycols. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Checking and repairing of main bearings, bolts and seal wear - Different types of electric motors - Working principles of different types of electric motors - Pressure, Temperature and its units - Ohm meter, Voltmeter and Ampere meter use - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Pumps and its types - Compressors and function of Screw compressor - Air purge valves - Fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Find leaks & repair it - Check & replace controls - Check & replace mechanical parts - Check & adjust centrifugal pumps | Theory-2 Hrs. Practical-4 Hrs. Total- 6 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |

## Install, Maintain and Repair Industrial Refrigeration System

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to install, maintain and repair industrial refrigeration system in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding installation, maintenance and repair industrial refrigeration system to provide you the basis for student work.

Duration:  30	Hours			                             Theory: 6	Hours				                  Practice: 	24 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify the selected design of industrial refrigeration system. | Trainee will be able to: - Identify location as per the design. - Select specifications system, check to ensure matching with selected design of the unit. - Prepare a list of equipment / items and material required for the job. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - Identify Different Refrigeration Systems - Explain Working of Refrigeration System - Different types of electric motors - Working principles of different types of electric motors - Refrigeration and its types - Industrial refrigeration - Record keeping and reportingPractical Activity: - Read and understand drawings | Theory-2 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU2. Install industrial refrigeration system | Trainee will be able to: - Select components of system according to requirements for the installation. - Prepare and level floor to install industrial refrigeration system according to layout plans. - Install industrial refrigeration system according to specifications, following manufacturer’s specification. - Install refrigeration equipment including piping & electrical wiring following standard practices and safety procedures. - Check and test system before commissioning, as per specifications and manufacturer’s instructions, and under the supervision of the engineer. - Record commissioning data indicating system pressures, electrical data, humidity &temperatures outside and inside cold room, and filed for future use. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - Installation Techniques - Introduction to Different Refrigeration Systems - Pressure, Temperature Values and their units - Ohm meter, Voltmeter and Ampere meter use - Commissioning process - Refrigeration and its types - Industrial refrigeration - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Pumps and its types - Compressors and functions of compressors - Air purge valves - Fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Read and understand drawings - Make foundations and hangers - Install components of refrigeration system - Install plumbing assembly Chilled Water Tank, condenser and cooling tower - Make water drain connections - Install anti freezing/defrosting and water level protection system | Theory-2 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU3. Maintain / repair industrial refrigeration system. | Trainee will be able to: - Check cold room / freezer room / ice plant and extent of repair / or maintenance ascertained and recorded. - Enlist equipment / items, material and accessories as required for the job. - Check all components of the electrical / electronic circuits according to standard practice and manufacturers specifications to ensure correct performance and rectify defects. - Check and ensure performance of electro - mechanical safety and control devices according to manufacturer’s specifications. - Check for correct performance of all mechanical devices such as drive belts etc. according to manufacturer’s specifications - Check and rectify defects for correct performance of all components of the refrigeration circuit according to manufacturer’s specifications. - Check defrost heaters, drain line, Pan heaters, fan delays, defrost timers, defrost termination devices and temperature controllers, replace where necessary to ensure proper functioning. - Check body mounts and restore to the required condition - Test system pressure, specified test instruments and repair gas leaks - Evacuate system by using vacuum pump and gas re-charge by weight using specified equipment according to specifications. - Check door heaters and door gaskets & door closers; repair where necessary to ensure proper functioning. - Check interior cooler space, cleaned and ensured dust / debris free. - Operate, check and test plant to ensure satisfactory performance according to manufacturer’s specifications. - Perform plant re-commissioning and handed over according to manufactures specifications observing following safety procedures, under the supervision of the superior and recorded readings / data obtained during commissioning of the plant and check against manufacturers specifications. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - Observe maintenance Schedule - Checking and repairing of main bearings, bolts and seal wear - Different types of electric motors - Working principles of different types of electric motors - Pressure, Temperature and its units - Ohm meter, Voltmeter and Ampere meter use - Commissioning process - Refrigeration and its types - Industrial refrigeration - Refrigerants and properties of refrigerants - Filters, strainers and lubrication oils - Working principle of cooling tower - Control devices and safety devices for operational parameters - Pumps and its types - Compressors and functions of compressors - Air purge valves - Fans and its types - Vibration and abnormal noises of electrical devices and machinery - Use of Different HVACR Tools - Record keeping and reporting Practical Activity: - Fault finding & Trouble shooting - Leak testing & Charge refrigerant in refrigeration system - Replace different parts | Theory-2 Hrs. Practical-8 Hrs. Total- 10 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |

## Service and Maintain Air Handling Unit (AHU)

Objective: This module covers the knowledge and  skills required to this learning module is designed to provide skills and knowledge to service and maintain air handling units in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding servicing and maintenance of air handling units to provide you the basis for student work.

Duration:  20	Hours			                             Theory: 8	Hours				                  Practice: 	12 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare for work. | Trainee will be able to: - Observe safe work practices and personal protective equipment (PPE) worn as required for the work to be performed. - Interpret work instructions to determine job requirements - Identify necessary tools and equipment in line with job requirements - Select necessary materials as per job requirement | - Hazards that are most likely to cause harm to health and safety with HVAC tools - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Air conditioning systems - Absorption air conditioning system - State Sequqnce of Operation of Chiller - Prepare Maintenance Schedule Practical Activity: - Check & Visually inspect AHU | Theory-2 Hrs. Practical-2 Hrs. Total- 4 Hrs . | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU2. Check and Identify faults | Trainee will be able to: - Observed systematic test and check in accordance with manufacturer’s instruction. - Check components of the Air-flow system according to manufactures specifications to ensure correct performance - Check booster fan and rotary fan performance according to the instruction - Check control settings/adjustments in conformity with service-manual specifications. - Check components of refrigeration and electrical / electronic circuit according to standard procedures - Identify system defects/fault symptoms and document using appropriate tools and equipment | - Hazards that are most likely to cause harm to health and safety with HVAC tools - Identification and use of Personal Protective Equipment (PPE) - Observe Maintenance Schedule - State Operation of all parts & Controls - Analyze Working of different parts of chiller & Control - Record keeping and reporting Practical Activity: - Check Complete Working of AHU | Theory-2 Hrs. Practical-2 Hrs. Total- 4 Hrs . | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU3. Service / Maintain of Cassette type air conditioner | Trainee will be able to: - Replace defective parts/components with identical or recommended appropriate equivalent ratings - Control settings/adjustments are performing conformity with service-manual specifications - Clean air filter and evaporator/cooling coil fins with specified cleaning agent - Perform ducting and fabrication conformity with the drawing - Check pressure control switch, pressure gauge and temperature - Operate and check unit to ensure satisfactory performance according to manufactures specifications | - Hazards that are most likely to cause harm to health and safety with HVAC tools - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Air conditioning systems - Absorption air conditioning system - Types of maintenance - Preventive maintenance - Prepare Maintenance schedule - Observe maintenance schedule - Perform Maintenance - Record keeping and reporting Practical Activity: - Replace filters - Calculate air flow rate - Calculate the temperature and flow of refrigerant | Theory-2 Hrs. Practical-4 Hrs. Total- 6 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |
| LU4. Clean and store of tools and equipment | Trainee will be able to: - Maintain a Clean tools and equipment as per instruction manual - Clean workplace in accordance with environmental requirement - Store tools and equipment safely in appropriate location according to standard workshop procedures. | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Checking and repairing of main bearings, bolts and seal wear - Different types of electric motors - Working principles of different types of electric motors - Pressure, Temperature and its units - Ohm meter, Voltmeter and Ampere meter use - Air Handling Units - Filters, its types and their properties - Working principle of cooling tower - Fans and their working principles - Ducting systems - Insulations and their properties - Control devices and safety devices for operational parameters - Pumps and its types - Compressors and function of Screw compressor - Air purge valves - Fans and its types - Vibration and abnormal noises of electrical devices and machinery - Record keeping and reporting Practical Activity: - Store Tools & Relevant Material | Theory-2 Hrs. Practical-4 Hrs. Total- 6 Hrs. | - Personal Protective Equipment - Basic tool Kit - db. meter - Digital Air Flow / Velocity Meter - Digital Optical Tachometer - Electronic Leak Detector - Laser Distance Measuring Device - Laser Temperature Measuring Device - Megohmmeter (0 - 1000 Volts) - Digital Capacitor Analyzer | Class Room and workshop |

## Check and Connect Basic Controls used in HVAC

Objective: This module covers the knowledge and  skills required to this learning module is designed to check and connect basic controls used in HVAC system in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding checking and connecting basic HVAC controls for HVAC system to provide you the basis for student work.

Duration:  30 Hours			Theory: 6 Hours			Practice: 24 Hours          	        Credit Hours:  3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify purpose of controls | Trainee will be able to: - Identify types of controls - Categorize interlocking system of control - Identify Sign and symbols - Identify term and abbreviations - Interpret specifications | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) Practical Activity: - Adjust AVO meter | Theory-1 Hrs Practical- 3 Hrs Total- 7 Hrs | - Personal Protective Equipment | Class room & Lab |
| LU2. Perform checking methods | Trainee will be able to: - Check calibration of calibration instruments - Apply relevant suitable conditions - Check results of controls - Compare results with normal conditions - Elaborate faulty controls | - American Society of Heating, Refrigeration, And Air Conditioning Engineers (ASHRAE) Practical Activity: - Observe behavior of different controls - Make necessary connections | Theory- 3Hrs Practical- 9 Hrs Total-12 Hrs | - Basic tool Kit | Class room & Lab |
| LU3.Perform connections of control | Trainee will be able to: - Collect and interpret drawings - Make necessary connections - Align sensor of controls - Check the function of devices and control - Check & Justify all the connections - Test the function of circuit | - Identification of HVAC Controls - Working principles of HVAC Control - Repair and maintenance of HVAC controls - Interpret the control circuits diagrams Practical Activity: - Apply relevant conditions of pressure & Temperature - Obtain end results | Theory- 2 Hrs Practical- 9 Hrs Total- 11 Hrs | - Different type of HVAC Controls | Class room & Lab |

## Prepare Control Circuits

Objective: This module covers the knowledge and  skills required to this learning module is designed to prepare control circuits for HVAC system in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding control circuits preparation to provide you the basis for student work.

Duration:  30 Hours			Theory: 6 Hours			Practice: 24 Hours          	        Credit Hours:  3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Interpret drawings and Specifications | Trainee will be able to: - Collect drawings - Interpreted drawings - Identify Sign and symbols - Identify term and abbreviations - Interpret specifications | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration, And Air Conditioning Engineers (ASHRAE) Practical Activity: - Use PPE for electric works - Identify & Draw circuit drawings - Make wiring circuit | Theory- 2 Hrs Practical- 6 Hrs Total-8 Hrs | - Personal Protective Equipment | Class room & Lab |
| LU2. Connect Direct online starter, controls and accessories | Trainee will be able to: - Identify and collect Tools, Equipment and Materials - Check Tools, Equipment and Materials - Connect Direct online starter, controls and accessories | - Different types of electric motors - Working principles of different types of control circuits Practical Activity: - Install & Connect components | Theory- 1 Hrs Practical- 6 Hrs Total- 7 Hrs | - Basic tool Kit | Class room & Lab |
| LU3. Connect Star-delta starter | Trainee will be able to: - Collect and interpret Star-delta starter - Make Star connections - Make delta connection - Connect Star-delta starter - Connect Auto-transformer starter | - Different types of controls - Interpret circuit diagrams Practical Activity: - Perform connection of delta starter | Theory- 1 Hrs Practical- 3 Hrs Total- 4 Hrs | - Basic tool Kit | Class room & Lab |
| LU4. Check and test circuit | Trainee will be able to: - Check & Justify all the connections of each starter, control and accessory - Test & check connection between motor and starters | - Pressure and pressure laws - Temperature and its units - Ohm meter, Voltmeter and Ampere meter - Record keeping and reporting Practical Activity: - Check & Test circuit | Theory- 1 Hrs Practical- 3 Hrs Total- 4 Hrs | - Different type of HVAC Controls | Class room & Lab |
| LU5. Clean the workplace | Trainee will be able to: - Clean tools and equipment - Dispose waste materials - Complete cleaning | - Workplace cleaning methodology and SOP’s Practical Activity: - Identify necessary steps involved in cleaning the workplace | Theory- 1 Hrs Practical- 6 Hrs Total- 7 Hrs | - Basic tool Kit | Class room & Lab |

## Measure Air Velocity

Objective: This module covers the knowledge and  skills required to this learning module is designed to measure air velocity in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding measuring of air velocity to provide you the basis for student work.

Duration:  10 Hours			Theory: 4 Hours			Practice: 6 Hours       	        Credit Hours:  1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify air flow equipment’s | Trainee will be able to: - Identify ducts - Identify fans and blowers - Identify dampers, grills and registers | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration, And Air Conditioning Engineers (ASHRAE) - Basic Knowledge of Terminology such as Air flow, pressure head, power, efficiency ESP, TSP, VP etc. Practical Activity: - Identify equipment for air flow | Theory-1 Hrs Practical- 3 Hrs Total- 4 Hrs | - Personal Protective Equipment - Basic tools kit - Velocity meter | Class room & Lab |
| LU2. Measure air velocity and pressure | Trainee will be able to: - Use of velocity & pressure measuring instruments - Use of capacitive based pressure sensors - Measure static and total pressure - Measure Pressure losses | - Describe air velocity - Functions of air velocity meters - Working principles and construction of centrifugal fans and recognize different Fan Types. Practical Activity: - Use of measuring instrument (Velocity Meter) | Theory- 1 Hrs Practical- 3 Hrs Total- 4 Hrs | - Personal Protective Equipment - Basic tools kit - Velocity meter | Class room & Lab |
| LU3. Calculation of air velocity and pressure | Trainee will be able to: - Calculate cross sectional area of duct - Calculate pressure losses - Calculate flow rate of air (CFM) - Use of tables and charts - Calculation of air velocity - Accuracy of measured air velocity | - Measurement of air velocity by velocity meters - Different types of electric motors - Significance of Fan Laws Practical Activity: - Calculate air velocity and pressure | Theory- 2 Hrs Practical- 0 Hrs Total- 2 Hrs | - Personal Protective Equipment - Basic tools kit Velocity meter | Class room & Lab |

## Produce HVAC Control System Drawings

Objective: This module covers the knowledge and  skills required to this learning module is designed to produce HVAC control system drawings in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding HVAC control system drawings to provide you the basis for student work.

Duration:  30 Hours			Theory: 12 Hours			Practice: 18 Hours       	        Credit Hours:  3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Initiate control system drawings | Trainee will be able to: - Enlist equipment’s used in circuit - Draw universal symbols - Identify color coding of wirings - Identify term and abbreviations | - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration, And Air Conditioning Engineers (ASHRAE) - Interpretation of drawings, symbols, cable number according to load - Describe different types of drawings (e.g. power, control, single line etc.) - Terms being used in drawing - Draw application of drawing forms - Draw scales used in drawing Practical Activity: - Draw control system drawing | Theory- 6 Hrs Practical- 9 Hrs Total- 15 Hrs | - Computer with Accessories and CAD software | Class room & Lab |
| LU2. Draw control system drawings | Trainee will be able to: - Draw Relevant symbols of equipment’s - Make necessary connections - Use color coding of wires - Complete wiring diagram | - Draw fundamentals units i.e. arcs, circles and ellipse Draw single stroke and double stroke gothic letters - Definitions of tolerance, limits and fits - Layout and line drawing - Draw drawings by AutoCAD - Record keeping and reporting Practical Activity: - Draw relevant symbols - Use & understand color coding | Theory- 6 Hrs Practical- 9 Hrs Total- 15 Hrs | - Computer with Accessories and CAD software | Class room & Lab |

## Adjust and Balance HVAC Controls

Objective: This module covers the knowledge and  skills required to this learning module is designed to adjust and balance HVAC controls in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding adjustment and balancing of HVAC controls to provide you the basis for student work.

Duration:  20 Hours			Theory: 8 Hours			Practice: 12 Hours     	        Credit Hours:  2

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1.Testing of HVAC controls | Trainee will be able to: - Collect relevant data - Examine collected data - Measure and compare actual values - Identify controlled conditions | - Types of hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) - Identification of HVAC Controls Practical Activity: - Collect & compare relevant data of unit, | Theory- 2 Hrs Practical- 3 Hrs Total- 5 Hrs | - Personal Protective Equipment - Basic tools Kit - Air velocity meters - Air Balancing kit | Class room & Lab |
| LU2.Adjusting of HVAC controls | Trainee will be able to: - Ensure recorded data represents actual measured - Mark settings of control permanently - Make adjustment of relevant parameters and measure readings to verify - Leave the system in proper order - Inspect finally | - Working principles of HVAC Control - Repair and maintenance of HVAC controls Practical Activity: - Make comparison of data and Make necessary adjustments according data | Theory-3 Hrs Practical- 6 Hrs Total- 9 Hrs | - Basic tools Kit - Air velocity meters - Air Balancing kit | Class room & Lab |
| LU3.Balance of HVAC controls | Trainee will be able to: - Examine final test result with design values - Make necessary adjustments - Check set results - Finish adjusting if required desired conditions - Make necessary adjustment if required | - Interpret the control circuits diagrams - Record keeping and reporting Practical Activity: - Balance the control according feed back | Theory- 3 Hrs Practical- 3 Hrs Total- 6 Hrs | - Basic tools Kit - Air velocity meters - Air Balancing kit | Class room & Lab |

## Operate HVAC Building Management System (BMS)

Objective: This module covers the knowledge and  skills required to this learning module is designed to operate HVAC building management system in accordance with the manufacturer’s specifications / guidelines. This unit covers the knowledge regarding HVAC BMS to provide you the basis for student work.

Duration:  30 Hours			Theory: 12 Hours			Practice: 18 Hours       	        Credit Hours:  3

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify Direct Digital Control (DDC) | Trainee will be able to: - Identify the Basic Control System - Identify the Temperature, Rh, Pressure sensors and Input to Processor - Classify the DDC Control Applications - Identify the functions and application range of automatic control in air-conditioning and refrigeration systems. - Identify the Communication Standards / Protocols for DDC | - Hazards that are most likely to cause harm - Identification and use of Personal Protective Equipment (PPE) - American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) Practical Activity: - Understand basic control and communication system | Theory- 3 Hrs Practical- 3 Hrs Total- 6 Hrs | - Personal Protective Equipment - Basic tool Kit | Class room & Lab |
| LU2. Read and interpret Sequence of Operation | Trainee will be able to: - Read and Interpret the layout plan of automatic air-conditioning and refrigeration control system equipment. - Read and interpret the Sequence of Operation for Complete HVAC System - Read and interpret the Control Drawings in combination to sequence of operation. | - Digital direct control system - Building management system - Read and interpret the control drawings - Practical Activity: - Understand HVAC system working | Theory- 3 Hrs Practical- 3 Hrs Total- 6 Hrs | - Personal Protective - Equipment Basic tool Kit | Class room & Lab |
| LU3. Use BMS to Save Energy | Trainee will be able to: - Identify the BMS use to conserve energy. Understand the trends of Plants operation. - Read and interpret the alarms from BMS System - Read the performance logs of HVAC System from BMS | - Conservation of energy Practical Activity: - Service & Maintain BMS parts and accessories | Theory- 3 Hrs Practical- 6 Hrs Total- 9 Hrs | - Personal Protective Equipment - Basic tool Kit | Class room & Lab |
| LU4. Maintain and Operate BMS | Trainee will be able to: - Clean the Electrical Contacts and check any loose connections. - Remove the dust from control components. (Controllers, Cards, VFDs etc.) - Check control cable connectivity - Lubricate the actuator moving parts | - Function of the actuator - Record keeping and reporting Practical Activity: - Read and interpret different obtained parameters - Obtained desired comfort conditions in controlled environment | Theory- 3 Hrs Practical- 6 Hrs Total- 9 Hrs | - Personal Protective Equipment - Basic Tool Kit | Class room & Lab |

## Develop Entrepreneurial Skills

Objective:After the completion of this competency standard, the Trainee will be expected to develop a business plan, collect information regarding funding sources, develop a marketing plan and develop basic business communication skills. Trainee’ss underpinning knowledge regarding entrepreneurial skills will be sufficient to provide you the basis for your work.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Develop a business plan | Trainee will be able to: - Conduct a market survey to collect following information: - Customer /demand - Tools, equipment, machinery and furniture with rates - Raw material - Supplier - Credit / funding sources - Marketing strategy - Market trends - Overall expenses - Profit margin - Select the best option in terms of cost, service, quality, sales, profit margin, overall expenses - Compile the information collected through the market survey, in the business plan format | - Main elements of business plan - Filling the business plan format - Enlist specific business terms used in the industry - Describe 7Cs of business communication | Theory- 2 Hr Practical- Hrs Total- 2 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Collect information regarding funding sources | Trainee will be able to: - Identify the available funding sources based on their terms and conditions, maximum loan limit, payback time, interest rate - Choose the best available option according to investment requirement - Prepare documents according to the loan agreement requirement - Include the information of funding sources in the business plan | - Enlist the available funding sources - Explain how to get loan to start a new business - Explain market survey and its tools e.g.: questionnaire, interview, observation etc | Theory- 2 Hr Practical- Hrs Total- 2 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Develop a marketing plan | Trainee will be able to: - Make a marketing plan for the business including product, price, placement, promotion, people, packaging and positioning - Include the information of marketing plan in the business plan | - 7ps of marketing including product, price, placement, promotion, people, packaging and positioning | Theory- 3 Hr Practical- Hrs Total- 3 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Develop basic business communication skills | Trainee will be able to: - Communicate with internal customers e.g.: labor, partners and external customers e.g.: suppliers, customers etc., using effective communication skills - Use different modes of communication to communicate internally and externally e.g.: presentation, speaking, writing, listening, visual representation, reading etc. - Use specific business terms used in the market | - Description of the market trends for specific product offering - Different modes of communication and their application in the industry | Theory- 3 Hr Practical- Hrs Total- 3 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Apply project information management and communications techniques

Objective:After the completion of this competency standard, the Trainee will be able to contribute to communications planning, Conduct information management activities, Communicate project information, Contribute to assessing effectiveness of communication.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Contribute to communications planning | Trainee will be able to: - Identify, source and contribute relevant information requirements to initial project documentation. - Contribute to developing and implementing the project communications plan and communications networks. | - Outline methods of reviewing communication outcomes | Theory- 2 Hr Practical- Hrs Total- 2 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Conduct information management activities | Trainee will be able to: - Act on and process project information according to agreed procedures as directed, to aid decision-making processes throughout project life cycle. - Maintain information to ensure data is secure and auditable. | - Summarize models and methods of communications management in context of project life cycle and other project management functions | Theory- 2 Hr Practical- Hrs Total- 2 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Communicate project information | Trainee will be able to: - Communicate with clients and other stakeholders during project using agreed networks, processes and procedures to ensure flow of necessary information. - Ensure reports are prepared and released according to authorization, or produced for release by others. - Seek information and advice from appropriate project authorities as required. | - Identification of Project Information, policies and procedures relevant - Summarize models and methods of communications management in context of project life cycle and other project management functions | Theory- 3 Hr Practical- Hrs Total- 3 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Contribute to assessing effectiveness of communication | Trainee will be able to: - Assist in ongoing review of project outcomes to determine effectiveness of communications-management activities. - Report communications-management issues and responses to higher project authorities for application of lessons learned to future projects. | - Assessment of effectiveness of project communication | Theory- 3 Hr Practical- Hrs Total- 3 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Apply Project Human Resources Management Approaches

Objective:After the completion of this competency standard, the Trainee will be able to assist in determining human resource requirements, Contribute to establishing and maintaining productive team relationships, assist with human resource monitoring, contribute to evaluating human resource practices.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Assist in determining human resource requirements | Trainee will be able to: - Analyze work breakdown structure to determine human resource requirements. - Prepare a skills analysis of project personnel against project task requirements. - Assist in assigning responsibilities for achieving project deliverables. | - Identification of alternative project personnel engagement options - Requirements for human resources. | Theory- 2Hr Practical- Hrs Total- 2Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Contribute to establishing and maintaining productive team relationships | Trainee will be able to: - Actively seek views and opinions of team members during task planning and implementation. - Promote cooperation and effective activities, goals and relationships within team. - Communicate with others using styles and methods appropriate to organizational standards, group expectations and desired outcomes. - Communicate information and ideas to others in a logical, concise and understandable manner. - Regularly seek feedback on nature and quality of work relationships, and use feedback as basis for own improvement and development. | - Explain job design principles and work breakdown structures - Describe learning and development approaches that can be incorporated into project life cycle - Project team relationship building | Theory- 3 Hrs Practical- Hrs Total- 3 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Assist with human resource monitoring | Trainee will be able to: - Monitor work of project personnel against assigned roles and responsibilities within delegated authority levels. - Monitor and control actual effort against project plan. - Review skill levels against allocated tasks and recommend solutions, where required, to others. - Advise others within delegated authority when assigned responsibilities are not met by project personnel. - Undertake work in a multi-disciplinary environment according to established human resource management practices, plans, guidelines and procedures. - Resolve conflict within delegated authority according to agreed dispute-resolution processes. - Assist in offering human resource development opportunities to individuals with skill gaps. | - Listing of methods for skills analysis and monitoring - Identification and description of project roles, responsibilities and reporting | Theory- 2 Hr Practical- Hrs Total- 2Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Contribute to evaluating human resource practices | Trainee will be able to: - Contribute to assessing effectiveness of project human resources management. - Document lessons learned to support continuous improvement processes | - Knowledge of effective project human resources management - Improvement of project processes | Theory- 3 Hr Practical- Hrs Total- 3 Hr | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Direct Human Resources Management Of A Project Program

Objective:After the completion of this competency standard, the Trainee will be able to direct human resource organization and staffing
across a program, direct project managers in relation to staff performance, and to provide leadership within the program. It applies to individuals who are program managers, managing a suite of projects (a program).

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Direct human resources management planning | Trainee will be able to: - Direct stakeholder assessment to establish a basis for stakeholder management within projects and overall program. - Direct stakeholder assessment to establish a basis for stakeholder management within projects and overall program. - Direct responsibility assignment for project activities and tasks, and establish authorization protocols. | - Identification and learning of human resource management methods, techniques and tools | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Manage program organization and staffing | Trainee will be able to: - Determine resource requirements for projects in consultation with project managers and appropriate stakeholders, to establish program staffing levels, allocation to projects and required competencies. - Direct project organization and structure to optimize alignment of individual and group competencies within projects. - Direct recruitment of staff for allocation to projects or reallocation within the organization, within agreed delegated authority, to meet competency requirements throughout the program. - Direct project managers use of human resources management (HRM) methods, techniques and tools, and modify for program requirements. - Utilize organizational HRM system and HRM processes across projects | - Project resource requirement planning - Recruitment of project staff and its allocation within organization | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Direct project staff performance management | Trainee will be able to: - Obtain agreement on performance measurement criteria for clarity of roles and responsibilities and ongoing assessment - Ensure systems for ongoing development and training of personnel across the program are established and implemented by project managers. - Measure individual’s performance against agreed criteria and authorize actions to overcome shortfalls in performance and encourage career progression. | - Identification of relevant legislation - Describe models of performance management and performance development. | Theory- 3 Hrs Practical- Hrs Total- 3 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Provide overall leadership to project teams | Trainee will be able to: - Manage a system of continuous improvement of staff to enhance program effectiveness. - Analyze individual and team performance and morale levels and take action where necessary. - Direct procedures for interpersonal communication, counseling and conflict resolution by project managers, and review results to maintain and promote a positive working environment. - Identify and positively manage intra-organizational and intra-project conflict to maximize achievement of program objectives. - Aggregate HRM lessons learnt for application in planning and, where appropriate, pass on information to others for consideration in strategic planning and direction. | - Management of system for staff effectiveness - Assessment of team performances - Project conflicts and their management | Theory- 3 Hrs Practical- Hrs Total- 3 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Develop A Project Management Plan

Objective:After the completion of this competency standard, the Trainee will be able to develop a plan for a telecommunications project, including assessing project requirements and planning for all stages to completion and final documentation. It applies to individuals who are likely to have responsibility for the provision of installations, maintenance, upgrades and new services.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare project management plan | Trainee will be able to: - Evaluate and assess project brief and related documents. - Produce document on project tasks and associated timelines, including installation processes and test requirements. - Assess and produce document on resource requirements to assist allocation of appropriate resources. - Produce training plan assessing training needs and associated timelines for efficient project implementation. - Determine and document budgetary requirements. - Discuss roles of all identified parties associated with project to ensure their involvement. - Produce project verification document, including monitoring and control processes, and review processes such as quality audits. - Consult with all relevant parties prior to finalizing draft plan and make changes as appropriate. | - Preparation of Project Plans and their management - Evaluation and assessment of project related documentation and tasks - Project Budget preparation | Theory- 3 Hrs Practical- Hrs Total- 3 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Develop and evaluate management plan | Trainee will be able to: - Produce preliminary plan for consultation, including identified factors that may impact on realization of project and observance of relevant legislation, codes, regulation and standards. - Consult with client and clarify any amendments. - Develop final plan with recommendations. | - Development and evaluation of project management plans - Client dealing for clarification and amendments in project plans - Finalization of plans | Theory- 3 Hrs Practical- Hrs Total- 3 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Communicate project information | Trainee will be able to: - Produce and document final plan to include implementation details and training needs. - Present plan to client and obtain sign off. | - Presentation of Project plan to client | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Contribute to assessing effectiveness of communication | Trainee will be able to: - Assist in ongoing review of project outcomes to determine effectiveness of communications-management activities. - Report communications-management issues and responses to higher project authorities for application of lessons learned to future projects. | - Review of project outcomes and asses effectiveness of business communication | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Maintain Business Resources

Objective:After the completion of this competency standard, the Trainee will be able to determine, administer and maintain resources and equipment to complete a variety of tasks. It applies to individuals who are skilled operators and apply a broad range of competencies in various work contexts. They may exercise discretion and judgment using appropriate theoretical knowledge of business resources and their basic maintenance to provide technical advice and support to a team.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Advise on resource requirements | Trainee will be able to: - Calculate estimates of future and present business resource needs in accordance with organizational requirements - Ensure advice is clear, concise and relevant to achieve organizational requirements. - Provide information on the most economical and effective choice of equipment, materials and suppliers. - Identify resource shortages and possible impact on operations |  | Theory- 3 Hrs Practical- Hrs Total- 3 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Monitor resource usage and maintenance | Trainee will be able to: - Ensure resource handling is in accordance with established organizational requirements including occupational health and safety requirements. - Use business technology to monitor and identify the effective use of resources. - Use consultation with individuals and teams to facilitate effective decision making on the appropriate allocation of resources. - Identify and adhere to relevant policies regarding resource use in the performance of operational tasks. - Routinely monitor and compare resource usage with estimated requirements in budget plans |  | Theory- 3 Hrs Practical- Hrs Total- 3 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Acquire resources | Trainee will be able to: - Ensure acquisition and storage of resources is in accordance with organizational requirements, is cost effective, and consistent with organizational timelines. - Acquire resources within available timelines to meet identified requirements. - Review resource acquisition processes to identify improvements in future resource acquisitions |  | Theory- 4 Hrs Practical- Hrs Total- 4 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Develop A Sales Plan

Objective:After the completion of this competency standard, the Trainee will be able to develop a sales plan for a product or service for a team covering a specified sales territory based on strategic objectives and in accordance with established performance targets. It applies to individuals working in a supervisory or managerial sales role who develop a sales plan for a product or service.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify organizational strategic direction | Trainee will be able to: - Obtain and analyze assessment of market needs and strategic planning documents - Review previous sales performance and successful approaches to identify factors affecting performance - Analyze information on market needs, new opportunities, customer profiles and requirements as a basis for decision making | - Assessment of market needs and strategic planning documents preparation - Knowledge of business opportunities, customer profiles and decision making | Theory- 2Hrs Practical- Hrs Total- 2Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Establish performance targets | Trainee will be able to: - Determine practical and achievable sales targets - Establish realistic time lines for achieving targets - Determine measures to allow for monitoring of performance - Ensure objectives of the sales plan and style of the campaign are consistent with organizational strategic objectives and corporate image | - Statistical techniques for analyzing sales and market trends | Theory- 2Hrs Practical- Hrs Total- 2Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Develop a sales plan for a product | Trainee will be able to: - Determine approaches to be used to meet sales objectives - Identify additional expertise requirements and allocate budgetary resources accordingly - Identify risks and develop risk controls - Develop advertising and promotional strategy for product - Identify appropriate distribution channels for product - Prepare a budget for the sales plan - Present documented sales plan to appropriate personnel for approval | - Principles and techniques for selling Sources of internal and external information - Identification of organizational strategic direction and developing a product sales plan - Preparation of sales plan and its approval | Theory- 2Hrs Practical- Hrs Total- 2Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Identify support requirements | Trainee will be able to: - Identify and acquire staff resources to implement sales plan - Develop an appropriate selling approach - Train staff in the selling approach selected - Develop and assess staff knowledge of product to be sold | - Resources requirement for sales plan | Theory- 2Hrs Practical- Hrs Total- 2Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU5. Monitor and review sales plan | Trainee will be able to: - Monitor implementation of the sales plan - Record data measuring performance versus sales targets - Make adjustments to sales plan as required to ensure required results are obtained | - Principles, monitoring and techniques for selling Sources of internal and external information | Theory- 2Hrs Practical- Hrs Total- 2Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Plan And Implement Business-To-Business Marketing

Objective: After the completion of this competency standard, the Trainee will be able to plan and implement business-to-business (B2B)
marketing. It applies to individuals who work in a supervisory capacity in a team environment, who possess a sound theoretical knowledge base and demonstrate a range of managerial skills to ensure business activities are conducted effectively. In this role, individuals may work in small, medium or large enterprises across a variety of industries.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify and evaluate business -to-business marketing strategies | Trainee will be able to: - Identify B2B markets in an industry context - Research characteristics of business markets in an industry context - Identify and analyze factors influencing business buyers in an industry context - Analyze the business buying process and its implications in the industry context - Research and analyze a range of B2B marketing strategies appropriate for the organization - Identify key personnel in buying decision process in the organization s business markets | - Identification of Business to Business markets | Theory- 2Hrs Practical- Hrs Total- 2Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Select business-to business marketing strategies | Trainee will be able to: - Analyze trends within business markets and identify B2B marketing opportunities for the organization - Identify and analyze success of the organization s previous B2B marketing strategies - Select most appropriate B2B marketing strategies and activities that fit with organization s strategic & marketing plans | - Preparation of business to business strategies | Theory- 2Hrs Practical- Hrs Total- 2Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Plan and develop business-to-business marketing activities | Trainee will be able to: - Record B2B marketing objectives and purpose - Calculate costs of B2B marketing activities with assistance of appropriate personnel - Select methods to report and measure effectiveness of B2B marketing activities - Assign responsibilities to team members for B2B marketing activities - Record B2B marketing plan and present to relevant stakeholders - Assemble required resources to implement B2B marketing plan | - Plan the business to business strategies | Theory- 2Hrs Practical- Hrs Total- 2Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Implement and monitor business-to business marketing plan | Trainee will be able to: - Schedule work on each B2B marketing campaign element, according to lead times required and marketing plan - Brief staff and suppliers on their budgets, timelines, roles and responsibilities, and legal and ethical requirements - Plan implementation of B2B marketing activities according to marketing plan - Identify & use evaluation criteria and evaluation methods to determine effectiveness of marketing plan - Analyze success indictors of B2B marketing plan and record performance according to organizational reporting requirements | - Trends in B2B marketing, corporate sector and business sector and preparation of plans | Theory- 4Hrs Practical- Hrs Total- 4 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Address Customer Needs

Objective: After the completion of this competency standard, the Trainee will be able to manage an ongoing relationship with a customer
over a period of time. This includes helping customers articulate their needs and managing networks to ensure customer needs are addressed. It applies to individuals who are expected to have detailed product knowledge in order to recommend customized solutions. In this role, individuals would be expected to apply organizational procedures and be aware of, and apply as appropriate, broader factors involving ethics, industry practice and relevant government policies and regulations.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Assist customer to articulate needs | Trainee will be able to: - Ensure customer needs are fully explored, understood and agreed - Explain and match available services and products to customer needs - Identify and communicate rights and responsibilities of customers to the customer as appropriate | - Explain organizational procedures and standards for establishing and maintaining customer service relationships. - Explain consumer rights and responsibilities | Theory- 2Hrs Practical- Hrs Total- 2Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Satisfy complex customer needs | Trainee will be able to: - Explain possibilities for meeting customer needs - Assist customers to evaluate service and/or product options to satisfy their needs - Determine and prioritize preferred actions - Identify potential areas of difficulty in customer service delivery and take appropriate actions in a positive manner | - Describe ways to establish effective regular communication with customers - Variations within a limited product and service range. | Theory- 2Hrs Practical- Hrs Total- 2Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Manage networks to ensure customer needs are addressed | Trainee will be able to: - Establish effective regular communication with customers - Establish, maintain and expand relevant networks to ensure appropriate referral of customers to products and services from within and outside the organization - Ensure procedures are in place to ensure that decisions about targeting of customer services are based on up-to-date information about the customer and the products and services available - Ensure procedures are put in place to ensure that referrals are based on the matching of the assessment of customer needs and availability of products and services - Maintain records of customer interaction in accordance with organizational procedures | - Outline details of products or services including with reference to possible alternative products and services | Theory- 2Hrs Practical- Hrs Total- 2Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Convert customer enquiries into sales | Trainee will be able to: - Use information provided by customers or accessed from customer relationship management (CRM) system to identify any need - Identify suitable products /services to meet needs - Make convincing sales pitches to customers following standard scripts - Handle customer queries, objections and rebuttals following standard scripts - Adapt your approach and style to customer preferences, within limits of your competence and authority - Refer issues outside your area of competence and authority to appropriate people, following your organization’s procedures - Identify and act on opportunities to up-sell or cross-sell other products/services to customers - Confirm customer wishes and needs in order to close sales - Obtain required financial information from customers, following your organization’s procedures - Complete your organization’s post-sales procedures in order to complete/fulfill sales - Comply with relevant standards, policies, procedures and guidelines when converting customer enquiries into sales | - Organizational standards for maintaining customer relationships to convert convincing sales pitches to customers need | Theory- 4 Hrs Practical- Hrs Total- 4 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Manage Personal Finances

Objective: After the completion of this competency standard, the Trainee will be able to develop, implement and monitor a personal
budget in order to plan regular savings and manage debt effectively.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Develop a personal budget | Trainee will be able to: - Calculate current living expenses using available information to prepare a personal budget. - Keep a record of all income and expenses for a short period of time to help estimate ongoing expenses. - Subtract total expenses from total income to determine a surplus or deficit budget for the specified period. - Find reasons for a deficit budget and ways to reduce expenditure identified. - Identify ways to increase income, if possible | - Preparing cash flow statement - Basic concepts of Time value of money - Understanding of current and fixed assets - Understanding of elements of equity and liabilities (long term and short term) - Identification of available financial resources - Step by step budget plan preparation - Budget review techniques | Theory- 3 Hrs Practical- Hrs Total- 3 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Develop longer term personal budget | Trainee will be able to: - Analyze income and expenditure and set longer term personal, work and financial goals. - Develop a longer-term budget based on the outcomes of short-term budgeting, and adjust to meet living, work and future career requirements. - Identify obstacles that might affect finances such as job loss, sickness or unexpected expenses contingency savings - Formulate a regular savings plan based on budget, using secure savings products and services. - Monitor expenditure against budget and identify areas of possible expenditure saving | - Develop a personal budget based on analysis of expenditure and income - Monitor expenditure for a period of up to 2 weeks. | Theory- 3 Hrs Practical- Hrs Total- 3 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Identify ways to maximize future finances | Trainee will be able to: - Determine sources and ways to maximize personal income, including from work, investments or available government payments/allowances. - Get further education or training to maintain or improve future income. - Identify the need for debt to finance living and other expenses, and determine the appropriate levels of debt and repayment. - Consolidate existing debt, where possible, to minimize interest costs and fees. - Seek professional money management services, where available, to ensure financial plans are effective and achievable | - Formulate goals and identify financial contingency plans | Theory- 4 Hrs Practical- Hrs Total-4 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Solve Problems Which Jeopardize Safety And Security

Objective:After the completion of this competency standard, the Trainee will be able to understand the complex negotiation in critical incidents and the development of strategic responses designed to resolve threatening incidents.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify a problem | Trainee will be able to: - Form a problem statement and analyze root cause. - Take initiative in tackling problems rather than relying solely on directives - Follow logic steps in understanding root cause and analyzing potential solutions. | - Explain organization’s policies, guidelines and procedures related to control and surveillance, safety and preventing and responding to incidents and breaches of orders covered in the range of variables. | Theory- 2Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Determine strategies for a required solution | Trainee will be able to: - Analyze all aspects of the incident for degree of hazard, priorities, optional outcomes and appropriate strategies - Analyze and determine strategies and priorities on the incident sought from a range of sources - Assess long term objectives against resources and priorities - Apply a range of communication techniques to make and maintain contact with the key people - Provide clear and factual information to enable an honest and realistic assessment of the interests of the key people and their positions - Resolve the conflict and express their likely consequences clearly and do an analysis of the benefits - Reassess points of disagreements for common positive Positions | - A person who demonstrates competency in this unit must be able to provide evidence of the ability to resolve problems which jeopardize safety and security. | Theory- 2Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Coordinate support services | Trainee will be able to: - Assess the need for support services in terms of the determined strategies and priorities - Negotiate the resources of support services according to established procedures and availability - Provide information on strategies to support services and maintain the communication - Delegate roles and responsibilities according to expertise and resources | - Explain organization’s management and accountability systems - Outline the guidelines for use of equipment and technology - Explain code of conduct | Theory- 2Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Restore order | Trainee will be able to: - Assess the incidents for degree of risk and take appropriate action to reduce and remove the impact of the incident and restore order - Take action designed to minimize risk and the preserve the safety and security of all involved - Take action to prevent the escalation of the incident appropriate to the circumstances and agreed procedures. - Carry out the use of force for the restoration of control and the maintenance of security in the least restrictive manner. - Complete reports accurately and clearly provided to the appropriate authority promptly - Review, evaluate and analyze the incident and the organizational response to it and report it promptly and accurately. | - Describe teamwork principles and strategies - Outline the principles of effective communication | Theory- 2Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU5. Provide leadership. direction and guidance to the work group | Trainee will be able to: - Link between the function of the group and the goals of the organization - Participate in decision making routinely to develop, implement and review work of the group and to allocate responsibilities where appropriate - Give opportunities and encouragement to others to develop new and innovative work practices and strategies - Identify conflict and resolve with minimum disruption to work group function - Provide staff with the support and supervision necessary to perform work safely and without risk to health - Allocate tasks within the competence of staff and support with appropriate authority, autonomy and training - Supervise appropriately the changing priorities and situations and takes into account the different needs of individuals and the requirements of the task | - Integration of employability skills with workplace tasks and job roles - Verification of competency to be transferred to other circumstances and environments | Theory- 2Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Coordinate a Work Team

Objective:After the completion of this competency standard, the Trainee will be able to achieve operational outcomes and effective
working relationships through managing and developing individuals and teams.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Develop and maintain a cooperative work group | Trainee will be able to: - Work contributions and suggestions from staff are continually sought and encouraged - Contributions to work group operations are acknowledged and suggestions are dealt with constructively - Develop staff skills according to work requirements - Implement new work practices - Address conflict between staff members in accordance with current personnel practices. | - Explain the principles of effective team operation - Explain the principles of human resource management - Describe the training delivery processes in the workplace | Theory- 2Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Communicate objectives and required standards | Trainee will be able to: - Inform the staff of the objectives and standards required - Commit to objectives and standards - Practices of safe, fair and participative work principals are and promote to staff | - Ability to coordinate a work team - Evidence of integration of employability skills with workplace tasks and job roles | Theory- 2Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Provide feedback on performance | Trainee will be able to: - Give constructive feedback on all aspects of work performance provided to individuals and team - Access and address performance in a fair and timely manner in accordance with relevant guidelines, procedures and natural justice | - Outline the industry assessment guidelines | Theory- 2Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Support and participate in development activities | Trainee will be able to: - Assess training needs of all staff, implemented and promoted - Devise an action plan to meet individual and group training and development needs is collaboratively developed, agreed to and implemented - Identify specific training needs of individuals - Encourage staff in applying skills and knowledge in the workplace - Provide training to the required standard on the job - Support and encourage staff to attend training courses and to take up other development opportunities. | - Employee feedback development procedures - Employee performance and development activities feedback - Mechanism for taking actions after the performance appraisals | Theory- 2Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU5. Provide leadership. direction and guidance to the work group | Trainee will be able to: - Link between the function of the group and the goals of the organization - Participate in decision making routinely to develop, implement and review work of the group and to allocate responsibilities where appropriate - Give opportunities and encouragement to others to develop new and innovative work practices and strategies - Identify conflict and resolve with minimum disruption to work group function - Provide staff with the support and supervision necessary to perform work safely and without risk to health - Allocate tasks within the competence of staff and support with appropriate authority, autonomy and training - Supervise appropriately the changing priorities and situations and takes into account the different needs of individuals and the requirements of the task | - Designing the training modules - Scheduling of trainings & allocation of trainers - Allocation of supportive resources | Theory- 2Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Lead Small Teams

Objective:After the completion of this competency standard, the Trainee will be able to lead small teams including setting and maintaining team and individual performance standards.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Facilitate team development | Trainee will be able to: - Identify work requirements, standards and purpose to team members. - Assist team to develop objectives, targets and key performance indicators relevant its purpose and workplace goals. - Allocate duties regard to the skills required to properly undertake the assigned task and according to company policy. - Identify roles, responsibilities and expectations of each team member. - Disseminate and discuss performance expectations to individual team members. | - Explain team dynamics and facilitation processes - Describe methods of monitoring performance - Outline the relevant legal requirements. - Outline strategies for dealing effectively with team member complaints or grievances | Theory- 4Hrs Practical- Hrs Total- 4 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Motivate and build the team | Trainee will be able to: - Develop positive and constructive relationships with and between team members - Facilitate team communication processes - Involve team members in the process of examining risks and options and making decisions, to ensure acceptance and support. - Encourage individual and team efforts and contributions. - Strengths and weaknesses of team members are determined and sharing of work tasks is promoted to up skill team members. - Recognize team members’ queries and discuss and deal with it. | - A person who demonstrates competency in this unit must be able to provide evidence of the ability to lead small teams. - State workplace policies and procedures | Theory- 3Hrs Practical- Hrs Total- 3 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Facilitate and monitor team effectiveness | Trainee will be able to: - Monitor the implementation of work plan and team and individual performance against agreed strategies, targets and standards, according to workplace policies and procedures. - Monitor performance against defined performance criteria and/or assignment instructions and corrective action taken if required. - Support team in identifying and resolving problems that may impede performance and to suggest improvements in team Performance. - Consult team members in any review and revision of team objectives and goals. - Address performance issues which cannot be rectified within the team to appropriate personnel according to employer policy. - Refer concerns of a team and individual are referred to next level of management or appropriate specialist and conduct negotiations on their behalf. - Keep team members inform of any changes in the priority allocated to assignments, or tasks which might impact on client/customer needs and satisfaction. - Monitor team operations to ensure that internal or external employer/client needs and requirements are met. - Provide follow-up communication on all issues affecting the team - Conduct team meetings to review work operations and address issues according to workplace policies and procedures. - Support team in identifying and resolving problems that may impede performance and to suggest improvements in team performance. - Consult team members in any review and revision of team objectives and goals. - Raise any inappropriate values and standards exhibited in the workplace with the person concerned. | - Explain conflict resolution techniques - Explain management styles - Evidence of integration of employability skills with workplace tasks and job roles and verify competency is able to be transfer | Theory- 3Hrs Practical- Hrs Total- 3 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Plan and organize work

Objective: After the completion of this competency standard, the Trainee will be able to set objectives and plan work activities, Plan and schedule work activities, Implement work plans, Monitor work activities, review and evaluate work plans and activities. Trainee will be able to plan and organize work in a small independent operation or of a section of a large organization.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Set objectives and plan work activities | Trainee will be able to: - Identify work objectives in consultation with supervisor and consistent with organizational aims. - Determine work activities, consistent with, and linked to objectives and broken down into steps in accordance with set time frames. - Establish work activity priorities and deadlines in consultation with others, as appropriate, optimizing the use of time and resources. - Identify your own and team responsibilities and levels of authority to ensure understanding of roles. - Assess resource implications of the work activities as appropriate consistent with workplace procedures. | - Explain Communication skills: sharing information, listening and understanding, negotiation, - Explain the ways of conducting team meetings - List down motivation skills | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Plan and schedule work activities | Trainee will be able to: - Coordinate schedule of work activities with personnel concerned. - Conduct work within established workplace policies and the business goals of the workplace. - Schedule work tasks | - Verify competency is able to be transferred to other situations - Outline the organization’s strategic plan, policies rules and regulations, laws and objectives for work unit activities and priorities | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Implement work plans | - Identify work methods and practices in consultation with personnel concerned. - Implement work plans in accordance with set time frames, resources and standards | Explain team dynamics and facilitation processes Describe the following Organizing Planning Presentation skills Team work | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Monitor work activities | Trainee will be able to: - Monitor work activities and compare with set objectives. - Monitor work performance - Report and coordinate deviations from work activities with appropriate personnel and in accordance with set standards. - Compile reporting requirements with in accordance with recommended format. - Maintain files in accordance with standard operating procedures | - Outline organizations policies, strategic plans, guidelines related to the role of the work unit | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU5. Review and evaluate work plans and activities | Trainee will be able to: - Review work plans, strategies and implementation based on accurate, relevant and current information. - Base the review on comprehensive consultation with appropriate personnel on outcomes of work plans and reliable feedback. - Get the feedback to identify and develop ways to improve competence within available opportunities. - Provide results of review to concerned parties and formed as the basis for adjustments/simplifications to be made to policies, processes and activities. - Conduct performance appraisal in accordance with organization rules and regulations. - Prepare performance appraisal report and document it regularly as per organization requirements. - Prepare recommendations and present to appropriate personnel/authorities. - Implement feedback mechanisms in line with organization policies. | - The evidence should integrate employability skills with workplace tasks and job roles | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Develop teams and individuals

Objective: After the completion of this competency standard, the Trainee will be able to determine individual and team development needs and facilitate the development of the workgroup۔

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Monitor and evaluate workplace learning | Trainee will be able to: - Utilize feedback from individuals or teams to identify and implement improvements in future learning arrangements. - Assess and record outcomes and performance of individuals/teams to determine the effectiveness of development programs and the extent of additional support. - Negotiate modifications to learning plans to improve the efficiency and effectiveness of learning. - Maintain records and reports of competency within organizational requirement. | - Explain the career paths and competency standards in the industry - List down coaching and mentoring principles - Elaborate planning skills to organize required resources and equipment to meet learning needs | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Develop team commitment and cooperation | Trainee will be able to: - Use open communication processes to obtain and share information are used by team. - Reach onto decisions by the team in accordance with its agreed roles and responsibilities. - Develop mutual concern and camaraderie in the team. | - A person who demonstrates competency in this unit must be able to provide evidence of the ability to develop teams and individuals. | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Plan learning and development in the team | Trainee will be able to: - Identify learning and development needs systematically in line with organizational requirements based on feedback on performance and self-evaluation. - Develop and implement learning plan to meet individual and group training and developmental needs - Encourage individuals to self -valuate performance and identify areas for improvement. | - Describe facilitation skills to conduct small group training sessions - Explain methods and techniques for eliciting and interpreting feedback | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Select suitable learning method | Trainee will be able to: - Identify learning and development program goals and objectives to match the specific knowledge and skills requirements of competency standards. - List down appropriately the learning delivery methods to the learning goals, the learning style of participants and availability of equipment and resources. - Identify resources and timelines required for learning activities are identified and approved in accordance with organizational requirements. | - Explain the ways of reporting skills to organize information; assess information for relevance and accuracy and elaborate on learning outcomes - Explain the ways to improve and develop team | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU5. Facilitate accomplishment of organizational goals | Trainee will be able to: - Participate in team activities and communication processes. - Develop individual and joint responsibility for their actions - Sustain collaborative efforts are sustained to attain organizational goals. | - Describe the methods for identifying and prioritizing personal development opportunities and options | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Apply problem solving techniques in the workplace using critical thinking

Objective:  After the completion of this competency standard, the Trainee will be able to apply the process of problem solving for problems beyond those associated directly with the process unit.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Analyze the problem | Trainee will be able to: - Evaluate issues/concerns are evaluated based on data gathered. - Identify possible causes of problem are identified within the area of responsibility as based on experience and the use of problem solving tools/analytical techniques. - Develop possible cause statements based on findings. - Use analogies to support reasoning. - Identify cause and effects are identified based on the criteria or information provided to support reasoning. | - Explain Analytical skills and broad knowledge of diagnostic tools - Explain broad knowledge of the client business domain - Elaborate broad understanding of organizational systems and functions Outline communication skills according to the type of audience - Explain the methods of questioning and active listening employed to clarify general information | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Identify possible solutions | Trainee will be able to: - Consider all possible options for solution of the problem in accordance with safety and operating procedures. - Determine strengths and weaknesses of possible options. - Take corrective action to solve the problem and determine its possible future causes. - Analyze past experience - Provide samples to support generalization. - Implement simulations as needed. | - Describe the ways to develop critical thinking - Explain methods and techniques for decision making within a limited range of options - Describe general customer service skills | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Recommend solution to higher management | Trainee will be able to: - Prepare report or documentation. - Present recommendations to appropriate personnel. - Follow up recommendations, if required. | - Explain the ways to improve teamwork in reference to personal responsibility | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Implement solution | Trainee will be able to: - Identify measurable objectives - Identify resource needs - Prepare timelines in accordance with plan. | - Develop teams and individuals and ask for individual feedback | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU5. Evaluate / monitor results and outcome | Trainee will be able to: - Identify processes and improvements based on evaluative assessment of problem. - Prepare recommendations and submit to superiors | - The evidence should integrate employability skills with workplace tasks and job roles and verify competency is able to be transferred to other situations | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Manage Human Resource Services

Objective: After the completion of this competency standard, the Trainee will be able to plan, manage and evaluate delivery of human resource services, integrating business ethics. It applies to individuals with responsibility for coordinating a range of human resource services across an organization. They may have staff reporting to them.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours: 1

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Determine strategies for delivery of human resource services | Trainee will be able to: - Analyze business strategy and operational plans to determine human resource requirements. - Review external business environment and likely impact on organization’s human resource requirements. - Consult line and senior managers to identify human resource needs in their areas. - Review organization’s requirements for diversity in the workforce. - Develop options for delivery of human resource services that comply with legislative requirements, organizational policies and business goals. - Develop and agree on strategies and action plans for delivery of human resource services. - Agree and document roles and responsibilities of human resource team, line managers, and external contractors | - Identify the key provisions of legal and compliance requirements that apply to managing human resources - Summarize the organization’s code of conduct | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU2. Manage the delivery of human resource services | Trainee will be able to: - Develop and communicate information about human resource strategies and services to internal and external stakeholders. - Develop and negotiate service agreements between the human resource team, service providers and client groups. - Document and communicate service specifications, performance standards and timeframes. - Document and communicate service specifications, performance standards and timeframes. - Agree on, and arrange monitoring of quality assurance processes. - Ensure that services are delivered by appropriate providers, according to service agreements and operational plans. - Identify and rectify underperformance of human resource team or service providers. - Identify appropriate return on investment of providing human resource services. | - Fundamentals of recruitment and selection process i.e. searching, screening, evaluation and control - Types of recruitment processes as per business requirement | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU3. Evaluate human resource service delivery | Trainee will be able to: - Establish systems for gathering and storing information needed to provide human resource services. - Survey clients to determine level of satisfaction. - Analyze feedback and surveys and recommend changes to service delivery. - Capture ongoing client feedback for the review processes. - Obtain approvals to variations in service delivery from appropriate managers. - Support agreed change processes across the organization. | - Explain human resource strategies and planning processes and their relationship to business and operational plans | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |
| LU4. Manage integration of business ethics in human resource practices | Trainee will be able to: - Ensure personal behavior is consistently ethical and reflects values of the organization. - Ensure code of conduct is observed across the organization, and its expectations are incorporated in human resource policies and practices. - Observe confidentiality requirements in dealing with all human resource information. - Deal promptly with unethical behavior. - Ensure all persons responsible for human resource functions understand requirements regarding their ethical behavior. | - Describe performance and contract management - Explain how feedback is used to modify the delivery of human resources. | Theory- 4Hrs Practical- Hrs Total- 4 Hrs | - Internet - Laptop/Computer - White board - Projector screen - Multimedia projector | Classroom |

## Develop workplace policy and procedures for sustainability.

Objective: After the completion of this competency standard, the Trainee will be able to develop and implement a workplace
sustainability policy and to modify the policy to suit changed circumstances. It applies to individuals with managerial responsibilities who undertake work developing approaches to create, monitor and improve strategies and policies within workplaces and engage with a range of relevant stakeholders and specialists.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours:  01

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Develop workplace sustainability policy | Trainee will be able to: - Define scope of sustainability policy - Gather information from a range of sources to plan and develop policy - Identify and consult stakeholders as a key component of the policy development process - Include appropriate strategies in policy at all stages of work for minimizing resource use, reducing toxic material and hazardous chemical use and employing life cycle management approaches - Make recommendations for policy options based on likely effectiveness, timeframes and cost - Develop policy that reflects the organization s commitment to sustainability as an integral part of business planning and as a business opportunity - Agree to appropriate methods of implementation, outcomes and performance indicators | - Outline the environmental or sustainability legislation, regulations and codes of practice applicable to the organization identify internal and external sources of information and - Explanation of plan and development of the organization sustainability policy | Theory- 2 Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU2. Communicate workplace sustainability policy | Trainee will be able to: - Promote workplace sustainability policy, including its expected outcome, to key stakeholders. - Inform those involved in implementing the policy about expected outcomes, activities to be undertaken and assigned responsibilities. | - Outline organizational systems and procedures that relate to sustainability | Theory- 2 Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU3. Implement workplace sustainability policy | Trainee will be able to: - Develop and communicate procedures to help implement workplace sustainability policy - Implement strategies for continuous improvement in resource efficiency - Establish and assign responsibility for recording systems to track continuous improvements in sustainability approaches | - Outline typical barriers to implementing policies and procedures in an organization and possible strategies to address them. | Theory- 2 Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU4. Review workplace sustainability policy implementation | Trainee will be able to: - Review workplace sustainability policy implementation. - Investigate successes or otherwise of policy. - Monitor records to identify trends that may require remedial action and use to promote continuous improvement of performance. - Modify policy and or procedures as required to ensure improvements are made | - Explain workplace policy development processes and practices | Theory- 4 Hrs Practical- Hrs Total- 4 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |

## Manage meetings

Objective: After the completion of this competency standard, the Trainee will be able to manage a range of meetings including
overseeing the meeting preparation processes, chairing meetings, organizing the minutes and reporting meeting outcomes. It applies to individuals employed in a range of work environments who are required to organize and manage meetings within their workplace, including conducting or managing administrative tasks in providing agendas and meeting material. They may work as senior administrative staff or may be individuals with responsibility for conducting and chairing meetings in the workplace

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours:  01

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare for meetings | Trainee will be able to: - Develop agenda in line with stated meeting purpose - Ensure style and structure of meeting are appropriate to its purpose - Identify meeting participants and notify them in accordance with organizational procedures - Confirm meeting arrangements in accordance with requirements of meeting - Dispatch meeting papers to participants within designated timelines | - Outline responsibilities of the chairperson and explain group dynamics in relation to managing meetings | Theory- 2 Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU2. Conduct meetings | Trainee will be able to: - Chair meetings in accordance with organizational requirements, agreed conventions for type of meeting and legal and ethical requirements - Conduct meetings to ensure they are focused, time efficient and achieve the required outcomes - Ensure meeting facilitation enables participation, discussion, problem solving and resolution of issues - Brief minute-taker on method for recording meeting notes in accordance with organizational requirements and conventions for type of meeting | - Describe options for meetings including face-to-face, tele-conferencing, web-conferencing and using webcams | Theory- 4 Hrs Practical- Hrs Total- 4 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU3. Follow up meetings | Trainee will be able to: - Check transcribed meeting notes to ensure they reflect a true and accurate record of the meeting and are formatted in accordance with organizational procedures and meeting conventions - Distribute and store minutes and other follow-up documentation within designated timelines, and according to organizational requirements - Report outcomes of meetings as required, within designated timelines | - Devise meeting terminology, structures, arrangements as per organizational procedures | Theory- 4 Hrs Practical- Hrs Total- 4 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |

## Manage recruitment selection and induction processes

Objective: After the completion of this competency standard, the Trainee will be able to manage all aspects of recruitment
selection and induction processes in accordance with organizational policies and procedures. It applies to individuals or human resource personnel who take responsibility for managing aspects of selecting new staff and orientating those staff in their new positions. It is not assumed that the individual will be directly involved in the selection processes themselves, although this may well be the case.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours:  01

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Develop recruitment, selection and induction policies and procedures | Trainee will be able to: - Analyze strategic and operational plans and policies to identify relevant policies and objectives - Develop recruitment, selection and induction policies and procedures and supporting documents - Review options for technology to improve efficiency and effectiveness of recruitment and selection process - Obtain support for policies and procedures from senior managers - Trial forms and documents supporting policies and procedures and make necessary adjustments - Communicate policies and procedures to relevant staff and provide training if required | - Describe recruitment and selection methods, including assessment centers - Describe the purpose of employee contracts and industrial relations - Summarize relevant legislation, regulations, standards and codes of practice that may affect recruitment, selection and induction | Theory- 2 Hrs Practical- Hrs Total- 2 Hr | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU2. Recruit and select staff | Trainee will be able to: - Determine future human resource needs in collaboration with relevant managers and sections - Ensure current position descriptors and person specifications for vacancies are used by managers and others involved in recruitment, selection and induction processes - Provide access to training and other forms of support to all persons involved in recruitment and selection process - Ensure advertising of vacant positions complies with organizational policy and legal requirements - Utilize specialists where necessary - Ensure selection procedures are in accordance with organizational policy and legal requirements - Ensure processes for advising applicants of selection outcome are followed - Ensure job offers and contracts of employment are executed promptly, and new appointments are provided with advice about salary, terms and conditions | - Explain the concept of outsourcing - Explain why terms and conditions of employment are an important aspect of recruitment | Theory- 4Hrs Practical- Hrs Total- 4Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU3. Manage staff induction | Trainee will be able to: - Provide access to training and ongoing support for all persons engaged in staff induction - Check induction processes are followed across the organization - Oversee management of probationary employees and provide them with feedback until their employment is confirmed or terminated - Obtain feedback from participants and relevant managers on extent induction process is meeting its objectives - Make refinements to induction policies and procedures | Explain the relevance of psychometric and skills testing programs to recruitment. | Theory- 4Hrs Practical- Hrs Total- 4Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |

## Manage personal work priorities and professional development

Objective: After the completion of this competency standard, the Trainee will be able to create systems and process to organize information and prioritize tasks. It applies to individuals working in managerial positions who have excellent organizational skills. The work ethic of individuals in this role has a significant impact on the work culture and patterns of behavior of others as managers at this level are role models in their work environment.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours:  01

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Establish personal work goals | Trainee will be able to: - Serve as a positive role model in the workplace through personal work planning - Ensure personal work goals, plans and activities reflect the organization s plans, and own responsibilities and accountabilities - Measure and maintain personal performance in varying work conditions, work contexts and when contingencies occur | Explain principles and techniques involved in the management and organization of: performance measurement personal behavior, self-awareness and personality traits identification a personal development plan personal goal setting time Discuss management development opportunities and options for self Outline organization s policies, plans and procedures | Theory- 2 Hrs Practical- Hrs Total- 2Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU2. Set and meet own work priorities | Trainee will be able to: - Take initiative to prioritize and facilitate competing demands to achieve personal, team and organizational goals and objectives - Use technology efficiently and effectively to manage work priorities and commitments - Maintain appropriate work-life balance, and ensure stress is effectively managed and health is attended to | Describe methods for achieving a healthy work-life balance | Theory- 4Hrs Practical- Hrs Total- 4Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU3. Develop and maintain professional competence | Trainee will be able to: - Assess personal knowledge and skills against competency standards to determine development needs, priorities and plans - Seek feedback from employees, clients and colleagues and use this feedback to identify and develop ways to improve competence - Identify, evaluate, select and use development opportunities suitable to personal learning style/s to develop competence - Participate in networks to enhance personal knowledge, skills and work relationships - Identify and develop new skills to achieve and maintain a competitive edge | Explain types of learning style/s and how they relate to the individual Describe types of work methods and practices that can improve personal performance. | Theory- 4Hrs Practical- Hrs Total- 4Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |

## Manage workforce planning

Objective: After the completion of this competency standard, the Trainee will be able to manage planning in relation to an
organization’s workforce including researching requirements, developing objectives and strategies, implementing initiatives and monitoring and evaluating trends. It applies to individuals who are human resource managers or staff members with a role in a policy or planning unit that focuses on workforce planning.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours:  01

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Research workforce requirements | Trainee will be able to: - Review current data on staff turnover and demographics - Assess factors that may affect workforce supply - Establish the organization’s requirements for a skilled and diverse workforce | Outline industrial relations relevant to the specific industry | Theory- 2 Hrs Practical- Hrs Total- 2Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU2. Develop workforce objectives and strategies | Trainee will be able to: - Review organizational strategy and establish aligned objectives for modification or retention of the workforce - Consider strategies to address unacceptable staff turnover, if required - Define objectives to retain required skilled labor - Define objectives for workforce diversity and cross-cultural management - Define strategies to source skilled labor - Communicate objectives and rationale to relevant stakeholders - Obtain agreement and endorsement for objectives and establish targets - Develop contingency plans to cope with extreme situations | Explain current information about external labor supply relevant to the specific industry or skill requirements of the organization | Theory- 2 Hrs Practical- Hrs Total- 2Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU3. Implement initiatives to support workforce planning objectives | Trainee will be able to: - Implement action to support agreed objectives for recruitment, training, redeployment and redundancy - Develop and implement strategies to assist workforce to deal with organizational change - Develop and implement strategies to assist in meeting the organization’s workforce diversity goals - Implement succession planning system to ensure desirable workers are developed and retained - Implement programs to ensure workplace is an employer of choice | - Strategies to assist workforce to deal with organizational change & work environment | Theory- 2 Hrs Practical- Hrs Total- 2Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU4. Monitor and evaluate workforce trends | Trainee will be able to: - Review workforce plan against patterns in exiting employee and workforce changes - Monitor labor supply trends for areas of over- or under-supply in the external environment - Monitor effects of labor trends on demand for labor - Survey organizational climate to gauge worker satisfaction - Refine objectives and strategies in response to internal and external changes and make recommendations in response to global trends and incidents - Regularly review government policy on labor demand and supply - Evaluate effectiveness of change processes against agreed objectives | Describe labor force analysis and forecasting techniques | Theory- 4 Hrs Practical- Hrs Total- 4 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |

## Undertake project work

Objective: After the completion of this competency standard, the Trainee will be able to undertake a straightforward project or
a section of a larger project. It covers developing a project plan, administering and monitoring the project, finalizing the project and reviewing the project to identify lessons learned for application to future projects. This unit applies to individuals who play a significant role in ensuring a project meets timelines, quality standards, budgetary limits and other requirements set for the project.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours:  01

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Define project | Trainee will be able to: - Access project scope and other relevant documentation - Define project stakeholders - Seek clarification from delegating authority of issues related to project and project parameters - Identify limits of own responsibility and reporting requirements - Clarify relationship of project to other projects and to the organization’s objectives - Determine and access available resources to undertake project | Give examples of project management tools and how they contribute to a project Explain the organization’s procedures and processes that are relevant to managing a project including: lines of authority and approvals quality assurance human resources budgets and finance recordkeeping reporting | Theory- 2 Hrs Practical- Hrs Total- 2Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU2. Develop project plan | Trainee will be able to: - Develop project plan in line with the project parameters - Identify and access appropriate project management tools - Formulate risk management plan for project, including Work Health and Safety (WHS) - Develop and approve project budget - Consult team members and take their views into account in planning the project - Finalize project plan and gain necessary approvals to commence project according to documented plan | - Outline types of documents and other sources of information commonly used in defining the parameters of a project | Theory- 2 Hrs Practical- Hrs Total- 2Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU3. Administer and monitor project | Trainee will be able to: - Take action to ensure project team members are clear about their responsibilities and the project requirements - Provide support for project team members, especially with regard to specific needs, to ensure that the quality of the expected outcomes of the project and document time lines are met - Establish and maintain required recordkeeping systems throughout the project - Implement and monitor plans for managing project finances, resources and quality - Complete and forward project reports as required to stakeholders - Undertake risk management as required to ensure project outcomes are met - Achieve project deliverables | - Outline the organization’s mission, goals, objectives and operations and how the project relates to them | Theory- 2 Hrs Practical- Hrs Total- 2Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU4. Finalize project | Trainee will be able to: - Complete financial recordkeeping associated with project and check for accuracy - Ensure transition of staff involved in project to new roles or reassignment to previous roles - Complete project documentation and obtain necessary sign-offs for concluding project | - Explain processes for identifying and managing risk in a project | Theory- 4 Hrs Practical- Hrs Total- 4Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |

## Identify and communicate trends in career development

Objective: After the completion of this competency standard, the Trainee will be able to conduct research to identify and communicate career trends. It establishes the need to interact professionally with others in assessing career needs, to effectively assist clients identify competencies they require for a career and employability in a given context. It also examines how to maintain quality of career development services and professional practice. It applies to individuals seeking to identify and communicate trends in career development.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours:  01

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Research and confirm career trends | Trainee will be able to: - Apply knowledge of changing organizational structures, lifespan of careers and methods of conducting work search, recruitment and selection processes - Analyze changing worker and employer issues, rights and responsibilities in context of changing work practices - Examine importance of quality careers development services - Maintain all research, documentation, sources and references (electronic or physical) to a high degree of currency and relevance - Analyze implications of relevant policy, legislation, professional codes of practice and national standards relating to worker and employer issues - Research changes and trends in theory of career development counseling and practice - Confirm clusters, levels and combinations of transferable employability skills and preferences that may open employment options spanning more than one occupation or career pathway | - Explain client care and counseling techniques and processes in the context of career development services - Describe diversity and its potential effects on career choices - Outline relevant policy, legislation, codes of practice and standards relevant to career development - Explain recruitment and selection processes in the context of career development services | Theory- 2 Hrs Practical- Hrs Total- 2Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU2. Assess and confirm ongoing career development needs of target group | Trainee will be able to: - Analyze history and records in assessing needs of target group - Assess success of previous career development services and techniques used for individual or target group - Deploy other means to investigate appropriate care and counseling approaches as required - Maintain privacy, security of all data, research, personal records according to relevant policy, legislation, professional codes of practice & national standards - Establish existing work-life balance requirements, issues and needs | - Outline human psychological development and needs in relation to careers development | Theory- 4 Hrs Practical- Hrs Total- 4 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU3. Maintain quality of career development services and professional practice | Trainee will be able to: - Analyze and review relevance of career theories, models, frameworks and research for target group - Incorporate into career development services and professional practice, major changes and trends influencing workplace and career-related options and choices - Comply with all relevant policy, legislation, professional codes of practice that influence delivery of career development services | - Describe a range of data gathering and research techniques - Explain techniques used to analyze trends. | Theory- 4 Hrs Practical- Hrs Total- 4 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |

## Apply specialist interpersonal and counseling interview skills

Objective: After the completion of this competency standard, the Trainee will be able to use advanced and specialized communication skills in the client-counselor relationship. This unit applies to individuals whose job role involves working with clients on personal and psychological issues within established policies, procedures and guidelines.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours:  01

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Communicate effectively | Trainee will be able to: - Identify communication barriers and use strategies to overcome these barriers in the client-counselor relationship - Facilitate the client-counselor relationship through selection and use of micro skills - Integrate the principles of effective communication into work practices - Observe and respond to non-verbal communication cues - Consider and respond to the impacts of different communication techniques on the client-counselor relationship in the context of individual clients - Integrate case note taking with minimum distraction | Legal and ethical considerations for communication in counseling practice, and how these are applied in individual practice: codes of conduct/practice discrimination duty of care human rights practitioner/client boundaries privacy, confidentiality and disclosure rights and responsibilities of workers, employers and clients work role boundaries responsibilities and limitations of the counselor role work health and safety Principles of person-centered practice Communication techniques and micro-skills including: attending behaviors active listening, reflection of content feeling, summarizing questioning skills open, closed, simple and compound questions client observation skills noting and reflecting skills providing client feedback Specialized counseling communication techniques, and how they are used, including: challenging reframing focusing K8: components of the communication process including: encoder decoder Obstacles to the counseling process Self-evaluation practices, including: how to recognize own biases Impact of own values on the counseling relationship. | Theory- 2 Hrs Practical- Hrs Total- 2Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU2. Use specialized counseling interviewing skills | Trainee will be able to: - Select and use communication skills according to the sequence of a counseling interview - Identify points at which specialized counseling interviewing skills are appropriate for inclusion - Use specialized counseling communication techniques based on their impacts and potential to enhance client development and growth - Identify and respond appropriately to strong client emotional reactions | - Key objectives of counseling interview - Stages of a counseling interview - Potential impacts of using different communication skills and techniques in counseling contexts | Theory- 4 Hrs Practical- Hrs Total- 4 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU3. Evaluate own communication | Trainee will be able to: - Reflect on and evaluate own communication with clients - Recognize the effect of own values and beliefs on communication with clients - Identify and respond to the need for development of own skills and knowledge | Impacts of trauma and stress on the communication process, including on: concentration and attention memory use of verbal and written language use of body language challenging within the counseling session Observational techniques including: facial expressions non-verbal behavior posture silence Ways in which different people absorb information, including: visual auditory kinesthetic K10: communication barriers and resolution strategies, including: environmental physical individual perceptions cultural issues language age issues disability K9: primary factors that impact on the communication process including: context participants rules messages noise feedback | Theory- 4 Hrs Practical- Hrs Total- 4 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |

## Work safely in an office environment

Objective: After the completion of this competency standard, the Trainee will be able to participate in workplace occupational health and safety (OHS) processes to protect workers own health and safety, and that of others.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours:  01

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Work safely | Trainee will be able to: - Follow established safety procedures when conducting work - Carry out pre-start systems and equipment checks in accordance with workplace procedures | - Explain responsibilities of employers and employees under relevant health and safety regulation | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU2. Implement workplace safety requirement | Trainee will be able to: - Identify designated persons for reporting queries and concerns about safety in the workplace - Identify existing and potential hazards in the workplace, report them to designated persons and record them in accordance with workplace procedures - Identify and implement workplace procedures and work instructions for controlling risks - Report emergency incidents and injuries to designated persons | - Report of potential hazards at the workplace to designated persons and record at workplace - Workplace procedures and work instructions for controlling risks | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector - Safety signs - Safety procedures - Variety of forms, formats used within the organization | Class Room |
| LU3. Participate in OHS consultative processes | Trainee will be able to: - Contribute to workplace meetings, inspections or other consultative activities - Raise OHS issues with designated persons in accordance with organizational procedures - Take actions to eliminate workplace hazards or to reduce risks | - Describe emergency procedures including procedures for fires, accidents and evacuation | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU4. Follow safety procedures | Trainee will be able to: - Identify and report emergency incidents - Follow organizational procedures for responding to emergency incidents | - Outline commonly used hazard signs and safety symbols | Theory- 4 Hrs Practical- Hrs Total- 4 Hrs | - Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector - Safety signs - Safety procedures - Variety of forms, formats used within the organization | Class Room |

## Develop workplace documents

Objective: After the completion of this competency standard, the Trainee will be able to interpret written information for workplace purposes as well as planning, drafting and reviewing a basic document before writing the final version. The focus is on the content and structure of written materials and not on the use of computer technology.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours:  01

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Interpret written information | Trainee will be able to: - Read workplace materials to identify the subject and key information for using or reporting to others. - Read procedural manuals and codes of practice to locate specific information to carry out work functions in accordance with policy and standards. - Read a range of written materials to locate and select required information for summaries, short reports and responses to requests. - Identify the cultural context and prior knowledge required to interpret workplace information and obtain assistance when required. - Determine audience and purpose for the document. - Seek assistance with interpretation of complex materials in accordance with organizational procedures. | - Explain the reading and writing procedures at a level to cope with a range of workplace materials - Explain the integration of information from a number of sources in order to generate meaning - Describe the ways to write and sequence paragraphs according to the required purpose of written material - Explain the response to diversity, including gender and disability - Describe the problem-solving skills to determine document design and production processes | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU2. Develop written materials | Trainee will be able to: - Identify and comply with established requirements for a range of written materials in accordance with organizational procedures & standard templates. - Determine format and structure. - Establish key points for inclusion. - Identify organizational requirements - Establish method of communication - Establish means of communication | - Describe the preparation of general information and papers according to target audience | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU3. Draft document | Trainee will be able to: - Develop draft document to communicate key points - Obtain and include any required additional information - Prepare written information in an accurate, concise and unambiguous manner that meets intended audience and organizational requirements. | - Explain the environmental policies such as those relating to paper use / wastage/recycling - Elaborate the ways of proofreading and editing documents to ensure clarity of meaning and conformity to organizational requirements - Elaborate spelling, punctuation and grammar for workplace documents at an experienced level | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU4. Review document | Trainee will be able to: - Check draft for suitability of tone for audience, purpose, format and communication style - Check draft for readability, grammar, spelling, sentence and paragraph construction and correct any inaccuracies or gaps in content. - Check draft for sequencing and structure - Check draft to ensure it meets organizational requirements - Ensure draft is proofread, where appropriate, by supervisor or colleague | - Ergonomic requirements devised for office work - Written material through selection and use of words, grammatical structures, headings and punctuation appropriate to the purpose | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU5. Write final document | Trainee will be able to: - Make and proofread necessary changes - Ensure document is sent to intended recipient within required time frames - File copy of document in accordance with organizational policies and procedures | - Resources to assist in document production, such as dictionary, thesaurus, templates, style sheets - Ways to produce business letters, memos, job applications, resumes, meeting agendas and minutes Format letters into a standard and window faced envelope. | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |

## Prepare and implement negotiation

Objective: After the completion of this competency standard, the Trainee will be able to prepare for and participate in a process of negotiation, Coordinate support services, Restore order, Provide leadership direction and guidance to the work group.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours:  01

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Prepare for the negotiation | Trainee will be able to: - Identify objectives and preferred outcome of the negotiation and determine minimum acceptable outcome - Understand in relation to what can be offered and what is needed from the other party - Gather information regarding the other party – objectives, needs, preferences, resources, what they want to achieve – in order to determine best negotiating points - List and rank the issues to consider concessions that may be made. - Find examples and refine negotiation argument - Check information to ensure it is correct and up-to-date. - Develop a negotiation plan that includes information about the other party and its interests and a set of responses and strategies to the anticipated tactics. - Prepare an agenda in advance, which includes discussion topics, participants, location and schedule | - Explain organization’s policies, guidelines and procedures related to control and surveillance, safety and preventing and responding to incidents and breaches of orders covered in the range of variables. | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU2. Participate in negotiations | Trainee will be able to: - Analyze all aspects of the incident for degree of hazard, priorities, optional outcomes and appropriate strategies - Analyze and determine strategies and priorities on the incident sought from a range of sources - Assess long term objectives against resources and priorities - Apply a range of communication techniques to make and maintain contact with the key people - Provide clear and factual information to enable an honest and realistic assessment of the interests of the key people and their positions - Resolve the conflict and express their likely consequences clearly and do an analysis of the benefits - Reassess points of disagreements for common positive positions | - Outline the principles of effective communication | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU3. Coordinate support services | Trainee will be able to: - Assess the need for support services in terms of the determined strategies and priorities - Negotiate the resources of support services according to established procedures and availability - Provide information on strategies to support services and maintain the communication - Delegate roles and responsibilities according to expertise and resources | - Explain organization’s management and accountability systems | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU4. Restore order | Trainee will be able to: - Assess the incidents for degree of risk and take appropriate action to reduce and remove the impact of the incident and restore order - Take action designed to minimize risk and the preserve the safety and security of all involved - Take action to prevent the escalation of the incident appropriate to the circumstances and agreed procedures. - Carry out the use of force for the restoration of control and the maintenance of security in the least restrictive manner. - Complete reports accurately and clearly provided to the appropriate authority promptly - Review, evaluate and analyze the incident and the organizational response to it and report it promptly and accurately. | - Describe teamwork principles and strategies | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU5. Provide leadership direction and guidance to the work group | Trainee will be able to: - Link between the function of the group and the goals of the organization - Participate in decision making routinely to develop, implement and review work of the group and to allocate responsibilities where appropriate - Give opportunities and encouragement to others to develop new and innovative work practices and strategies - Identify conflict and resolve with minimum disruption to work group function - Provide staff with the support and supervision necessary to perform work safely and without risk to health - Allocate tasks within the competence of staff and support with appropriate authority, autonomy and training - Supervise appropriately the changing priorities and situations and takes into account the different needs of individuals and the requirements of the task | - Outline the guidelines for use of equipment and technology - Explain code of conduct | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |

## Maintain professionalism in the workplace

Objective: After the completion of this competency standard, the Trainee will be able to maintain a professional image in the
workplace, including behaving ethically, demonstrating motivation, respecting timeframes and maintaining personal appearance.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours:  01

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Respect work timeframes | Trainee will be able to: - Demonstrate punctuality in meeting, set working hours and times. - Utilize working hours only for working and follow company regulations. - Complete work tasks within deadlines according to order of priority - Supervisors are informed of any potential delays in work times or projects | - Explain application of good manners and right conduct - Outline the company code of conduct/values | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU2. Maintain personal appearance and hygiene | Trainee will be able to: - Clean hair, body and nails regularly. - Wear suitable cloths for the workplace, and respect local and cultural contexts - Meet specific company dress code requirements | - Describe common products used for oral and personal hygiene | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU3. Maintain adequate distance with colleagues and clients | Trainee will be able to: - Respect personal space of colleagues and clients with reference to local customs and cultural contexts. - Keep sufficient distance from others - Avoid cross transmission of infections (especially through respiration) | - State workplace hygiene standards - Explain basic practices for oral and personal hygiene | Theory- 2Hrs Practical- Hrs Total-2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Mulmediaprojector | Class Room |
| LU4. Work in an ethical manner | Trainee will be able to: - Follow company values/ethics codes of ethics and/or conduct, policies and guidelines. - Use company resources in accordance with company ethical standards. - Conduct personal behavior and relationships in accord with ethical standards and company policies. - Undertake work practices in compliance with company ethical standards, organizational policy and guidelines. - Instruct co-workers on ethical, lawful and reasonable directives. - Share company values /practices with co-workers using appropriate behavior and language. - Report work incidents /situations and/or resolved in accordance with company protocol /guidelines. | - Outline the Company regulations, performance and ethical standards - Explain work responsibilities/job functions - Describe communication skills | Theory- 4Hrs Practical- Hrs Total- 4 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |

## Maintain professional development and career professionalism

Objective: After the completion of this competency standard, the Trainee will be able to promote own learning career growth and
advancement.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours:  01

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Identify own learning needs | Trainee will be able to: - Identify earning needs through evaluation of existing skills and knowledge against job and career progression requirements. - Gather feedback and appraisal is gathered from supervisors, colleagues and clients and used to identify learning needs and skill gaps. - Give advice to relevant personnel regarding identified professional needs. | - Explain all possible learning and development tools: training, mentoring, coaching, networking, seminars, project assignments - Elaborate methods of obtaining feedback - Describe Workplace policies and procedures | Theory- 4Hrs Practical- Hrs Total-4 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU2. Motivate and build the team | Trainee will be able to: - Sought opportunities are sought for undertaking skill-development activities and are planned in liaison with work group and relevant personnel. - Follow and apply advice on the job coaching /mentoring - Undertake formal training programs where available. - Utilize knowledge and skills gained through professional development activities in the workplace and for career development. - Collect constructive assessment and feedback on work performance from colleagues and supervisor to identify ongoing learning needs and opportunities | - Describe fundamental rights at work including gender sensitivity - Outline methodology to identify own learning needs and preferred learning style | Theory- 4Hrs Practical- Hrs Total-4 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU3. Maintain professional growth and development | Trainee will be able to: - Sought recognitions as evidence of career advancement. - Obtain licenses and/or certifications relevant to job and career - Lay down professional goals and strategies to develop the required skills and knowledge through professional development | - Explain Range of options for undertaking personal skill development - Explain education, qualification and certification systems in the country | Theory- 2 Hrs Practical- Hrs Total- 2 Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |

## Organize schedules

Objective: After the completion of this competency standard, the Trainee will be able to manage appointments and diaries for
personnel within an organization, using manual and electronic diaries, schedules and other appointment systems. It applies to individuals employed in a range of work environments who provide administrative support to teams and individuals.

Duration:  10 Hours			Theory:  10 Hours			Practice:  0 Hours          	        Credit Hours:  01

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Establish schedule requirements | Trainee will be able to: - Identify organizational requirements and protocols for diaries and staff planning tools - Identify organizational procedures for different types of appointments - Determine personal requirements for diary and schedule items for individual personnel - Establish appointment priorities and clarify in discussion with individual personnel | - Identify the key provisions of relevant legislation, standards and codes that affect aspects of business operations or the achievement of team goals - Describe organizational requirements for managing appointments for personnel within the organization | Theory- 5 Hrs Practical- Hrs Total-5Hrs | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |
| LU2. Manage schedules | Trainee will be able to: - Identify recurring appointments and deadlines, and schedule these in accordance with individual and organizational requirements - Establish availability of attendees, and schedule new appointments in accordance with required timelines and diary commitments - Negotiate alternative arrangements and confirm when established appointments are changed - Record appointments and manage schedules in accordance with organizational policy and procedures | - Summarize the range of appointment systems that could be used - Outline important considerations when managing the schedules of others. | Theory- 5 Hrs Practical- Hrs Total- 5 Hr | Internet MS Office Smartphone Laptop / Computer Smartphone Printer White board Projector screen Multimedia projector | Class Room |

## Perform word-processing applications

Objective: This unit describes the skills and knowledge required to operate word- processing applications and perform basic operations, including creating and formatting documents, creating tables and printing labels. It applies to individuals in the workplace using fundamental knowledge of word-processing under direct supervision or with limited responsibility.

Duration: 12 Hours							Theory: 6 Hours				Practice: 06 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Apply workplace health and safety (WHS) practices | Trainee will be able to: - Use workplace ergonomic work practices and strategies - Organize work area to ensure an ergonomic work environment | - OHS principles and responsibilities for ergonomics, such as work periods and breaks Practical activity - Identify potential hazards in computer lab and use appropriate actions to mitigate them* | Theory-01 Hrs Practice-00 Hrs Total- 01 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Create documents | Trainee will be able to: - Open word-processing application, create document and add data according to information requirements - Use document templates as required - Use simple formatting tools when creating the document - Save document to directory | - Create and save new file - Use of appropriate template as required Practical activity - Develop a documents in MS word using format tools as per the requirement of the task. | Theory-1 Hrs Practice-01 Hrs Total- 2 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Customize basic settings to meet page layout conventions | Trainee will be able to: - Adjust page layout to meet information requirements - Open and view different toolbars - Change font format to suit document purpose - Change alignment and line spacing according to document information requirements - Modify margins to suit the document purpose - Open and switch between several documents | - Understand and edit page layout Practical activity - Open MS word and change select appropriate layout of the page as per the requirement adding header and footer in the document. | Theory-01 Hrs Practice-01 Hrs Total- 02 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Format documents | Trainee will be able to: - Use formatting features and styles as required - Highlight and copy text from another area in the document or from another active document - Insert headers and footers to incorporate necessary data - Save document in another file format - Save and close document to a storage device | Practical activity - Formatting word document | Theory-1 Hrs Practice-01 Hrs Total- 2 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Create tables | Trainee will be able to: - Insert standard table into document - Change cells to meet information requirements - Insert and delete columns and rows as necessary - Use formatting tools according to style requirements | Practical activity - Create and edit table | Theory-1 Hrs Practice-01 Hrs Total- 2 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Add images | Trainee will be able to: - Insert appropriate images into document and customize as necessary - Position and resize images to meet document formatting needs | Practical activity - Insert, position and resize images | Theory-1 Hrs Practice-01 Hrs Total- 2 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Print documents | Trainee will be able to: - Preview document in print preview mode - Select basic print settings - Print document or part of document from printer | Practical activity - Printing document according to organization need | Theory-00 Hrs Practice-01 Hrs Total- 01 Hrs | Desktop Computer/Laptop | Computer Lab Class room |

## Operate Basics Computer Functions

Objective: This module covers the knowledge, skills and attitudes and values needed to perform basic computer operations which include inputting, accessing, producing and transferring data using the appropriate hardware and software.

Duration: 18 Hours							Theory: 03 Hours				Practice: 15 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Plan and prepare for task to be undertaken | Trainee will be able to: - Requirements of task are determined as per standard - operating procedures - Appropriate hardware and software is selected according to task assigned and required outcome - Task is planned to ensure | - Main types of computers and basic features of different operating systems - Main Parts of computer - Calculating computer capacity Practical activity - Select the appropriate hardware & software as per the requirement of task. | Theory-01 Hrs Practice-03 Hrs Total- 04 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Input data into computer | Trainee will be able to: - Data are entered into the computer using appropriate program/application in accordance with company procedures - Accuracy of information is checked and information is saved in accordance with standard operating procedures - Inputted data are stored in storage media according to requirements - Work is performed within ergonomic guidelines | - Storage devices and basic categories of memory - Basic ergonomics of computer use Practical activity - Select storage devices to store input data | Theory-0.5 Hrs Practice-03 Hrs Total- 3.5 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Access information using computer | Trainee will be able to: - Correct program/application is selected based on job requirements - Program/application containing the information required is accessed according to company procedures - Desktop icons are correctly selected, opened and closed for navigation purposes - Keyboard techniques are carried out in line with OH & S requirements for safe use of keyboards | - Relevant types of software - OH & S principles and responsibilities - Basic ergonomics of keyboard use Practical activity - Operate the computer and its different application | Theory-0.5 Hrs Practice-03 Hrs Total- 3.5 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Produce/output data using computer system | Trainee will be able to: - Entered data are processed using appropriate software commands - Data are printed out as required using computer hardware/peripheral devices in accordance with standard operating procedures - Files and data are transferred between compatible systems using computer software, hardware/ peripheral devices in accordance with standard operating procedures | - Relevant types of software Practical activity - Develop a required documents in MS word and take out print. | Theory-0.5 Hrs Practice-03 Hrs Total- 3.5 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Maintain computer equipment and systems | Trainee will be able to: - Systems for cleaning, minor maintenance and replacement of consumables are implemented - Procedures for ensuring security of data, including regular back-ups and virus checks are implemented in accordance with standard operating procedures - Basic file maintenance procedures are implemented in line with the standard operating procedures | - General security - Viruses Practical activity - Create a proper backup of computer data and install anti-virus software | Theory-0.5 Hrs Practice-03 Hrs Total- 3.5 Hrs | Desktop Computer/Laptop | Computer Lab Class room |

## Develop Computer Application skills

Objective: This module describes the performance outcomes, skills and knowledge required to identify, select and operate three commercial software packages, including a word-processing, a spreadsheet and presentation application package.

Duration: 18 Hours							Theory: 03 Hours				Practice: 15 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Use appropriate OHS office work practices | Trainee will be able to: - Use safe work practices to ensure ergonomic, work organization, energy and resource conservation requirements are addressed - Use wrist rests and document holders where appropriate - Use monitor anti-glare and radiation reduction screens where appropriate | - OHS principles and responsibilities for ergonomics, such as work periods and breaks Practical activity - Identify potential hazards in computer lab and use appropriate actions to mitigate them* | Theory-01 Hrs Practice-03 Hrs Total- 04 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Install and remove software | Trainee will be able to: - Select software to be installed - Follow installation instructions - Delete unrequired software | - Application software packages used by the organization - Basic knowledge of system usage - Basic knowledge of install and remove software - Import and export software functions Practical activity - Identify the required software, install and uninstall these software from the computer. | Theory-0.5 Hrs Practice-03 Hrs Total- 3.5 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Use appropriate word-processing software | Trainee will be able to: - Select word-processing software appropriate to perform activity - Identify document purpose, audience and presentation requirements, and clarify with personnel as required - Identify organizational requirements for text-based business documents and design document structure and layout to ensure consistency of style and image - Match document requirements with software functions to provide efficient production of documents - Use technical functions, other data and formatting to finalize documents - Ensure the naming and storing of documents in appropriate directories or folders and the printing of documents to the required specifications | - Current business practices related to Practical activity - using software to prepare reports - Functions and uses of word processing | Theory-0.5 Hrs Practice-03 Hrs Total- 3.5 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Use appropriate spreadsheet software | Trainee will be able to: - Select spreadsheet software appropriate to perform activity - Identify document purpose, audience and presentation requirements, and clarify with personnel as required - Enter simple formulas and functions using cell referencing where required - Customize spreadsheet settings and format documents to meet requirements - Ensure the naming and storing of documents in appropriate directories or folders and the printing of documents to the required specifications | - Functions and uses of Spreadsheet Practical activity - Prepare a spreadsheet using different functions and formulas. | Theory-0.5 Hrs Practice-03 Hrs Total- 3.5 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Use appropriate presentation software | Trainee will be able to: - Select software application package appropriate to perform activity - Identify purpose, audience and presentation requirements, and clarify with personnel as required - Use technical functions, other data and formatting to finalize documents - Ensure documents are named and stored in appropriate directories or folders and printed to required specifications - Make a presentation | - Functions and uses of presentation software Practical activity - Prepare a presentation using Microsoft power point application. | Theory-0.5 Hrs Practice-03 Hrs Total- 3.5 Hrs | Desktop Computer/Laptop | Computer Lab Class room |

## Operate Presentation Packages

Objective: This module describes the skills and knowledge required to operate power point processing applications and perform basic operations, including creating and formatting presentations, adding slide show effects and printing presentations and notes. It applies to individuals in the workplace using fundamental knowledge of PowerPoint processing under direct supervision or with limited responsibility.

Duration: 09 Hours							Theory: 03 Hours				Practice: 06 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Create Presentations | Trainee will be able to: - Open presentation package and create a simple design for a presentation according to organizational requirements - Open blank presentation and add text and graphics - Apply existing styles within a presentation - Use presentation template and slides to create a presentation - Use various tools to improve the look of the presentation - Save presentation to the appropriate storage device and folder | Practical activity - Basic technical terminology to read help files and prompts | Theory-0.5 Hrs Practice-1.5 Hrs Total- 02 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Customize basic settings | Trainee will be able to: - Adjust display to meet user requirements - Open and view different toolbars to view options - Ensure font settings are appropriate for the presentation purpose - View multiple slides at once | Practical activity - effect of formatting and appearance on the readability and usability of presentation | Theory-0.5 Hrs Practice-02 Hrs Total- 03 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Format presentations | Trainee will be able to: - Use and incorporate organizational charts and bulleted lists, and modify as required - Add objects and manipulate to meet presentation purposes - Import objects and modify for presentation purposes - Modify slide layout, including text and colors, to meet presentation requirements - Use formatting tools as required within the presentation - Duplicate slides within and across a presentation - Reorder sequence of slides and delete slides for presentation purposes - Save presentation in another format - Save to storage device and close presentation | Practical activity - Insert objects and charts | Theory-01 Hrs Practice-01 Hrs Total- 02 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Add slide show effects | Trainee will be able to: - Incorporate pre-set animation and multimedia effects into presentation as required to enhance the presentation - Add slide transition effects to presentation to ensure smooth progression through the presentation - Test presentation for overall effect - Use onscreen navigation tools to start and stop slide show or move between different slides as required | Practical activity - suitable presentation effects for different audiences | Theory-0.5 Hrs Practice-01 Hrs Total- 1.5 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Print presentation and notes | Trainee will be able to: - Select appropriate print format for presentation - Select preferred slide orientation - Add notes and slide numbers - Preview slides and run spell check before presentation - Print selected slides and submit presentation to appropriate person for feedback | Practical activity - Preview and print presentations | Theory-0.5 Hrs Practice-01 Hrs Total- 1.5 Hrs | Desktop Computer/Laptop | Computer Lab Class room |

## Operate Spreadsheet Application

Objective: This module describes the skills and knowledge required to operate Spreadsheet and perform basic operations, including creating and formatting spreadsheet, creating tables, incorporating chart and object in it, and printing labels.

Duration: 12 Hours							Theory: 05 Hours				Practice: 07Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Create spreadsheets | Trainee will be able to: - Open the spreadsheet application, create spreadsheet files and enter numbers, text and symbols into cells according to information requirements - Enter simple formulas and functions using cell referencing when required - Correct formulas when error messages occur - Use a range of common tools during spreadsheet development - Edit columns and rows within the spreadsheet - Use the auto-fill function to increment data where required - Save the spreadsheet to a folder on a storage device | Practical activity - basic technical terminology related to reading help files and prompts - purpose, use and function of spreadsheet applications - create, edit and save spread sheet | Theory-01 Hrs Practice-1 Hrs Total- 02Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Customize basic settings | - Adjust page layout to meet user requirements or special needs - Open and view different toolbars - Change font settings so they are appropriate for the document purpose - Change alignment options and line spacing according to spreadsheet formatting features - Format cell to display different styles as required - Modify margin sizes to suit the purpose of the spreadsheets - View multiple spreadsheets concurrently | Practical activity - Formatting spread sheet | Theory-1 Hrs Practice-2Hrs Total- 3 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Format spreadsheet | Trainee will be able to: - Use formatting features as required - Copy selected formatting features from another cell in the spreadsheet or from another active spreadsheet - Use formatting tools as required within the spreadsheet - Align information in a selected cell as required - Insert headers and footers using formatting features - Save spreadsheet as another file type - Save to storage device and close spreadsheet | Practical activity - effect of formatting and appearance on the readability and usability of spreadsheets | Theory-01 Hrs Practice-01 Hrs Total- 02 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Incorporate object and chart in spreadsheet | - Import an object into an active spreadsheet - Manipulate imported object by using formatting features - Create a chart using selected data in the spreadsheet - Display selected data in a different chart - Modify chart using formatting features | Practical activity - Inserting and editing object in spread sheet - Inserting and modifying chart in spreadsheet | Theory-1 Hrs Practice-2 Hrs Total- 3 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Print spreadsheet | - Preview spreadsheet in print preview mode - Select basic printer options - Print spreadsheet or selected part of spreadsheet - Submit the spreadsheet to appropriate person for approval or feedback | Practical activity - Preview and Print spread sheet | Theory-1 Hrs Practice-01 Hrs Total- 2 Hrs | Desktop Computer/Laptop | Computer Lab Class room |

## Install computer operating systems and hardware

Objective: This module describes the performance outcomes, skills and knowledge required to select, configure and use computer operating systems and basic computer hardware.

Duration: 12 Hours							Theory: 03 Hours				Practice: 09 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Identify operating system and hardware components | Trainee will be able to: - Determine ICT organizational requirements and specifications - Identify and select operating system - Identify appropriate external hardware components - Identify internal hardware components | - Basic knowledge of current industry-accepted operating system, hardware and software products Practical activity - Identify which operating system can be installed on the given hardware system | Theory-01 Hrs Practice-03 Hrs Total- 04 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Install and configure operating system and application software with hardware components | Trainee will be able to: - Install and configure operating system to meet organizational requirements - Identify the functions associated with the operating system and associated boot process - Configure power-management settings to minimize power consumption as an environmentally sustainable measure - Use both the graphical user interface and the command line interface to perform basic tasks - Install or upgrade application software onto the operating system and hardware configuration - Determine the relationship between an application program, the operating system and hardware - Identify general differences between the different computer platforms and their respective operating systems | - Compatibility of an operating system, in respect to other versions Practical activity - Install Microsoft office application in the given system. | Theory-01 Hrs Practice-03 Hrs Total- 04 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Optimize operating system and hardware components | - Optimize operating system using included tools or third-party utilities - Customize the graphical user interface - Use techniques unique to the command line interface - Set up and configure external hardware components and check functionality - Install drivers as appropriate and check functionality | - Function of single-user and multi-user operating systems - Interoperability between operating systems Practical activity Check compatibility of the required drivers, install and check their functionality. | Theory-01 Hrs Practice-03 Hrs Total- 04 Hrs | Desktop Computer/Laptop | Computer Lab Class room |

## Perform writing and editing skills

Objective: This module describes the skills and knowledge required to apply the conventions of plain English to writing and editing tasks of different forms. It also includes editing and proofreading techniques. It applies to individuals in various writing contexts who write and edit texts using appropriate language, style, grammar, spelling, and standard conventions for editing and proofreading.

Duration: 09 Hours							Theory: 03 Hours				Practice: 06 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Apply clear and appropriate language and style to writing and editing tasks | Trainee will be able to: - Use safe work practices including addressing ergonomic requirements when undertaking writing tasks - Use clear, concise and plain English in writing and editing tasks - Apply appropriate paragraph structure to written material to ensure clarity of meaning and ease of reading - Make clear and logical connections between sentences, paragraphs and sections - Determine and incorporate the language and style of the audience | Practical activity - Main features of clear, concise and plain English language for written material | Theory-0.5 Hrs Practice-1.5 Hrs Total- 02 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Apply the appropriate voice, tone and tense | Trainee will be able to: - Determine appropriate voice, tone and tense of the written materials according to audience requirements - Maintain consistent voice, tone and tense throughout written material | Practical activity - Appropriate use of tenses required in written material | Theory-0.5 Hrs Practice-02 Hrs Total- 03 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Apply appropriate grammar, spelling and punctuation | Trainee will be able to: - Apply appropriate grammar conventions to a range of written contexts including use of numbers, quotations, and tables - Apply appropriate spelling and punctuation conventions in writing and editing tasks. | Practical activity - Grammar, punctuation and spelling conventions that meet the task requirements | Theory-01 Hrs Practice-01 Hrs Total- 02 Hrs | Desktop Computer/Laptop | Computer Lab Class room |
| - Perform editing and proofreading tasks to meet requirements | Trainee will be able to: - Edit written material to ensure clear meaning through language and paragraphs, consistent voice, tone and tense - Copyedit written material by checking grammar, spelling and punctuation using standard editing conventions - Proofreading using style guides and by monitoring written material for errors | Practical activity - Editing conventions used in substantive editing and copyediting of written material - Basic software used to write and collect feedback | Theory-0.5 Hrs Practice-01 Hrs Total- 1.5 Hrs | Desktop Computer/Laptop | Computer Lab Class room |

- Members of Curriculum Development Committee

The following members participated in the Curriculum development Committee:

| S# | Name | Designation | Organization |
| --- | --- | --- | --- |
| 1 | Muhammad Adil | Instructor | University of Lahore |
| 2 | Amina Irfan | Instructor | University of Lahore |
| 3 | Ahsan Shahbaz | Manager | PSS, Lahore |
| 4 | Muhammad Imran | Lecturer | University of Lahore |
| 5 | Amir Amin | HoD | Polytechnic Institute, Lahore |
| 6 | Saifullah Khan | AD(Technical) | PITAC LAhore |
| 7 | Salman Khalid | AD(RAC) | PITAC LAhore |
| 8 | Muhammad Rizwan Zafar Ch | HoD Mechanical | Technology College Lahore |
| 9 | Shahid Saeed | Instructor | GATC LAhore |
| 10 | Ms Fahmee Maqsood | System Engineer | Power Zone Lahore |
| 11 | Fahmee Maqsood | Assistant Manager | ZOOM LAhore |
| 12 | Noor ul Haq | Instructor | GCT Mughalpura, Lahore |
| 13 | Syed Jamil Asghr Naqvi | Experimental Officer | Environmental Control System Plan, NPSL Islamabad |
| 14 | Danish Khan | DACUM, Facilitator | NPSL, PCSIR Islamabad |
| 15 | Mr. Muhammad Ishaq | Deputy Director TE | NAVTTC, Islamabad |