Competency Standards

for

National Diploma Level 4 in

“Hydro Power Plant Technician”

National Vocational and Technical Training Commission (NAVTTC)

Government of Pakistan

FOREWORD

National Vocational and Technical Training Commission (NAVTTC) extends its gratitude and appreciation to representatives of business, industry, academia, government agencies, provincial TEVTAs, sector skill councils and trade associations who spared time and extended their expertise for the development of National Vocational Qualification for Level - IV Hydro Power Plant Technician. This work would not have been possible without the technical support of the experts.

It may not be out of place to mention here that all the experts of Industry, Academia and TVET experts of TEVTAs, Energy Sector Experts Pakistan, work diligently for making this qualification worthy and error free for which all credit goes to them. However, NAVTTC accepts the responsibility of all the errors and omissions still prevailing in the Qualification document.

It is also noteworthy that development of Skill Standards is a dynamic and ongoing process, and the developed competency standards need periodic review and updating owing to the constant technological advancements, development in scientific knowledge, and growing experience of implementation at the grass root level as well as the demand of energy sector. The NAVTTC, Government of Pakistan will ensure to keep the qualifications abreast with the changing demands of both national and international job markets.

Executive Director (NAVTTC)

Table of Contents

1.	Introduction	4

1.1.	Date of development:	5

1.2.	Date of review & validation:	5

1.3.	Entry requirement of trainee:	5

1.4.	Trainer Qualification Requirement	5

1.5.	Codes of qualification (ISCED)	5

2.	Summary of Competency Standards and contact hours	5

3.	Qualification Levelling and Packaging	6

4.	Description of Qualification Package	6

5.	Competency Standards	7

5.1 0713E&E4101 Apply Entrepreneurial Skill	7

5.2 0713E&E4102 Operate Hydraulic Machines	10

5.3 0713E&E4103 Calibrate Electrical Equipment	12

5.4 0713E&E4104 Diagnose Electrical Fault in Generator	16

5.5 0713E&E4105 Carryout Transmission of Electrical Power	19

5.6 0713E&E4106 Carryout Distribution of Electrical Power	21

5.7 0713E&E4107 Carryout Protection of Distribution and Transmission System	23

5.8 0713E&E4108 Install Turbine	27

5.9 0713E&E4109 Install Generator	30

5.10 0713E&E4110 Control HP plant shutdown for emergency standby electrical systems	33

5.11 0713E&E4111 Analyze faults in HP plant operation	36

5.12 0713E&E4112 Carry out preventive maintenance procedures as part of HP operations	39

5.13 On Job Training	42

6.	List of Consumables, Tools, Machinery & Equipment	42

7.	Members of Qualifications Development Committee	49

# Introduction

The National Vocational and Technical Training Commission (NAVTTC) acknowledge the vital role of vocational and technical education in equipping Pakistan's workforce with the skills and competencies necessary to thrive in emerging industries. To address the increasing demand for skilled professionals in dynamic and innovative sectors, NAVTTC has initiated the development of Competency Standards (CS) for the trade of Hydro Power Plant technician in Pakistan. This initiative underscores NAVTTC’s commitment to workforce development, enhancing employability, and driving Pakistan’s digital transformation while aligning with global industry trends.

Hydro Power Plant Technology is a rapidly growing sector with significant contributions to the global economy, spanning industries such as rural electrification, sustainable energy, agriculture, and industrial applications. This multidisciplinary field demands expertise in hydrodynamics, electrical engineering, turbine design, power generation, and system integration. With the accelerating adoption of renewable energy solutions, the hydro industry is witnessing a surge in demand for skilled professionals, creating substantial career opportunities both locally and internationally. By establishing these competency standards, NAVTTC ensures the development of a workforce prepared to meet industry requirements and contribute to Pakistan's economic advancement.

The qualification framework for Hydro Power Plant Technician focuses on equipping learners with essential skills and knowledge, ranging from entrepreneurial skills, Operate Hydraulics Machines, Electrical Equipment, Electrical Fault in Generator, Transmission of Electrical Power, Distribution of Electrical Power, Protection of Distribution and Transmission System, Install Turbine, Install Generator, Control HP plant shutdown for emergency standby electrical systems, Analyze faults in HP plant operation, preventive maintenance procedures as part of HP operations.

| ## Date of development: | 03rd March 2025 – 07th March 2025 |
| --- | --- |
| ## Date of review & validation: | 7th March 2025 |
| ## Entry requirement of trainee: | Secondary School Certificate or Equivalent and Level 3 |
| ## Trainer Qualification Requirement | Minimum DAE with 5 years of hands-on experience in Hydro Power Plant Technician OR Minimum Bachelor’s with 3 years of hands-on experience in Hydro Power Plant Technician |
| ## Codes of qualification (ISCED) | Code: 0713E&E41 Description: National Diploma Level 4 “Hydro Power Plant Technician” |

# Summary of Competency Standards and contact hours

| Competency Standards | NVQF Level | Category | Estimated Contact Hours |  |  | Cr Hr |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Th | Pr | Total |  |
| 0713E&E4101 Apply Entrepreneurial Skill | 4 | Generic | 2 | 6 | 8 | 0.5 |
| 0713E&E4102 Operate Hydraulics Machines | 4 | Technical | 10 | 40 | 50 | 3 |
| 0713E&E4103 Calibrate Electrical Equipment | 4 | Technical | 4 | 22 | 26 | 1.5 |
| 0713E&E4104 Diagnose Electrical Fault in Generator | 4 | Technical | 10 | 60 | 70 | 4 |
| 0713E&E4105 Carryout Transmission of Electrical Power | 4 | Technical | 10 | 40 | 50 | 3 |
| 0713E&E4106 Carryout Distribution of Electrical Power | 4 | Technical | 10 | 40 | 50 | 3 |
| 0713E&E4107 Carryout Protection of Distribution and Transmission System | 4 | Technical | 5 | 50 | 55 | 3 |
| 0713E&E4108 Install Turbine | 4 | Technical | 10 | 60 | 70 | 4 |
| 0713E&E4109 Install Generator | 4 | Technical | 10 | 60 | 70 | 4 |
| 0713E&E4110 Control HP plant shutdown for emergency standby electrical systems | 4 | Technical | 5 | 40 | 45 | 2.5 |
| 0713E&E4111 Analyze faults in HP plant operation | 4 | Technical | 5 | 50 | 55 | 3 |
| 0713E&E412 Carry out preventive maintenance procedures as part of MHP operation | 4 | Technical | 4 | 40 | 45 | 2.5 |
| 0713E&E413 On Job Training | 4 | Technical | - | - | 240 | 6 |
| Total |  |  | 85 | 508 | 834 | 40 |

# Qualification Levelling and Packaging

| S # | Occupations / Short Course | Modules/CS Codes | Level | Occupation Credit Hours | Training duration |
| --- | --- | --- | --- | --- | --- |
| 1. | Hydro Power Plant Technician | 0713E&E410-1 to 0713E&E41-12 | 4 | 40 | 1 year |

# Description of Qualification Package

| Level 2 | Level 3 | Level 4 | Level 5 |
| --- | --- | --- | --- |
| Micro Hydro Power Plant Assistant | Micro Hydro Power Plant Operator | Hydro Power Plant Technician | - DAE Civil Technology - DAE Electrical Technology - DAE Mechanical Technology |

# Competency Standards

### 5.1 0713E&E4101 Apply Entrepreneurial Skill

Overview:

This competency standard covers the underpinning knowledge and skills required for a trainee to be competent in developing entrepreneurial skills and business operations within the energy sector. After completing this competency standard, the student will be able to successfully perform all the tasks related to communication, business structuring, financial management, customer engagement, and regulatory compliance in accordance with the essence of the Competency-Based Training (CBT) System.

| Competency Units | Performance Criteria |
| --- | --- |
| Communicate Effectively in a Professional Environment | - Enlist technical terminology in energy sector. - Deliver messages to team members & supervisors as per SOPs. - Demonstrate active listening skills in discussions. |
| Prepare Reports and Documentation | - Prepare daily operation log as per procedures. - Prepare document for maintenance records as per SOPs. - Document troubleshooting reports as per SOPs. - Maintain organized record-keeping system as per procedures. |
| Develop Customer Relationship and Service Skills | - Resolve customer concerns related to energy sector services as per procedures. - Educate consumers about energy efficiency and sustainable solutions as per instructions. - Maintain professionalism while interacting with clients and stakeholders. - Build long-term relationships by ensuring customer satisfaction and trust. |
| Demonstrate business fundamentals in the energy sector | - Identify the basics of energy business models and revenue generation. - Identify key stakeholders involved in energy projects. - Analyze cost and pricing structures for energy distribution. - Evaluate market trends and business opportunities within the energy sector. |
| Apply Financial Management Skills | - Prepare cost estimations for energy projects. - Track operational expenses and recommend cost-saving measures. - Identify basic financial terms related to energy businesses. - Develop budgeting strategies to enhance financial sustainability. |
| Follow Entrepreneurial Best Practices | - Identify market opportunities for energy services. - Develop strategies for business growth and customer acquisition. - Implement risk management techniques for sustainable business operations. - Enlist funding opportunities for energy projects. - Enlist investment opportunities for energy projects. |
| Implement Safety and Regulatory Compliance | - Enlist to legal and safety requirements for energy operations. - Enlist government policies and licensing requirements. - Enlist occupational health and safety regulations. - Enlist environmental compliance and sustainable energy practices. |
| Identify Business Opportunities in the Energy Sector | - Conduct market research to identify potential energy business opportunities. - Analyze demand for decentralized energy solutions. - Evaluate the impact of renewable energy trends on energy businesses. - Develop a feasibility study for launching an energy service. |
| Develop Structure of The New Energy Business | - Identify different business models for an energy company. - Establish roles and responsibilities within the energy enterprise. - Design an operational workflow for energy distribution. - Demonstrate compliance with industry standards and regulations. |
| Develop Strategy to Attract Customers | - Create marketing and outreach campaigns to promote energy services. - Engage with potential customers through digital platforms and local events. - Build partnerships with stakeholders and community leaders. - Develop customer incentives to enhance service adoption. |
| Create Portfolios on Facebook, Instagram and LinkedIn | - Create a Facebook Page - Upload Portfolio Content on Facebook - Create a Facebook Group - Join already created Facebook groups for freelancers - Create Profile on Instagram - Upload Portfolio Content on Instagram - Create LinkedIn Profile, company page and showcase page - Create LinkedIn group - Join LinkedIn groups for freelancers |

Knowledge & Understanding

- Fundamentals of effective oral and written communication in a technical environment.

- Report writing techniques for documentation, maintenance logs, and incident reports.

- Customer relationship management (CRM) for energy sector professionals.

- Basic principles of entrepreneurship, including market analysis, financial planning, and risk assessment.

- Energy sector regulations related to business operations and compliance.

- Business ethics and professionalism in customer interactions and negotiations.

- Financial management essentials such as cost estimation, budgeting, and revenue tracking.

- Safety and environmental considerations in energy operations.

- Strategies for scaling energy businesses and identifying investment opportunities.

- Methods to attract and retain customers in the energy sector.

- Understanding of market research, business structuring, and promotional strategies in the energy sector.

Critical Evidence(s) Required

The candidate needs to produce the following critical evidence(s) to be declared competent in this competency standard:

- Write sample daily operation log/technical report as per instructions.

- Prepare basic financial plan for an energy project as per instructions.

- Handle a simulated customer complaint resolution as per instructions.

- Demonstrate professional behavior during role-play scenario as per instructions.

- Prepare safety assessment checklist for an energy facility.

Consumables, Tools, Machinery & Equipment

The tools and equipment required for this competency standard are given below:

| List of Tools, Machinery & Equipment |  |  |
| --- | --- | --- |
| Sr. No | Item | Quantity |
|  | Directories of existing businesses | 25 |
|  | Examples of business plans | 25 |
|  | Sample of financial plans | 25 |
|  | Business planner templates | 25 |
|  | Start-up-costs estimator | 25 |

### 5.2 0713E&E4102 Operate Hydraulic Machines

Overview:

This competency standard covers the skills and knowledge required to Categorize fluid mechanics, Illustrate Hydro kinetics, Measure Flow of fluid Through Pipes, Measure fluid pressure through Impact of Jet, Identify and use of Water Turbines, illustrate water Pumps, Categorize Hydraulic Valves and Seals, Classify and use of Hydraulic machines, Illustrate Hydraulic Actuators, Identify Hydraulic Circuits and Accessories and Operate Pneumatic Simple Machines

| Competency Units | Performance Criteria |
| --- | --- |
| Categorize fluid mechanics | - Classify fluids - List properties of fluids. - Illustrate application of fluid mechanics principles. |
| Illustrate Hydro kinetics | - List principles of hydrokinetics. - Calculate velocity and pressure distribution in fluid flow as per instructions. - Interpret impact of external forces on fluid. |
| Measure Flow of fluid Through Pipes | - Identify flow measurement devices. - Calibrate measurement device as per SOPs. - Measure flow rate of the given fluid as per instructions. |
| Measure fluid pressure through Impact of Jet | - Test jet impact apparatus as per SOPs. - Calibrate measurement instruments as per SOPs. - Record forces exerted by the jet as per procedures. - Calculate fluid pressure from the force readings. |
| Operate Water Turbines | - Categorize types of water turbines. - Select water turbine as per instructions. - Install water turbine system as per SOPs. - Operate water turbine as per SOPs. |
| Operate water Pumps | - List types of water pumps. - Install given water pump as per instructions. - Calculate Suction head, Delivery head and Total lift of the given pump. |
| Operate Hydraulic Valves and Seals | - List types of hydraulic valves. - Operate given hydraulic valves as per SOPs. - List types of hydraulic seals. - Check leakage of Hydraulic Seals as per SOPs. |
| Calculate the performance of Hydraulic machines | - List types of hydraulic machines. - Operate hydraulic controls as per SOPs. - Calculate efficiency of given hydraulic machine as per instructions. |
| Operate Hydraulic Actuators | - List types of hydraulic actuators. - Install given hydraulic actuators as per SOPs. - Calculate efficiency of given hydraulic actuator as per instructions. |
| Identify Hydraulic Circuits and Accessories | - Draw hydraulic circuits as per instructions. - List components in given hydraulic circuit. - Analyse performance of given hydraulic circuit. |

Knowledge & Understanding

The candidate must possess underpinning knowledge and understanding required to carry out tasks covered in this competency standard. Therefore he/she must be able to:

- Understand Fluid Properties.

- Analyse Fluid Flow Types.

- Understand Hydraulic Pressure.

- Design and Analyse Hydraulic Circuits.

- Select Appropriate Hydraulic Machines.

- Understand Simple Fluid Mechanics Calculations.

- Implement Safety Procedures.

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Measure the following fluid properties

  - Density

  - Viscosity

  - Flow rates as per given instructions.

- Solve given problems using Bernoulli’s equation and the continuity equation

- Design simple hydraulic circuits and check their performance as per instructions.

Consumables, Tools, Machinery & Equipment

| List of Tools, Machinery & Equipment |  |  |
| --- | --- | --- |
| S. No | Items | Quantity |
| 1. | Hydraulic Trainer Kit (with actuators, valves, circuit board) | 2 Sets |
| 2. | Flow Measuring Apparatus (Venturi meter / Orifice Meter) | 2 Sets |
| 3. | Pressure Gauge Set (with manometers) | 3 Sets |
| 4. | Impact of Jet Apparatus | 1 Set |
| 5. | Hydraulic Pump Test Rig (Centrifugal & Reciprocating) | 2 Sets |
| 6. | Water Turbine Test Rig (Pelton / Francis / Kaplan) | 2 Sets |
| 7. | Hydraulic Valve Test Bench | 1 Set |
| 8. | Measuring Cylinders / Flow Meter | 4 |
| 9. | Stop Watch | 5 |
| 10. | Transparent Pipes for Flow Visualization | 3 Sets |
| 11. | Hydraulic Seals & Valve Cut Section Models | 2 Sets |
| 12. | Hydraulic Motor Test Kit | 1 Set |
| 13. | Computer System with Simulation Software (Hydraulic Systems) | 2 PCs |
| 14. | Safety Goggles | 25 |
| 15. | Tool Kit (Spanner Set, Screwdrivers, Allen Keys, etc.) | 5 Sets |
| 16. | White Board & Markers for Circuit Drawing | - Boards |

| List of Consumables |  |  |
| --- | --- | --- |
| S. No | Items | Quantity |
| 1. | Hydraulic Oil (Standard Grade) | 40 Litres |
| 2. | Marking Chalk / Soapstone | 30 Pieces |
| 3. | Rubber Seals and Gaskets (Assorted sizes) | 50 Pieces |
| 4. | Teflon Tape | 20 Rolls |
| 5. | Transparent Tubing (for experiments) | 30 Meters |
| 6. | Lubricating Oil | 5 Litres |
| 7. | Thread Sealant | 10 Bottles |
| 8. | Clean Rags / Wiping Cloths | 100 Pieces |
| 9. | Hand Gloves (Rubber/Nitrile for fluid handling) | 25 Pairs |
| 10. | Washers and Small Fittings | 100 Pieces |
| 11. | Cleaning Spray / Degreaser | 5 Bottles |
| 12. | Fluid Sample Containers | 25 |
| 13. | Disposable Aprons | 25 |
| 14. | Lab Notebooks / Recording Sheets | 25 |

### 5.3 0713E&E4103 Calibrate Electrical Equipment

Overview:

This competency standard covers the skills and knowledge required to calibrate ammeter, voltmeter, ohmmeter, multi-meter, capacitor, inductor and 2-wire/4-wire resistor by direct comparison method.

| Competency Units | Performance Criteria |
| --- | --- |
| Perform Pre Calibration activity | - Perform functional and physical check of under test equipment/UUT (Unit Under Test) as per SOPs. - Prepare equipment receipt with specifications and allot unique code. - Keep the equipment in controlled environment for thermal stabilization as per SOPs. - Turn ON the equipment for warm-up as per SOPs. - Record the under-test equipment specifications, environmental condition of laboratory as per procedures. |
| Calibrate Ammeter | - Select reference/Standard Current Source as per SOPs. - Connect cable on the basis of under test ammeter range as per SOPs. - Connect the under-test ammeter with Reference/Standard Current Source at current terminals as per SOPs. - Select calibration points on under test ammeter as per SOPs. - Perform zeroing on under test as per SOPs. - Verify the connections are as per connection diagram in the equipment manual before applying current. - Apply the Reference current and record the value displayed on the under-test ammeter and Reference. - Change the reference value and observe it on under test equipment. - Take at least three set of measurement on each calibration point. - Take values in ascending (zero to maximum) order then descending (max to zero) order and again ascending order. |
| Calibrate Voltmeter | - Select the Reference/Standard Voltage Source as per SOPs. - Connect the under-test voltmeter with Reference/Standard Voltage Source at voltage terminals. - Select calibration points on under test voltmeter as per procedures. - Perform zeroing on under test as per SOPs. - Verify the connections are as per connection diagram in the equipment manual before applying voltage - Apply the Reference voltage and record the value displayed on the under-test voltmeter and Reference. - Change the reference value and observe it on under test equipment. - Take at least three set of measurement on each calibration point. - Take values in ascending (zero to maximum) order then descending (max to zero) order and again ascending order. - Stop the voltage source and remove the connecting cables as per procedures. |
| Calibrate Ohmmeter | - Select the Reference/Standard Resistance Source (Fixed/Discrete) as per SOPs. - Connect the under-test ohmmeter with Reference/Standard Resistance Source at resistance terminals as per SOPs. - Select calibration points on under test ohmmeter as per procedure. - Check zero error by shortening the probes and perform zeroing on under test as per SOPs. - Verify the connections are as per connection diagram in the equipment manual before applying resistance - Apply the Reference resistance and record the value displayed on the under-test ohmmeter and Reference. - Change the reference value and observe it on under test equipment. - Take at least three set of measurement on each calibration point. - Take values in ascending (zero to maximum) order then descending (max to zero) order and again ascending order. - Stop the resistance source and remove the connecting cables as per SOPs. |
| Calibrate multimeter | - Select the Reference/Standard according to the multi-meter specifications. - Connect the under test multi-meter with Reference/Standard as per selected parameter. - Select parameter (Voltage AC/DC, Current AC/DC, Resistance, Capacitance) on both Reference and under test equipment one by one as per SOPs. - Check zero error for each parameter and nullify as per SOPs. - Verify the connections are as per connection diagram in the equipment manual before applying Reference value for each parameter - Apply the Reference value of each parameter and record the value displayed on the under test Multimeter and Reference. - Take at least three set of measurement on each calibration point. - Take values in ascending (zero to maximum) order then descending (max to zero) order and again ascending order. - Stop the Standard Reference and remove the connecting cables as per SOPs. |

Knowledge & Understanding

- Explain Calibration and technical procedure for the calibration of ammeter, voltmeter,

ohmmeter, multi-meter, inductor, capacitor and resistor.

- Differentiate between Reference Standard and (Unit under Test) UUT.

- Explain resolution, standard deviation, and uncertainty.

- Explain difference between precision and accuracy

- Differentiate between fixed and discrete resistor

- Explain calculation method of error off error and uncertainty budget

- What is the coverage factor

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Calibrate Standard Inductor as per instructions.

Consumables, Tools, Machinery & Equipment

| List of Tools, Machinery & Equipment |  |  |
| --- | --- | --- |
| S. No | Items | Quantity |
| 1. | Calibration Bench Setup | 1 Unit |
| 2. | Standard Calibrated Ammeter (Digital) | 2 Units |
| 3. | Standard Calibrated Voltmeter (Digital) | 2 Units |
| 4. | Precision Ohmmeter | 2 Units |
| 5. | Calibrated Multimeter (Reference Standard) | 2 Units |
| 6. | Function Generator | 1 Unit |
| 7. | Variable Power Supply (0-30V, 5A) | 2 Units |
| 8. | Digital Oscilloscope | 1 Unit |
| 9. | Test Leads with Banana Plugs | 10 Sets |
| 10. | Safety Gloves and Mats | 5 Sets |
| 11. | Tool Kit (Screwdrivers, Wire Cutter, etc.) | 5 Sets |
| 12. | Insulation Resistance Tester | 1 Unit |
| 13. | Work Benches with Electrical Boards | 5 Units |

| List of Consumables |  |  |
| --- | --- | --- |
| S. No | Item | Quantity |
| 1. | Marker Pens and Labels | 25 Sets |
| 2. | Electrical Tapes | 10 Rolls |
| 3. | Fuses (Assorted Ratings) | 100 Units |
| 4. | Solder Wire | 500 Grams |
| 5. | Flux Paste | 5 Tins |
| 6. | Cleaning Alcohol (Isopropyl) | 5 Liters |
| 7. | Cotton Swabs & Cloth | 25 Sets |
| 8. | Wiring Cables (Flexible, Multi-core) | 100 Meters |
| 9. | Notebooks and Calibration Log Sheets | 25 Units |
| 10. | Connector Terminals | 200 Pieces |
| 11. | Batteries for Multimeters (9V/AA) | 50 Units |
| 12. | Heat Shrink Sleeves | 50 Pieces |

### 5.4 0713E&E4104 Diagnose Electrical Fault in Generator

Overview:

This Competency Standard covers the skills and knowledge required to inspect and service ignition system, inspect and service alternator, inspect and service display panel, inspect and service governor /Actuator System, inspect and service charging system, inspect and service warning system, to diagnose electric fault (s) in generator.

| Competency Units | Performance Criteria |
| --- | --- |
| Inspect/Service Ignition System | - Identify the tools and equipment as per job requirement. - Check DC power supply of ignition coil and distributor as per SOPs. - Check HT leads as per SOPs. - Check spark plugs as per SOPs. |
| Inspect/Service Alternator | - Identify the tools and equipment as per job requirement. - Check DC output voltage as per SOPs. - Check belt as per SOPs. |
| Inspect/Service Warning System | - Identify tools and equipment as per job requirement. - Check oil sensor as per SOPs. - Check temperature sensor as per SOPs. - Check fuel sensor as per SOPs. - Check over/under load module as per SOPs. |
| Inspect/Service Charging System | - Identify the tools and equipment as per job requirement. - Check battery power leads as per SOPs. - Check charging circuit of alternator as per SOPs. |
| Troubleshoot Wiring | - Identify the tools and equipment for checking of supply. - Check the main supply as per SOPs. - Check the breakers as per SOPs. - Ensure the supply off as per SOPs. - Perform open circuit and short Circuit test with meter as per SOPs. - Identify the faults as per procedures. - Remove the fault as per SOPs. |

Knowledge & Understanding

- Define Ignition coil and Distributor.

- Define High Tension (HT) Leads.

- Functions of Spark Plug.

- Describe DC alternator.

- Knowledge about voltage of Alternator.

- Knowledge about Display Panel.

- Data Screen.

- Types of circuit breakers / Relays.

- Describe Governor / Actuator.

- Describe charging system.

- Describe Warning system.

- Describe open circuit test.

- Describe short circuit test.

- Define fuse, miniature circuit breaker.

- Distinguish between fuse and miniature circuit breaker.

- List the parts of fuse & M.C.B.

- Compare the advantages & disadvantages of fuse & M.C.B.

- Classify cables with respect to insulation, core, voltage grade & current carrying capacity.

- Calculation of cable size.

- Find size of cable for respective load.

- Name components of earthling system.

- Define earth electrode, earth continuity conductor &earthling lead.

- Explain the earth fault current.

- Find size of earth continuity conductor, earthling lead & earth electrodes.

Critical Evidence(s)

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Differentiate between Ignition coil and distributor.

- List functions of High Tension (HT) Leads.

- List functions of Spark Plug.

- List functions of Display Panel / Data Screen.

Consumables, Tools, Machinery & Equipment

| List of Tools, Machinery & Equipment |  |  |
| --- | --- | --- |
| S. No | Items | Quantity |
| 1. | Digital Multimeter (True RMS) | 5 Units |
| 2. | Analog Multimeter | 3 Units |
| 3. | Clamp Meter | 3 Units |
| 4. | Battery Load Tester | 2 Units |
| 5. | Ignition System Tester | 2 Units |
| 6. | Timing Light | 2 Units |
| 7. | Alternator Test Bench | 1 Unit |
| 8. | Starter Motor Bench Tester | 1 Unit |
| 9. | Auto Electrical Diagnostic Tool | 1 Unit |
| 10. | Insulation Resistance Tester (Megger) | 2 Units |
| 11. | Basic Hand Tool Set (Pliers, Screwdrivers, etc.) | 5 Sets |
| 12. | Wire Stripper & Crimper Tool | 5 Sets |
| 13. | Safety Gloves and Goggles | 10 Sets |
| 14. | Workbenches with Electrical Panels | 5 Units |

| List of Consumables |  |  |
| --- | --- | --- |
| S. No | Item | Quantity |
| 1. | Electrical Tape (Insulated) | 10 Rolls |
| 2. | Fuses (Assorted Ratings) | 100 Pieces |
| 3. | Wiring Harness Samples | 10 Sets |
| 4. | Terminal Lugs and Connectors | 200 Pieces |
| 5. | Battery Terminals | 50 Pieces |
| 6. | Cleaning Spray (Contact Cleaner) | 5 Cans |
| 7. | Zip Ties | 300 Pieces |
| 8. | Heat Shrink Tubing | 100 Pieces |
| 9. | Carbon Brushes (Assorted Sizes) | 30 Sets |
| 10. | Insulating Sleeves | 50 Meters |
| 11. | Marker Pens and Cable Tags | 25 Sets |
| 12. | Notebooks and Fault Logs | 25 Units |

### 5.5 0713E&E4105 Carryout Transmission of Electrical Power

Overview:

This Competency standard deals with the skills and knowledge required to select the conductor for transmission line, sort different effects on Transmission lines during conduction, select the right insulator from different types according to the requirement, make foundation and erect poles and towers, perform stringing work and sag of transmission lines, install lightning arrester in a transmission system as per requirement.

| Competency Units | Performance Criteria |
| --- | --- |
| Select The Conductor For Transmission Line. | - Selected tools and equipment according to job requirement. - Select voltage level for transmission as per SOPs. - Select the conductor in accordance with current value as per procedures. |
| Select Insulator | - Select insulator according to utility as per SOPs. - Separate healthy, punctured and broken disk as per procedures. - Calculate number of disks according to voltage level of transmission lines. |
| Perform Stringing Work And Sag Of Transmission Lines | - Calculate sag and bring it in accordance with clearance standards of WPADA/NTDCL. - Remove effects of wind and ice on Transmission Line as per SOPs. - Adjust sag in line with existing temperature as per SOPs. |
| Install Lightning Arrester In A Transmission System As Per Requirement | - Select Lightening Arrestors for Substation/Grid station with respect to the current. - Install lightning arrestor as per SOPs. - Carryout connections for grounding as per SOPs. |

Knowledge & Understanding

- Describe the Current carrying capacity of different conductors.

- Describe the benefits/cost of high voltage Transmission.

- Define Ferranti effect.

- Define Skin effect.

- Define corona effect.

- Define the types of insulators.

- Define suspension type and string.

- Define Cree page distance.

- Define tower and pole type.

- Define Foundation type.

- Describe tower assembly.

- Elaborate Standards for erection and foundation.

- Define hazards and safety codes.

- Describe Sag calculation.

- Explain Effect of weather condition on sag.

- Explain Effect of sag on insulator assembly.

- Define Lightning arrester with respect its types according to the requirements.

- Define usage of Lightning Arrester.

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Install lightning arrestor as per instructions.

- Check resistance of installed lightening arrestor as per instructions.

Consumables, Tools, Machinery & Equipment

| List of Tools, Machinery & Equipment |  |  |
| --- | --- | --- |
| S. No. | Items | Quantity |
| 1 | Lightning Arrester | 05 |
| 2 | Chain block | 25 |
| 3 | Temperature gage | 25 |
| 4 | Safety material | 25 |
| 5 | Dipole | 25 |
| 6 | Conductors. (Different Types) | As Required |
| 7 | Insulators. (Different Types) | As Required |
| 8 | Poles | As Required |

### 5.6 0713E&E4106 Carryout Distribution of Electrical Power

Overview:

This Competency standard deals with the skills and knowledge required to select he conductor for distribution of power, Improve the Power factor, Separate the correct insulator from different types according to the requirement, Make Foundation and Erect poles and structures, Supervise construction of Trenches Cable try and select appropriate cable, Perform stringing work and sag of distribution lines, Measure performance of distribution lines and take steps to improve Primary and secondary distribution, Install the equipment for grounding of Substation/Transmission lines, Select and justify the use of reactor in a system, Install Lightning Arrester in a Distribution system as per requirement, Install Lightning Arrester in a Distribution system as per requirement.

| Competency Units | Performance Criteria |
| --- | --- |
| Select The Conductor For Distribution Of Power. | - Select tools and equipment according to job requirement. - Select the voltage level for Distribution as per SOPs. - Select the conductor in accordance with current (A) value. |
| Select The Correct Insulator | - Select appropriate insulator according to utility. - Separate healthy, broken and punctured disk as per SOPs. - Calculate number of disks according to voltage level of transmission lines as per procedures. |
| Supervise Construction Of Trenches ,Cable Try And Select Appropriate Cable | - Select cable among belted, screamed and pressure cable as per SOPs. - Supervise trench among direct laying and draw solid system as per SOPs. - Select cable tray as per procedures. |
| Install The Equipment For Grounding Of Substation/Trans Mission Lines | - Carryout grounding (Resistance, Reactance, solid) as per SOPs. - Supervise grounding in accordance with WAPDA as per SOPs. - Select copper conductor depending on the capacity of grid. - Test resistance of ground using Magger meter as per SOPs. - Carry out the jointing of copper conductor as per SOPs. |

Knowledge & Understanding

- Describe the Current carrying capacity of different conductors.

- Explain the benefits/cost of high voltage Transmission.

- Define the power Factor.

- Define the types of insulators.

- Define suspension type and string.

- Define Cree page distance.

- Define tower and pole type.

- Define Foundation type.

- Describe structure assembly.

- Understand Standards.

- Define hazards and follow safety codes.

- Explain Cable sizing.

- Describe Cable tray types.

- Describe Trenches Standards.

- Explain Importance of insulation material for selection of appropriate cables.

- Calculate Sag.

- Explain effect of weather condition on sag.

- Explain effect of sag on insulator assembly.

- Describe voltage drop, voltage regulation and power loses in a distribution system.

- Explain the reasons of voltage drop on a line.

- Explain Concepts of grounding.

- Describe Necessity of grounding.

- Describe Types of grounding.

- Describe Resistance Requirement for grounding.

- Explain WAPDA standards.

- Explain types and working principal of reactors.

- Explain Advantages and disadvantages of different types of reactors.

- Define Lightning arrester with respect it’s types according to the requirements.

- Define usage of Lightning Arrester.

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Select cable among belted, screamed and pressure cable as per instructions.

- Test resistance of ground using Magger meter as per instructions.

Consumables, Tools, Machinery & Equipment

| List of Tools, Machinery & Equipment |  |  |
| --- | --- | --- |
| S.No | Items | Quantity |
| 1 | Power factor improvement panel | 25 |
| 2 | Voltmeter | 25 |
| 3 | Temperature gage | 25 |
| 4 | Chain block | 25 |
| 5 | Theodolite | 01 |
| 6 | Megger | 25 |
| 7 | Earthling equipment | 25 |
| 8 | Insulators | 25 |
| 9 | Poles | As Required |

### 5.7 0713E&E4107 Carryout Protection of Distribution and Transmission System

Overview:

This Competency standard deals with the skills and knowledge required to Install the equipment for grounding of Substation/Transmission lines, Categorize and rectify the symmetrical and asymmetrical faults, Install Circuit breaker in a distribution system (Substation/Grid station), Install an isolator at grid station/substation, install appropriate relays for the protection of power system, Carry out Bus Bar protection, Carry out time graded protection of feeder, Install a fuse in a circuit (Transformer and Distribution panels), Supervise Protection of power transformer, Carryout protection arrangement for alternator.

| Competency Units | Performance Criteria |
| --- | --- |
| Install Relay For Protection | - Select relay according to job requirement. - Make connections of relay according to given drawing. - Perform basic settings of relay as per specifications. |
| Perform Operations Of Relay | - Identify type of relay installed. - Interpret operation manual of relay. - Perform advanced setting of relay as per specifications. |
| Perform Troubleshooting Of Relay | - Check connections of relay as per SOPs. - Reset functionality of relay as per SOPs. - Inject current to check healthiness of operation of relay as per SOPs. |
| Carry Out Bus Bar Protection | - Check connection of differential relay for bus bar as per SOPs. - Perform frame leakage protection as per SOPs. - Perform circuiting current protection as per SOPs. |
| Carry Out Protection Of Power Transformer | - Select differential relay as per job requirement. - Make connections of CT with differential relay as per SOPs. - Perform setting of current transformer (CT) as per SOPs. |
| Install The Equipment For Grounding Of Substation/Trans Mission Lines | - Carryout grounding (Resistance, Reactance, solid) as per instructions. - Supervise the grounding in accordance with WAPDA Standards. - Select copper conductor as per instructions. - Test the resistance of ground using Magger meter. - Carry out the jointing of copper conductor as per SOPs. |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out the tasks covered in this competency standard. This includes the knowledge of:

- Explain Type of faults in power system

- Explain the problems arising due to short circuit on power line

- Describe Necessity of Circuit breaker

- Explain Working principal for fault.

- Explain different types of circuit breaker

- Define different types of relays

- Define the working principal of relays of different type respectively

- Explain the purpose of relays and the need of relays

- Describe the Selection criteria.

- Describe working of frame protection

- Explain concept of time graded protection.

- Define Buss Bar protection

- Describe rating of circuit breaker

- Explain Using principal of an isolator

- Describe Usage of isolator

- Describe Types of isolator

- Describe working principal

- Explain rating parameters

- Explain fuse materials

- Define types of fuse

- Define advantages and disadvantages.

- Define faults on transformer

- Describe Merz-prize system

- Explain protection for different types of connection.

- Explain Alternators faults

- Describe Protection against stator faults

- Explain Balanced earth fault protection

- Explain stator in-turn protection

- Explain Concepts of grounding

- Describe Necessity of grounding

- Describe Types of grounding

- Describe Resistance Requirement for grounding

- Explain WAPDA standards

- Explain types and working principal of reactors.

- Explain Advantages and disadvantages of different types of reactors.

- Define Lightning arrester with respect it’s types according to the requirements

- Define usage of Lightning Arrester

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Carryout protection arrangement for alternator as per instructions.

Consumables, Tools, Machinery & Equipment

| List of Tools, Machinery & Equipment |  |  |
| --- | --- | --- |
| S.No | Items | Quantity |
| 1. | Protective Relay Test Set | 2 Units |
| 2. | Digital Multimeter (True RMS) | 5 Units |
| 3. | Clamp Meter | 3 Units |
| 4. | Megger (Insulation Resistance Tester) | 2 Units |
| 5. | Primary Injection Kit | 1 Unit |
| 6. | Secondary Injection Test Set | 1 Unit |
| 7. | CT/PT Analyzer | 1 Unit |
| 8. | Relay Calibration Bench | 1 Unit |
| 9. | Earth Resistance Tester | 2 Units |
| 10. | Safety Helmet and Gloves | 10 Sets |
| 11. | Tool Kit (Pliers, Wrenches, Screwdrivers) | 5 Sets |
| 12. | Portable Grounding and Shorting Equipment | 2 Sets |
| 13. | Substation Layout Board (Demo/Training) | 1 Unit |
| 14. | Bus Bar Assembly Demo Unit | 1 Unit |

| List of Consumables |  |  |
| --- | --- | --- |
| S. No | Item | Quantity |
| 1. | Insulating Tape (High Voltage) | 15 Rolls |
| 2. | Cable Lugs and Connectors | 200 Pieces |
| 3. | Ferrules and Cable Tags | 250 Pieces |
| 4. | Heat Shrink Tubing | 50 Meters |
| 5. | Grounding Rods (for training setup) | 5 Units |
| 6. | Solder Wire and Flux | 10 Sets |
| 7. | Cable Markers | 100 Pieces |
| 8. | Zip Ties | 300 Pieces |
| 9. | Contact Cleaner Spray | 5 Cans |
| 10. | Electrical Safety Posters/Charts | 5 Sets |
| 11. | Documentation Sheets and Relay Logs | 25 Books |

### 5.8 0713E&E4108 Install Turbine

Overview:

This competency standard covers the skills and knowledge required to verify foundation layout of turbines, assemble hydro turbine, make mechanical coupling, perform alignment and calibration of turbine, perform testing and commissioning, perform inspection and documentation.

| Competency Units | Performance Criteria |
| --- | --- |
| Verify Foundation Layout | - Check Load-Bearing Capacity of foundation as per SOPs. - Check Soil Suitability of site as per procedures. - Check durability of material as per procedures. - Check Leveling of foundation as per procedures. |
| Assemble Hydro Turbine | - Position turbine fix/stay vanes as per SOPs. - Position the turbine base onto the foundation as per procedures. - Install the main shaft onto the turbine base as per procedures. - Install and connect necessary systems as per procedures. |
| Perform Mechanical Coupling | - Align the turbine shaft and generator as per SOPs. - Install the coupling between the turbine shaft and generator shaft as per procedures. - Tighten the coupling bolts and studs as per SOPs. - Perform a test run as per procedures. |
| Perform Alignment and Calibration of Turbine | - Align the turbine components on the foundation as per SOPs. - Verify all components are within the manufacturer's specified tolerances for alignment. - Perform calibration of the control systems as per procedures. - Conduct operational tests of turbine as per procedures. |
| Perform Testing and Commissioning | - Perform Pre-Commissioning inspection of all turbine components as per SOPs. - Conduct a dry run test to check the mechanical systems as per procedures. - Control penstock gate of the turbine as per procedures. - Verify that the turbine meets design specifications as per procedures. - Calibrate control systems, and make any necessary adjustments as per procedures. |
| Perform Inspection and Documentation | - Conduct visual inspection of the turbine as per SOPs. - Measure key parameters Using instruments as per procedures. - Record all inspection findings, test results, and any maintenance or adjustments made as per procedures. |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes the knowledge of:

- foundation for hydro turbine

- hydro turbine types

- calibration process of hydro turbine

- testing and commissioning of hydro turbine

- inspection criteria

Critical Evidence(s)

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Draw design diagrams of turbine and generator assembly as per instructions.

Consumables, Tools, Machinery & Equipment

| List of Tools, Machinery & Equipment |  |  |
| --- | --- | --- |
| S.No | Items | Quantity |
| 1. | Hydraulic Turbine Model (Training Unit) | 1 Unit |
| 2. | Alignment Tools (Dial Gauge, Feeler Gauge) | 3 Sets |
| 3. | Mechanical Coupling Kit | 2 Sets |
| 4. | Torque Wrench | 3 Units |
| 5. | Foundation Layout Laser Level | 2 Units |
| 6. | Portable Crane / Chain Block | 2 Units |
| 7. | Vernier Caliper / Micrometer Set | 5 Sets |
| 8. | Vibration Analyzer | 1 Unit |
| 9. | Calibration Equipment Set | 1 Set |
| 10. | Testing & Commissioning Panel (Demo Type) | 1 Unit |
| 11. | Inspection Flashlight and Mirror Set | 3 Sets |
| 12. | Safety PPE (Helmet, Gloves, Goggles) | 15 Sets |
| 13. | Tool Kit (Spanners, Screwdrivers, Allen Keys) | 5 Sets |

| List of Consumables |  |  |
| --- | --- | --- |
| S.No | Item | Quantity |
| 1. | Foundation Bolts and Anchors | 50 Pieces |
| 2. | Shims and Alignment Plates | 100 Pieces |
| 3. | Thread Lock and Grease | 10 Tubes |
| 4. | Marking Chalks / Paints | 10 Sets |
| 5. | Cable Ties and Clamps | 200 Pieces |
| 6. | Cleaning Rags and Wipes | 100 Pieces |
| 7. | Documentation and Inspection Log Sheets | 25 Books |
| 8. | Calibration Stickers and Labels | 100 Pieces |
| 9. | Gasket Sheets (for mock flange setup) | 5 Sheets |
| 10. | Lubricating Oil for Testing | 10 Liters |

### 5.9 0713E&E4109 Install Generator

Overview:

This competency standard covers the skills and knowledge required to verify foundation layout, assemble synchronous generator, make, perform alignment and calibration of generator, make electrical connection, perform testing and commissioning, perform inspection and documentation.

| Competency Units | Performance Criteria |
| --- | --- |
| Verify Foundation Layout | - Inspect visible cracks, deformation, or signs of wear and tear on the foundation as per procedures. - Inspect the soil or ground around the foundation for any signs of erosion, waterlogging, or instability as per procedures. - Compile report of inspection as per SOPs. |
| Cu2. Perform A.C Generator Coupling | - Position the generator onto the foundation as per SOPs. - Couple generator and turbine shaft as per procedures. - Tighten the coupling bolts and studs as per SOPs. - Install and connect necessary systems as per SOPs. |
| Cu3. Perform Alignment and Calibration of Generator | - Identify and select tools according to the job requirement. - Align the turbine shaft and generator as per SOPs. - Perform a test run to verify that the coupling functions correctly as per SOPs. |
| Cu4. Make Electrical Connections | - Select tools according to the job requirement. - Connect power output terminals with transformer/panel board as per SOPs. - Connect current transformer (CT) and potential transformer (PT) as per SOPs. - Check grounding connections of generator as per SOPs. |
| Cu5. Perform Testing and Commissioning | - Select tools according to job requirement. - Check speed and frequency of generator as per SOPs. - Check voltage and current of generator as per SOPs. - Check vibrations produced by generator as per SOPs. |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes the knowledge of:

- Understanding of Synchronous generator and Asynchronous generator.

- Knowledge of Cooling and lubrication system of synchronous generator.

Critical Evidence(s)

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Perform coupling of given generator and turbine as per instructions.

- Determine RPM, frequency and voltage of the given generator according to instructions.

Consumables, Tools, Machinery & Equipment

| List of Tools, Machinery & Equipment |  |  |
| --- | --- | --- |
| S.No | Items | Quantity |
| 1. | Generator Installation Training Unit | 1 Unit |
| 2. | Alignment Tools (Dial Gauge, Feeler Gauge) | 3 Sets |
| 3. | Mechanical Coupling Kit (for AC generator) | 2 Sets |
| 4. | Torque Wrench | 3 Units |
| 5. | Foundation Layout Laser Level | 2 Units |
| 6. | Electrical Testing Kit (Multimeter, Clamp Meter) | 5 Sets |
| 7. | Calibration Equipment Set | 1 Set |
| 8. | Electrical Tool Kit (Crimper, Wire Stripper, etc.) | 5 Sets |
| 9. | Lifting Equipment (Chain Block or Hoist) | 2 Units |
| 10. | Insulation Resistance Tester (Megger) | 1 Unit |
| 11. | Safety PPE (Gloves, Helmet, Goggles) | 15 Sets |
| 12. | Vibration Analyzer | 1 Unit |

| List of Consumable Material |  |  |
| --- | --- | --- |
| S.No | Item | Quantity |
| 1. | Foundation Bolts and Grouting Material | 40 Sets |
| 2. | Electrical Connectors (Lugs, Terminals) | 200 Pieces |
| 3. | Cable Marking Tags and Labels | 150 Pieces |
| 4. | Insulation Tape & Heat Shrink Tubes | 30 Rolls |
| 5. | Cable Ties and Clamps | 200 Pieces |
| 6. | Cleaning Rags and Degreaser | 100 Pieces |
| 7. | Marking Chalks / Paint | 10 Sets |
| 8. | Documentation Sheets and Logbooks | 25 Books |
| 9. | Grease / Thread Locker for Coupling | 10 Tubes |
| 10. | Gasket Material for Flange Joints | 5 Sheets |
| 11. | Electrical Cables (For Demo Connections) | 30 Meters |

### 5.10 0713E&E4110 Control HP plant shutdown for emergency standby electrical systems

Overview:

This competency standard is intended for people in a senior position who are responsible for controlling HP plant shutdown for emergency standby electrical systems. People holding credit for this competency standard are able to: Prepare emergency standby electrical system; shut down and isolate emergency standby electrical system; service emergency standby electrical system; monitor emergency standby electrical system and stabilize transient condition.

| Competency Units | Performance Criteria |
| --- | --- |
| Prepare Emergency Standby Electrical System | - Carry out pre-condition’s preparation for plant as per SOPs. - Prepare plant for service as per SOPs. - Document preparation for plant shut-down as per SOPs. |
| Shut Down and Isolate Emergency Standby Electrical System | - Carry out pre-condition for shutdown as per SOPs. - Isolate emergency standby electrical system as per SOPs. - Document plant shutdown and isolation as per SOPs. |
| Service Emergency Standby Electrical System | - Apply hazard and risk identification as per SOPs. - Perform servicing of electrical system as per SOPs. - Document servicing activity as per SOPs. |
| Monitor Emergency Standby Electrical System and Stabilize Transient Condition | - Monitor plant operating condition as per SOPs. - Identify and react upon out of normal conditions as per SOPs. - Compare actual output values against expected requirements as per procedures. - Document transient conditions, actions and results. |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes the knowledge of:

- Safety requirements; Specifications; Hazard identification.

- Impact of decision on plant operation.

- Pre-condition procedures.

- Shutdown procedure.

- Isolation procedure.

- Documentation process.

- Problem solving process.

- Energy conversion process.

- Mechanical plant component application and interrelation.

- Electrical plant component application and interrelation.

- Function of instrumentation components.

- Documentation process.

- Priority setting.

- Documentation process.

Critical Evidence(s)

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- List steps for preparation for HP plant shutdown.

- List steps to execute the shutdown process.

- List steps for servicing and maintenance during shutdown.

- Explain system monitoring and safety compliance procedure.

Consumables, Tools, Machinery & Equipment

| List of Tools, Machinery & Equipment |  |  |
| --- | --- | --- |
| S.No | Items | Quantity |
| 1. | Emergency Standby Generator (Training Purpose) | 1 Unit |
| 2. | Circuit Breaker Testing Kit | 1 Set |
| 3. | Lockout/Tagout Kit | 3 Sets |
| 4. | Electrical Panel Simulator (for emergency system) | 1 Unit |
| 5. | Battery Bank with Inverter (for training use) | 1 Set |
| 6. | Digital Multimeter | 5 Units |
| 7. | Clamp Meter | 3 Units |
| 8. | Electrical Tool Kit (Insulated) | 5 Sets |
| 9. | Phase Rotation Tester | 2 Units |
| 10. | Load Bank (for testing under load conditions) | 1 Unit |
| 11. | Safety PPE Kit (Helmet, Gloves, Boots, Goggles) | 15 Sets |
| 12. | Generator Shutdown Simulator Panel | 1 Unit |

| List of Consumables |  |  |
| --- | --- | --- |
| S.No | Item | Quantity |
| 1. | Fuses and Miniature Circuit Breakers (MCBs) | 40 Pcs |
| 2. | Cable Lugs and Connectors | 150 Pcs |
| 3. | Electrical Tape and Insulation Tubes | 30 Rolls |
| 4. | Cleaning Spray for Electrical Contacts | 10 Cans |
| 5. | Wiring Labels and Tags | 100 Pcs |
| 6. | Nuts, Bolts and Fasteners (Electrical) | 200 Pcs |
| 7. | Marking Chalks and Stickers | 10 Sets |
| 8. | Logbooks and Monitoring Sheets | 25 Books |
| 9. | Cable Ties and Mounting Clips | 200 Pcs |
| 10. | Safety Signs and Labels for Emergency System | 10 Sets |
| 11. | Spare Indicator Bulbs/LEDs for Control Panel | 50 Pcs |

### 5.11 0713E&E4111 Analyze faults in HP plant operation

Overview:

This competency standard is intended for people in a senior position who analyses faults in HP plant operations. People holding credit for this competency standard are able to: Plan and prepare for fault analysis; test plant and auxiliary equipment operation; analyses plant and auxiliary equipment faults; and record findings.

| Competency Units | Performance Criteria |
| --- | --- |
| Diagnose Faults in HP Plant | - Select tools and equipment according to job requirement. - Adopt safety practices as per SOPs. - Interpret specifications and drawings regarding civil structure. - Diagnose faults in MHP plant as per SOPs. |
| Test Plant and Auxiliary Equipment Operation | - Perform tests according to SOPs. - Observe plant and equipment for correct operational response as per procedures. - Take corrective action when response is not in accordance with documentation as per SOPs. - Return plant and equipment to required operation status on completion of test as per procedures. |
| Analyze Plant and Allied Equipment Faults | - Analyze technical and operational information. - Determine necessary actions to rectify fault as per SOPs. - Maintain plant integrity and personnel safety as per procedures. - Take action to rectify the fault as per procedures. |
| Prepare Documentation of Faults Diagnose | - Mention the fault occurred in the logbook as per SOPs. - Prepare final report with findings and recommendations. - Submit report to supervisor as per SOPs. |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes the knowledge of:

- Safety requirements; Specifications; Hazard identification.

- Drawing and symbol specifications.

- Tools and equipment and calibration meter.

- Test procedures.

- Dealing with unplanned events.

- Operation of plant components.

- Safe working procedures.

- Analyzing plant faults.

- Monitoring plant operation.

- Safe working procedures.

- Work completion details.

Critical Evidence(s)

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- List steps for fault diagnosis in HP.

- List steps for inspection & data collection.

Consumables, Tools, Machinery & Equipment

| List of Tools, Machinery & Equipment |  |  |
| --- | --- | --- |
| S.No | Items | Quantity |
| 1. | MHP Plant Fault Simulation Kit | 1 Unit |
| 2. | Digital Multimeter | 5 Units |
| 3. | Clamp Meter | 3 Units |
| 4. | Insulation Resistance Tester (Megger) | 2 Units |
| 5. | Thermal Imaging Camera (for hot-spot detection) | 1 Unit |
| 6. | Oscilloscope (for signal diagnostics) | 1 Unit |
| 7. | Vibration Analyzer (for mechanical fault detection) | 1 Unit |
| 8. | Electrical Tool Kit (Insulated) | 5 Sets |
| 9. | Laptop with Diagnostic Software | 2 Units |
| 10. | Whiteboard with Markers (for fault analysis sessions) | 1 Set |
| 11. | Fault Logging & Analysis Charts | 5 Sets |

| List of Consumable |  |  |
| --- | --- | --- |
| S.No | Item | Quantity |
| 1. | Fault Report Logbooks | 25 Books |
| 2. | Electrical Contact Cleaner Spray | 10 Cans |
| 3. | Fuses, MCBs and Relays (Assorted) | 50 Pcs |
| 4. | Cable Lugs and Connectors | 100 Pcs |
| 5. | Insulation Tape | 30 Rolls |
| 6. | Tagging Labels for Fault Identification | 100 Pcs |
| 7. | Graph Paper and Analysis Sheets | 100 Sheets |
| 8. | Stickers for Fault Area Marking | 50 Pcs |
| 9. | Printouts of Fault Diagnosis Flowcharts | 25 Sets |
| 10. | Pens, Pencils, Erasers, Rulers | 25 Sets |

### 5.12 0713E&E4112 Carry out preventive maintenance procedures as part of HP operations

Overview:

This competency standard is intended for those who carry out preventive maintenance as part of HP operations. ‘Preventive maintenance’ in this context refers to the systematic care and servicing of machinery, equipment and infrastructure by inspection, detection, and correction of early failures either before they occur or before they develop into major defects. People holding credit for this competency standard are able to: Plan and prepare for preventive maintenance; perform daily routine checks; perform preventive maintenance; and complete work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Plan For Preventive Maintenance | - Select tools and equipment as per job requirements. - Adopt safety and regulatory practices as per SOPs. - Interpret drawings as per SOPs. |
| - Perform Daily Routine Checks | - Check for suspended trash or material at screens as per SOPs. - Check for water leakage or overflow as per SOPs. - Check for sand sedimentation as per SOPs. - Check for deformation or crack as per SOPs. - Check for mechanical malfunction as per SOPs. |
| - Perform Preventive Maintenance | - Remove debris as per SOPs. - Flush out sand sedimentation as per procedures. - Remove sand and rocks as per procedures. - Reduce water intake as per SOPs. - Remove/Replace worn or faulty components as per SOPs. - Record maintenance procedures, and report subsequent actions. |
| - Perform Documentation of Preventive Maintenance | - Complete work-related documents as per SOPs. - Perform final quality inspection as per procedures. - Clean up and store tools, equipment and materials as per SOPs. |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes the knowledge of:

- Safety requirements; Specifications; Hazard identification.

- Drawings and symbols specifications.

- Tools and equipment and calibration.

- Inspection requirements.

- Facilities and equipment to be checked include but are not limited to:

  - Intake and waterway; Sedimentation basin, headrace, tailrace, fore bay; penstock; turbine; generator; load stabilizer; transformer; transmission and distribution lines.

- Maintenance procedures.

- Hazards and risks associated with maintenance.

- Consequences of not performing preventive maintenance.

- Checklists and reports, and importance.

- Importance of quality.

- Waste disposal procedures.

- Care of tools and equipment.

Critical Evidence(s)

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- List steps for maintenance planning & scheduling.

- List steps for inspection & monitoring.

- List steps for cleaning & lubrication.

Consumables, Tools, Machinery & Equipment

| List of Tools, Machinery & Equipment |  |  |
| --- | --- | --- |
| S. No | Items | Quantity |
| 1. | Preventive Maintenance Toolkit (spanners, pliers, etc.) | 5 Sets |
| 2. | Digital Multimeter | 5 Units |
| 3. | Infrared Thermometer | 2 Units |
| 4. | Vibration Analyzer | 1 Unit |
| 5. | Grease Gun | 3 Units |
| 6. | Portable Inspection Lamp | 3 Units |
| 7. | Lubrication System Test Kit | 1 Unit |
| 8. | Laptop/Tablet (for digital logs and checklists) | 2 Units |
| 9. | Safety Helmet with Face Shield | 10 Units |
| 10. | Lockout-Tagout (LOTO) Kit | 2 Sets |

| List of Consumables |  |  |
| --- | --- | --- |
| S. No | Item | Quantity |
| 1. | Maintenance Checklist Sheets | 100 Sheets |
| 2. | Grease and Lubricants | 10 Liters |
| 3. | Cleaning Cloths | 50 Pcs |
| 4. | Cable Ties | 100 Pcs |
| 5. | Dust Masks | 50 Pcs |
| 6. | Safety Gloves | 25 Pairs |
| 7. | Replacement Fuses and Nuts | 50 Pcs |
| 8. | Insulation Tape | 30 Rolls |
| 9. | Documentation Logbooks | 25 Books |
| 10. | Labels for Equipment Tagging | 100 Pcs |

### 5.13 On Job Training

Overview:

The on-job training component of this qualification provides learners with the opportunity to apply their acquired skills and knowledge in real world environments. During this phase, students must take on entry level or support roles such as Hydropower Technician, Electrical Maintenance Technician (Hydro), Mechanical Maintenance Technician (Hydro), Plant Maintenance Supervisor, Operations and Maintenance (O&M) Technician and Hydropower System Troubleshooter. These roles span across various hydro power plants that enable learners to contribute in the development of hydro power infrastructures while fulfilling the requirements of qualification.

As alternate arrangement, in case of non-availability of the concerned industry, the trainees may fulfill requirements of the qualification through conduct of project on the pattern of final year students of Diploma of Associate Engineers (DAEs) or Engineering Universities.

Trainees shall install the turbine and generator of a hydro-power system in accordance with technical specifications, set up the transmission and distribution network including protective and switching devices, make accurate electrical connections between the generator and the distribution line, and perform testing and commissioning of the entire network to ensure safe and reliable power delivery, simulating real-world deployment of hydroelectric infrastructure.

# List of Consumables, Tools, Machinery & Equipment

| 4A. List of Consolidated Consumables |  |  |
| --- | --- | --- |
| S.No | Item | Quantity |
| 1 | Hydraulic Oil (Standard Grade) | 40 Liters |
| 2 | Marking Chalk / Soapstone | 30 Pieces |
| 3 | Rubber Seals and Gaskets (Assorted sizes) | 50 Pieces |
| 4 | Teflon Tape | 20 Rolls |
| 5 | Transparent Tubing (for experiments) | 30 Meters |
| 6 | Lubricating Oil | 5 Liters |
| 7 | Thread Sealant | 10 Bottles |
| 8 | Clean Rags / Wiping Cloths | 100 Pieces |
| 9 | Hand Gloves (Rubber/Nitrile for fluid handling) | 25 Pairs |
| 10 | Washers and Small Fittings | 100 Pieces |
| 11 | Cleaning Spray / Degreaser | 5 Bottles |
| 12 | Fluid Sample Containers | 25 |
| 13 | Disposable Aprons | 25 |
| 14 | Lab Notebooks / Recording Sheets | 25 |
| 15 | Marker Pens and Labels | 25 Sets |
| 16 | Electrical Tapes | 10 Rolls |
| 17 | Fuses (Assorted Ratings) | 100 Units |
| 18 | Solder Wire | 500 Grams |
| 19 | Flux Paste | 5 Tins |
| 20 | Cleaning Alcohol (Isopropyl) | 5 Liters |
| 21 | Wiring Cables (Flexible, Multi-core) | 100 Meters |
| 22 | Notebooks and Calibration Log Sheets | 25 Units |
| 23 | Connector Terminals | 200 Pieces |
| 24 | Batteries for Multimeters (9V/AA) | 50 Units |
| 25 | Heat Shrink Sleeves | 50 Pieces |
| 26 | Wiring Harness Samples | 10 Sets |
| 27 | Terminal Lugs and Connectors | 200 Pieces |
| 28 | Battery Terminals | 50 Pieces |
| 29 | Cleaning Spray (Contact Cleaner) | 5 Cans |
| 30 | Zip Ties | 300 Pieces |
| 31 | Heat Shrink Tubing | 100 Pieces |
| 32 | Carbon Brushes (Assorted Sizes) | 30 Sets |
| 33 | Insulating Sleeves | 50 Meters |
| 34 | Marker Pens and Cable Tags | 25 Sets |
| 35 | Notebooks and Fault Logs | 25 Units |
| 36 | Insulating Tape (High Voltage) | 15 Rolls |
| 37 | Ferrules and Cable Tags | 250 Pieces |
| 38 | Grounding Rods (for training setup) | 5 Units |
| 39 | Solder Wire and Flux | 10 Sets |
| 40 | Cable Markers | 100 Pieces |
| 41 | Electrical Safety Posters/Charts | 5 Sets |
| 42 | Documentation Sheets and Relay Logs | 25 Books |
| 43 | Foundation Bolts and Anchors | 50 Pieces |
| 44 | Shims and Alignment Plates | 100 Pieces |
| 45 | Thread Lock and Grease | 10 Tubes |
| 46 | Cable Ties and Clamps | 200 Pieces |
| 47 | Foundation Bolts and Grouting Material | 40 Sets |
| 48 | Cable Marking Tags and Labels | 150 Pieces |
| 49 | Insulation Tape & Heat Shrink Tubes | 30 Rolls |
| 50 | Cleaning Rags and Degreaser | 100 Pieces |
| 51 | Marking Chalks / Paint | 10 Sets |
| 52 | Documentation Sheets and Logbooks | 25 Books |
| 53 | Grease / Thread Locker for Coupling | 10 Tubes |
| 54 | Gasket Material for Flange Joints | 5 Sheets |
| 55 | Electrical Cables (For Demo Connections) | 30 Meters |
| 56 | Fuses and Miniature Circuit Breakers (MCBs) | 40 Pcs |
| 57 | Cleaning Spray for Electrical Contacts | 10 Cans |
| 58 | Wiring Labels and Tags | 100 Pcs |
| 59 | Nuts, Bolts and Fasteners (Electrical) | 200 Pcs |
| 60 | Logbooks and Monitoring Sheets | 25 Books |
| 61 | Cable Ties and Mounting Clips | 200 Pcs |
| 62 | Safety Signs and Labels for Emergency System | 10 Sets |
| 63 | Spare Indicator Bulbs/LEDs for Control Panel | 50 Pcs |
| 64 | Fault Report Logbooks | 25 Books |
| 65 | Electrical Contact Cleaner Spray | 10 Cans |
| 66 | Fuses, MCBs and Relays (Assorted) | 50 Pcs |
| 67 | Tagging Labels for Fault Identification | 100 Pcs |
| 68 | Graph Paper and Analysis Sheets | 100 Sheets |
| 69 | Stickers for Fault Area Marking | 50 Pcs |
| 70 | Printouts of Fault Diagnosis Flowcharts | 25 Sets |
| 71 | Maintenance Checklist Sheets | 100 Sheets |
| 72 | Grease and Lubricants | 10 Litres |
| 73 | Dust Masks | 50 Pcs |
| 74 | Safety Gloves | 25 Pairs |
| 75 | Replacement Fuses and Nuts | 50 Pcs |
| 76 | Documentation Logbooks | 25 Books |
| 77 | Labels for Equipment Tagging | 100 Pcs |
| 78 | 3 wire types (copper, aluminum, steel – 1.5m each) | 100 Meters |
| 79 | Leak detection spray | 20 units |
| 80 | Hydraulic seals | 20 units |
| 81 | Thread seal tape | 20 units |
| 82 | Teflon tape | 20 units |
| 83 | Gaskets | 20 units |
| 84 | Pipe sealant | 20 units |
| 85 | Lab Notebooks / Recording Sheets | 20 units |

| 4B. Consolidated List of Tools, Machinery & Equipment |  |  |
| --- | --- | --- |
| S.No | Item | Quantity |
| 1 | Directories of existing businesses | 25 |
| 2 | Examples of business plans | 25 |
| 3 | Sample of financial plans | 25 |
| 4 | Business planner templates | 25 |
| 5 | Start-up-costs estimator | 25 |
| 6 | Hydraulic Trainer Kit (with actuators, valves, circuit board) | 2 Sets |
| 7 | Flow Measuring Apparatus (Venturi meter / Orifice Meter) | 2 Sets |
| 8 | Pressure Gauge Set (with manometers) | 3 Sets |
| 9 | Impact of Jet Apparatus | 1 Set |
| 10 | Hydraulic Pump Test Rig (Centrifugal & Reciprocating) | 2 Sets |
| 11 | Water Turbine Test Rig (Pelton / Francis / Kaplan) | 2 Sets |
| 12 | Hydraulic Valve Test Bench | 1 Set |
| 13 | Measuring Cylinders / Flow Meter | 4 |
| 14 | Stop Watch | 5 |
| 15 | Transparent Pipes for Flow Visualization | 3 Sets |
| 16 | Hydraulic Seals & Valve Cut Section Models | 2 Sets |
| 17 | Hydraulic Motor Test Kit | 1 Set |
| 18 | Computer System with Simulation Software (Hydraulic Systems) | 2 PCs |
| 19 | Tool Kit (Spanner Set, Screwdrivers, Allen Keys, etc.) | 5 Sets |
| 20 | White Board & Markers for Circuit Drawing | 2 Boards |
| 21 | Calibration Bench Setup | 1 Unit |
| 22 | Standard Calibrated Ammeter (Digital) | 2 Units |
| 23 | Standard Calibrated Voltmeter (Digital) | 2 Units |
| 24 | Precision Ohmmeter | 2 Units |
| 25 | Calibrated Multimeter (Reference Standard) | 2 Units |
| 26 | Function Generator | 1 Unit |
| 27 | Variable Power Supply (0-30V, 5A) | 2 Units |
| 28 | Digital Oscilloscope | 1 Unit |
| 29 | Test Leads with Banana Plugs | 10 Sets |
| 30 | Tool Kit (Screwdrivers, Wire Cutter, etc.) | 5 Sets |
| 31 | Work Benches with Electrical Boards | 5 Units |
| 32 | Analog Multimeter | 3 Units |
| 33 | Clamp Meter | 3 Units |
| 34 | Battery Load Tester | 2 Units |
| 35 | Ignition System Tester | 2 Units |
| 36 | Timing Light | 2 Units |
| 37 | Alternator Test Bench | 1 Unit |
| 38 | Starter Motor Bench Tester | 1 Unit |
| 39 | Auto Electrical Diagnostic Tool | 1 Unit |
| 40 | Insulation Resistance Tester (Megger) | 2 Units |
| 41 | Basic Hand Tool Set (Pliers, Screwdrivers, etc.) | 5 Sets |
| 42 | Wire Stripper & Crimper Tool | 5 Sets |
| 43 | Workbenches with Electrical Panels | 5 Units |
| 44 | Lightning Arrester | 5 |
| 45 | Chain block | 25 |
| 46 | Temperature gage | 25 |
| 47 | Dipole | 25 |
| 48 | Conductors. (Different Types) | As Required |
| 49 | Insulators. (Different Types) | As Required |
| 50 | Poles | As Required |
| 51 | Power factor improvement panel | 25 |
| 52 | Voltmeter | 25 |
| 53 | Theodolite | 1 |
| 54 | Earthling equipment | 25 |
| 55 | Insulators | 25 |
| 56 | Protective Relay Test Set | 2 Units |
| 57 | Primary Injection Kit | 1 Unit |
| 58 | Secondary Injection Test Set | 1 Unit |
| 59 | CT/PT Analyzer | 1 Unit |
| 60 | Relay Calibration Bench | 1 Unit |
| 61 | Earth Resistance Tester | 2 Units |
| 62 | Safety Helmet and Gloves | 10 Sets |
| 63 | Tool Kit (Pliers, Wrenches, Screwdrivers) | 5 Sets |
| 64 | Portable Grounding and Shorting Equipment | 2 Sets |
| 65 | Substation Layout Board (Demo/Training) | 1 Unit |
| 66 | Bus Bar Assembly Demo Unit | 1 Unit |
| 67 | Hydraulic Turbine Model (Training Unit) | 1 Unit |
| 68 | Alignment Tools (Dial Gauge, Feeler Gauge) | 3 Sets |
| 69 | Mechanical Coupling Kit | 2 Sets |
| 70 | Torque Wrench | 3 Units |
| 71 | Foundation Layout Laser Level | 2 Units |
| 72 | Portable Crane / Chain Block | 2 Units |
| 73 | Vernier Caliper / Micrometer Set | 5 Sets |
| 74 | Vibration Analyzer | 1 Unit |
| 75 | Calibration Equipment Set | 1 Set |
| 76 | Testing & Commissioning Panel (Demo Type) | 1 Unit |
| 77 | Inspection Flashlight and Mirror Set | 3 Sets |
| 78 | Safety PPE (Helmet, Gloves, Goggles) | 15 Sets |
| 79 | Generator Installation Training Unit | 1 Unit |
| 80 | Mechanical Coupling Kit (for AC generator) | 2 Sets |
| 81 | Electrical Tool Kit (Crimper, Wire Stripper, etc.) | 5 Sets |
| 82 | Lifting Equipment (Chain Block or Hoist) | 2 Units |
| 83 | Emergency Standby Generator (Training Purpose) | 1 Unit |
| 84 | Circuit Breaker Testing Kit | 1 Set |
| 85 | Lockout/Tagout Kit | 3 Sets |
| 86 | Electrical Panel Simulator (for emergency system) | 1 Unit |
| 87 | Battery Bank with Inverter (for training use) | 1 Set |
| 88 | Electrical Tool Kit (Insulated) | 5 Sets |
| 89 | Phase Rotation Tester | 2 Units |
| 90 | Load Bank (for testing under load conditions) | 1 Unit |
| 91 | Safety PPE Kit (Helmet, Gloves, Boots, Goggles) | 15 Sets |
| 92 | Generator Shutdown Simulator Panel | 1 Unit |
| 93 | HP Plant Fault Simulation Kit | 1 Unit |
| 94 | Thermal Imaging Camera (for hot-spot detection) | 1 Unit |
| 95 | Vibration Analyzer (for mechanical fault detection) | 1 Unit |
| 96 | Laptop with Diagnostic Software | 2 Units |
| 97 | Whiteboard with Markers (for fault analysis sessions) | 1 Set |
| 98 | Fault Logging & Analysis Charts | 5 Sets |
| 99 | Preventive Maintenance Toolkit (spanners, pliers, etc.) | 5 Sets |
| 100 | Infrared Thermometer | 2 Units |
| 101 | Grease Gun | 3 Units |
| 102 | Portable Inspection Lamp | 3 Units |
| 103 | Lubrication System Test Kit | 1 Unit |
| 104 | Laptop/Tablet (for digital logs and checklists) | 2 Units |
| 105 | Safety Helmet with Face Shield | 10 Units |
| 106 | Lockout-Tagout (LOTO) Kit | 2 Sets |
| 107 | Breakers | 20 units |
| 108 | hydraulic benches | 4 units |
| 109 | Pipes and fittings | 20 units |
| 110 | Viscometers | 5 units |
| 111 | Stopwatch | 20 units |
| 112 | Computers/simulation software | 20 units |
| 113 | DC Power Supply | 5 units |
| 114 | Resistive load | 20 units |
| 115 | Connecting Leads | 100 units |
| 116 | Transmission line model | 2 units |
| 117 | Measuring tape | 20 units |
| 118 | WPADA/NTDCL clearance standards chart | 5 units |
| 119 | Temperature reference chart | 5 units |
| 120 | Safety Equipment’s | 20 units |
| 121 | lightning arrestors of different types | 50 units |
| 122 | Insulators. (Different Types) | 20 units |
| 123 | Disc insulator | 20 units |
| 124 | Tachometer | 5 units |
| 125 | Flow Meters | 5 units |
| 126 | Stopwatch | 5 units |
| 127 | Hydraulic Valve Test Bench | 5 units |
| 128 | Hydraulic Seals & Valve Cut Section Models | 2 Units |
| 129 | Hydraulic Motor Test Kit | 2 Units |
| 130 | tool Kit (Spanner Set, Screwdrivers, Allen Keys, etc.) | 5 units |
| 131 | Water Turbine Test Rig (Pelton / Francis / Kaplan) | 5 units |
| 132 | Alternator Test Bench | 5 units |
| 133 | Auto Electrical Diagnostic Tool | 5 units |
| 134 | Lockout/tagout kit | 5 units |
| 135 | Transparent Pipes for Flow Visualization | 20 units |
| 136 | Flow Measuring Apparatus (Venturi meter / Orifice Meter) | 5 units |
| 137 | Hydraulic Trainer Kit (with actuators, valves, circuit board) | 2 Units |
| 138 | Auto Electrical Diagnostic Tool | 5 units |
| 139 | Digital Multimeter (True RMS) | 5 units |
| 140 | Belt tension gauge | 5 units |
| 141 | Hydraulic Flow Apparatus | 2 Units |
| 142 | hydraulic benches | 2 Units |
| 143 | pressure gauges | 2 Units |
| 144 | Bernoulli’s apparatus | 2 Units |
| 145 | Pitot tube Flowmeters | 2 Units |
| 146 | Viscometer | 5 units |
| 147 | Spark plug tester | 20 units |
| 148 | Insulation resistance tester | 5 units |
| 149 | Francis turbine trainer | 2 Units |
| 150 | Pelton turbine trainer | 2 Units |
| 151 | Kaplan turbine demo models | 2 Units |
| 152 | Mini hydro power plant simulator | 2 Units |
| 153 | Synchronous generator trainer sets | 2 Units |
| 154 | Smart grid simulators | 2 Units |
| 155 | Battery management system trainers (BMS) | 2 Units |
| 156 | Inverter and power converter trainers | 2 Units |
| 157 | Ultrasonic flow meters | 5 units |
| 158 | Thermographic (IR) cameras for thermal analysis | 2 Units |
| 159 | Water level sensors and pressure transmitters | 2 Units |
| 160 | PLC training kits (e.g., Siemens, Allen-Bradley) | 1 Unit |
| 161 | HMI panels and SCADA simulation tools | 1 Unit |
| 162 | Smart sensors (temperature, pressure, flow) | 20 units |
| 163 | Vibration analyzers (condition monitoring) | 2 Units |
| 164 | Pressure calibrators (digital) | 2 Units |
| 165 | Temperature calibrators (dry block and bath type) | 2 Units |
| 166 | Phase sequence testers | 5 units |

# Members of Qualifications Development Committee

The Qualifications Development Committee consisted of following members:

| S.No | Name | Organization |
| --- | --- | --- |
|  | Engr. Tauseef Hussain Qasmi | Water & Power Department Government of Gilgit-Baltistan |
|  | Engr. Dr. Tauqeer Akhtar | Punjab Irrigation and Power Department, Government of Punjab |
|  | Mr. Sheraz Ali | Environmental Protection Agency (EPA) GB |
|  | Abdul Basit Mansoor | Pak PWD Gujranwala |
|  | Engr. Navid Ali | KP-TEVTA |
|  | Engr. Danial Rahim | AAJSONS (Pvt.) Ltd Upper Chitral |
|  | Mr. Umar Ali Shah | MHRSC Chitral |
|  | Engr. Asif Hayat | AKRSP |
|  | Mr. Asif Fareed | Independent Consultant |
|  | Mr. Ejaz Ahmed | GVTTC Diamer GB |
|  | Engr. Hayat Baig | Baig Hydro Designs Gilgit |
|  | Engr. Arif Hussain | Karakoram International University Gilgit |