Instruction Sheet for the Candidate

| Qualification | National Vocational Certificate Level 2 in Instrumentation Technology |
| --- | --- |
| Competency Standard | Perform Testing of Electrical Wiring (Level 2) |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name______________________________________________________ Registration/Roll Number_______________________________________ |
| Guidance for Candidate | To meet this standard, you are required to complete the following within time frame (for practical demonstration & assessment): - Perform Earth leakage Test. - Perform Open Circuit Test - Perform Short Circuit Test - Perform Continuity/Loop Test - Perform Visual Test - Perform Insulation Test - Perform Polarity Test - Perform Earth Resistance Test - Perform Murray Loop Test - Perform BLAVIER & Earth Loop Test |
| Time: 03 Hrs. | During a practical assessment, under observation by an assessor, you are required to |
| Minimum Evidence Required | Perform Earth leakage Test. - Ensure the socket must be at least 13A for RCD plug in. - Adjust the sensitivity of RCD. - Ensure tripping time must not exceed than 200msec. - Plug the RCD in socket and switch on socket outlet. - Ensure P-N and P-E light up. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. - Move the selection switch to 180o. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. - Move selection switch to 0°. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. Perform Open Circuit Test - Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. - Connect ohmmeter between starting and ending terminals of live conductor. - Ensure the reading must be near to 0 ohm. - Repeat P2 to P3 for neutral and earth conductor. Perform Short Circuit Test - Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. - Connect one terminal of ohmmeter with live conductor. - Connect the other terminals of ohmmeter with neutral conductor. - Ensure the reading must be infinity (No reading). - Connect ohmmeter between live conductor and earth conductor. - Ensure the reading must be infinity (No reading) Perform Continuity/Loop Test - Connect all metal clad switches, metal parts, conduits with earth. - Open the main switch. - Turn on all the switches. - Connect earth continuity tester with conduit and independent earth. - Measure the resistance value with tester which must not be more than 1 ohm. Perform Visual Test - Check the wires joints. - Check if there is any spark. - Check over heating of wires. - Check all the appliances are on or fluctuating. - Check all indications of meters. - Check Voltages on all phases. - Check the DB and Breakers. - Check the main supply is coming properly. Perform Insulation Test - Switch off the main breaker. - Short circuit all lighting connections. - Connect merger between line and earth. - Rotate the merger to generate the voltage. - Read the merger dial and ensure that the insulation resistance should not be less than 50M ohm of any single circuit. Perform Polarity Test - Switch off the main switch. - Disconnect all loads. - Switch on all circuit control switches. - Connect ohm meter between main line and all the terminal of sockets and load points one by one. - Ensure meter reading value must be less than 1 ohm. Perform Earth Resistance Test - Place 3 electrodes in earth at distance of 10m apart between every electrode. - Connect terminal E of earth resistance tester to first electrode. - Connect terminal P of earth resistance tester to the second electrode. - Connect terminal C of the earth resistance tester with third electrode. - Measure the resistances after applying specific voltage. - Repeat 1 to 5 by interacting earthling regions. - Ensure 3 readings must be equal. Perform Murray Loop Test - Connect galvanometer with Wheatstone bridge. - Connect positive terminal of DC source with Wheatstone bridge. - Connect negative terminal of DC source with ground. - Connect remaining two terminal of Wheatstone bridge with two cores of the cable. - Short the other end of these two cores of cable. - Note the reading of galvanometer. - Calculate Rx. - Repeat the 1 to 7 for other cores of the cable. Perform BLAVIER & Earth Loop Test - Connect galvanometer with Wheatstone bridge. - Connect positive terminal of DC source with Wheatstone bridge. - Connect negative terminal of DC source with ground. - Connect remaining two terminal of Wheatstone bridge with two cores of the cable. - Short the other end of these two cores of cable. - Note the reading of galvanometer. - Calculate Rx. - Repeat the 1 to 7 for other cores of the cable. |

Self-Assessment Checklist

| Candidate Name |  |
| --- | --- |
| Registration No. |  |
| Qualification | National Vocational Certificate Level 2 in Instrumentation Technology |
| Competency Standard | Perform Testing of Electrical Wiring (Level 2) |
| Purpose of Assessment | Formative Assessment |
| Assessment Task | - Perform Earth leakage Test. - Perform Open Circuit Test - Perform Short Circuit Test - Perform Continuity/Loop Test - Perform Visual Test - Perform Insulation Test - Perform Polarity Test - Perform Earth Resistance Test - Perform Murray Loop Test - Perform BLAVIER & Earth Loop Test |

I can……………….

| Performance Criteria | Yes | No |
| --- | --- | --- |
| - Ensure the socket must be at least 13A for RCD plug in. |  |  |
| - Adjust the sensitivity of RCD. |  |  |
| - Ensure tripping time must not exceed than 200msec. |  |  |
| - Plug the RCD in socket and switch on socket outlet. |  |  |
| - Ensure P-N and P-E light up. |  |  |
| - Press the test button. |  |  |
| - Ensure that RCD will trip and reading must be shown less than 200msec. |  |  |
| - Move the selection switch to 180o. |  |  |
| - Press the test button. |  |  |
| - Ensure that RCD will trip and reading must be shown less than 200msec. |  |  |
| - Move selection switch to 0°. |  |  |
| - Press the test button. |  |  |
| - Ensure that RCD will trip and reading must be shown less than 200msec. |  |  |
| - Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. |  |  |
| - Connect ohmmeter between starting and ending terminals of live conductor. |  |  |
| - Ensure the reading must be near to 0 ohm. |  |  |
| - Repeat P2 to P3 for neutral and earth conductor. |  |  |
| - Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. |  |  |
| - Connect one terminal of ohmmeter with live conductor. |  |  |
| - Connect the other terminals of ohmmeter with neutral conductor. |  |  |
| - Ensure the reading must be infinity (No reading). |  |  |
| - Connect ohmmeter between live conductor and earth conductor. |  |  |
| - Ensure the reading must be infinity (No reading) |  |  |
| - Connect all metal clad switches, metal parts, conduits with earth. |  |  |
| - Open the main switch. |  |  |
| - Turn on all the switches. |  |  |
| - Connect earth continuity tester with conduit and independent earth. |  |  |
| - Measure the resistance value with tester which must not be more than 1 ohm. |  |  |
| - Check the wires joints. |  |  |
| - Check if there is any spark. |  |  |
| - Check over heating of wires. |  |  |
| - Check all the appliances are on or fluctuating. |  |  |
| - Check all indications of meters. |  |  |
| - Check Voltages on all phases. |  |  |
| - Check the DB and Breakers. |  |  |
| - Check the main supply is coming properly. |  |  |
| - Switch off the main breaker. |  |  |
| - Short circuit all lighting connections. |  |  |
| - Connect merger between line and earth. |  |  |
| - Rotate the merger to generate the voltage. |  |  |
| - Read the merger dial and ensure that the insulation resistance should not be less than 50M ohm of any single circuit. |  |  |
| - Switch off the main switch. |  |  |
| - Disconnect all loads. |  |  |
| - Switch on all circuit control switches. |  |  |
| - Connect ohm meter between main line and all the terminal of sockets and load points one by one. |  |  |
| - Ensure meter reading value must be less than 1 ohm. |  |  |
| - Place 3 electrodes in earth at distance of 10m apart between every electrode. |  |  |
| - Connect terminal E of earth resistance tester to first electrode. |  |  |
| - Connect terminal P of earth resistance tester to the second electrode. |  |  |
| - Connect terminal C of the earth resistance tester with third electrode. |  |  |
| - Measure the resistances after applying specific voltage. |  |  |
| - Repeat 47 to 51 by interacting earthling regions. |  |  |
| - Ensure 3 readings must be equal. |  |  |
| - Connect galvanometer with Wheatstone bridge. |  |  |
| - Connect positive terminal of DC source with Wheatstone bridge. |  |  |
| - Connect negative terminal of DC source with ground. |  |  |
| - Connect remaining two terminal of Wheatstone bridge with two cores of the cable. |  |  |
| - Short the other end of these two cores of cable. |  |  |
| - Note the reading of galvanometer. |  |  |
| - Calculate Rx. |  |  |
| - Repeat the 54 to 61 for other cores of the cable. |  |  |
| - Connect galvanometer with Wheatstone bridge. |  |  |
| - Connect positive terminal of DC source with Wheatstone bridge. |  |  |
| - Connect negative terminal of DC source with ground. |  |  |
| - Connect remaining two terminal of Wheatstone bridge with two cores of the cable. |  |  |
| - Short the other end of these two cores of cable. |  |  |
| - Note the reading of galvanometer. |  |  |
| - Calculate Rx. |  |  |
| - Repeat the 62 to 68 for other cores of the cable. |  |  |

Candidate’s Signature__________________ Assessor’s Signature____________________

Date: _______________________________

Assessors Judgment Guide

| Qualification | National Vocational Certificate Level 2 in Instrumentation Technology |
| --- | --- |
| Competency Standard | Perform Testing of Electrical Wiring (Level 2) |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name: ______________________________________________________________ Registration/Roll Number: ______________________Signature: _______________ |
| Assessment Outcome | COMPETENT NOT YETCOMPETENT Name of the Assessor________________________________________________ Assessor’s code:____________________________________________________ Signature: ________________________________ |

| Assessment Summary (to be filled by the assessor) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Activity | Method |  |  |  |  | Result |  |
| Nature of Activity | Written | Oral | Observation | Portfolio | Role Play | Competent | Not Yet Competent |
| Practical Skill Demonstration |  |  |  |  |  |  |  |
| Knowledge Assessment |  |  |  |  |  |  |  |
| Other Requirement |  |  |  |  |  |  |  |

Observation Checklist

| Assessment Task |  | - Perform Earth leakage Test. - Perform Open Circuit Test - Perform Short Circuit Test - Perform Continuity/Loop Test - Perform Visual Test - Perform Insulation Test - Perform Polarity Test - Perform Earth Resistance Test - Perform Murray Loop Test - Perform BLAVIER & Earth Loop Test |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| During the practical assessment, candidate demonstrated the following: |  |  |  | Yes | No | Remarks |
|  | Ensure the socket must be at least 13A for RCD plug in. |  |  |  |  |  |
|  | Adjust the sensitivity of RCD. |  |  |  |  |  |
|  | Ensure tripping time must not exceed than 200msec. |  |  |  |  |  |
|  | Plug the RCD in socket and switch on socket outlet. |  |  |  |  |  |
|  | Ensure P-N and P-E light up. |  |  |  |  |  |
|  | Press the test button. |  |  |  |  |  |
|  | Ensure that RCD will trip and reading must be shown less than 200msec. |  |  |  |  |  |
|  | Move the selection switch to 180o. |  |  |  |  |  |
|  | Press the test button. |  |  |  |  |  |
|  | Ensure that RCD will trip and reading must be shown less than 200msec. |  |  |  |  |  |
|  | Move selection switch to 0°. |  |  |  |  |  |
|  | Press the test button. |  |  |  |  |  |
|  | Ensure that RCD will trip and reading must be shown less than 200msec. |  |  |  |  |  |
|  | Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. |  |  |  |  |  |
|  | Connect ohmmeter between starting and ending terminals of live conductor. |  |  |  |  |  |
|  | Ensure the reading must be near to 0 ohm. |  |  |  |  |  |
|  | Repeat P2 to P3 for neutral and earth conductor. |  |  |  |  |  |
|  | Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. |  |  |  |  |  |
|  | Connect one terminal of ohmmeter with live conductor. |  |  |  |  |  |
|  | Connect the other terminals of ohmmeter with neutral conductor. |  |  |  |  |  |
|  | Ensure the reading must be infinity (No reading). |  |  |  |  |  |
|  | Connect ohmmeter between live conductor and earth conductor. |  |  |  |  |  |
|  | Ensure the reading must be infinity (No reading) |  |  |  |  |  |
|  | Connect all metal clad switches, metal parts, conduits with earth. |  |  |  |  |  |
|  | Open the main switch. |  |  |  |  |  |
|  | Turn on all the switches. |  |  |  |  |  |
|  | Connect earth continuity tester with conduit and independent earth. |  |  |  |  |  |
|  | Measure the resistance value with tester which must not be more than 1 ohm. |  |  |  |  |  |
|  | Check the wires joints. |  |  |  |  |  |
|  | Check if there is any spark. |  |  |  |  |  |
|  | Check over heating of wires. |  |  |  |  |  |
|  | Check all the appliances are on or fluctuating. |  |  |  |  |  |
|  | Check all indications of meters. |  |  |  |  |  |
|  | Check Voltages on all phases. |  |  |  |  |  |
|  | Check the DB and Breakers. |  |  |  |  |  |
|  | Check the main supply is coming properly. |  |  |  |  |  |
|  | Switch off the main breaker. |  |  |  |  |  |
|  | Short circuit all lighting connections. |  |  |  |  |  |
|  | Connect merger between line and earth. |  |  |  |  |  |
|  | Rotate the merger to generate the voltage. |  |  |  |  |  |
|  | Read the merger dial and ensure that the insulation resistance should not be less than 50M ohm of any single circuit. |  |  |  |  |  |
|  | Switch off the main switch. |  |  |  |  |  |
|  | Disconnect all loads. |  |  |  |  |  |
|  | Switch on all circuit control switches. |  |  |  |  |  |
|  | Connect ohm meter between main line and all the terminal of sockets and load points one by one. |  |  |  |  |  |
|  | Ensure meter reading value must be less than 1 ohm. |  |  |  |  |  |
|  | Place 3 electrodes in earth at distance of 10m apart between every electrode. |  |  |  |  |  |
|  | Connect terminal E of earth resistance tester to first electrode. |  |  |  |  |  |
|  | Connect terminal P of earth resistance tester to the second electrode. |  |  |  |  |  |
|  | Connect terminal C of the earth resistance tester with third electrode. |  |  |  |  |  |
|  | Measure the resistances after applying specific voltage. |  |  |  |  |  |
|  | Repeat 47 to 51 by interacting earthling regions. |  |  |  |  |  |
|  | Ensure 3 readings must be equal. |  |  |  |  |  |
|  | Connect galvanometer with Wheatstone bridge. |  |  |  |  |  |
|  | Connect positive terminal of DC source with Wheatstone bridge. |  |  |  |  |  |
|  | Connect negative terminal of DC source with ground. |  |  |  |  |  |
|  | Connect remaining two terminal of Wheatstone bridge with two cores of the cable. |  |  |  |  |  |
|  | Short the other end of these two cores of cable. |  |  |  |  |  |
|  | Note the reading of galvanometer. |  |  |  |  |  |
|  | Calculate Rx. |  |  |  |  |  |
|  | Repeat the 54 to 61 for other cores of the cable. |  |  |  |  |  |
|  | Connect galvanometer with Wheatstone bridge. |  |  |  |  |  |
|  | Connect positive terminal of DC source with Wheatstone bridge. |  |  |  |  |  |
|  | Connect negative terminal of DC source with ground. |  |  |  |  |  |
|  | Connect remaining two terminal of Wheatstone bridge with two cores of the cable. |  |  |  |  |  |
|  | Short the other end of these two cores of cable. |  |  |  |  |  |
|  | Note the reading of galvanometer. |  |  |  |  |  |
|  | Calculate Rx. |  |  |  |  |  |
|  | Repeat the 62 to 68 for other cores of the cable. |  |  |  |  |  |
| Competent |  |  | Not Yet Competent |  |  |  |

Knowledge Assessment

| Qualification | National Qualification Automation & Process Control (Level 5) |
| --- | --- |
| Competency Standard | Perform Testing of Electrical Wiring (Level 2) |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name:______________________________________________________________ Registration/Roll Number: _________________ Candidate Signature:___________ |
| Assessment Outcome | COMPETENT NOT YETCOMPETENT Name of the Assessor:________________________________________________ Assessor’s code:____________________________________________________ Signature of the Assessor:_______________________ |

Candidate’s response is not required to be identical, but similar concepts and/or keywords must be used. Oral questioning may be used to clarify candidate understanding of topic and its application.

| Questions (Candidate confidently answered questions correctly and demonstrated understanding of the topics and their application) |  | Satisfactory | Not Satisfactory |
| --- | --- | --- | --- |
|  | Explain the function of RCD. |  |  |
|  | Explain the purpose of continuity test. |  |  |
|  | Polarity test is used to detect the correct amount of current |  |  |
|  | - TRUE - FALSE |  |  |
|  | Explain P-E and P-N |  |  |
|  | Explain the purpose of insulation resistance test. |  |  |
|  | Explain the function of distribution box |  |  |
|  | Explain which meters are used for open circuit and short circuits test. |  |  |

Feedback to the Candidate

Candidate’s Signature__________________ Assessor’s Signature _________________