Competency Standards

For

National Diploma Level 4

in

Transformer Technician

National Vocational and Technical Training Commission (NAVTTC)

Government of Pakistan

FOREWORD

The National Vocational and Technical Training Commission (NAVTTC) sincerely acknowledges and appreciates the valuable contributions of representatives from business, industry, academia, government bodies, provincial TEVTAs, sector skill councils, and trade associations who devoted their time and expertise in the development of the National Vocational Qualification for Transformer Technician (Level-IV). The successful completion of this qualification framework would not have been possible without their technical support and guidance.

NAVTTC recognizes the dedicated efforts of experts from Industry, Academia, TEVTAs, and related sectors who worked diligently to ensure the quality, relevance, and accuracy of this qualification. The credit for this achievement goes to their hard work; however, NAVTTC takes full responsibility for any errors or omissions that may still exist in the qualification document.

It is important to highlight that the development of competency standards is a continuous and evolving process. With ongoing advancements in technology, scientific research, and practical experience at the field level, periodic review and updating of these standards is essential. NAVTTC, Government of Pakistan, remains committed to keeping the Dairy Technician qualification aligned with the dynamic needs of the dairy industry and the changing demands of both national and international labor markets.

Executive Director (NAVTTC)

Table of Contents

1.	Introduction:	2

1.1.	Date of Development:	2

1.2.	Date of Review & Validation:	2

1.3.	Entry requirement:	2

1.4.	Trainer Qualification Requirement	2

1.5.	Codes of Qualification (ISCED)	2

2.	Summary of competencies	3

3.	Qualification Levelling and Packaging	3

4.	Detail of Competency Standards	4

0713E&E4301: Maintain Safe Working Environment of Transformer	4

0713E&E4302: Perform Installation and Commissioning of Transformer	6

0713E&E4303: Perform Preventive Maintenance of Transformer	9

0713E&E4304: Perform Corrective Maintenance of Transformer	10

0713E&E4305: Perform Transformer Winding Operation	12

0713E&E4306: Fabricate & Weld Transformer Components	15

0713E&E4307: Develop Entrepreneurship/Business	18

0713E&E4308: On-Job Training/Project	20

5.	List of Tools and Equipment Required for the Qualification:	21

6.	List of Consumable items Required for the Qualification:	23

7.	Members of Qualifications Development Committee	25

# Introduction:

This training course is designed for the occupation of ‘Microgrid Technician’ in the energy sector. A Microgrid Technician is responsible for the installation, operation, maintenance, control and troubleshooting of Microgrid systems, ensuring efficient and reliable energy distribution. The specific duties of a Microgrid Technician depend on the type of Microgrid system and its scale. Technicians are responsible for monitoring and maintaining electrical and control systems, integrating renewable energy sources, managing battery storage, and ensuring compliance with safety and regulatory standards. Their duties also include diagnosing faults, conducting performance assessments, optimizing system efficiency, and coordinating with engineers and other stakeholders. Additionally, they are responsible for training junior technicians and ensuring adherence to operational standards. Microgrid Technicians play a crucial role in maintaining resilient and sustainable energy solutions. To meet the growing demand for skilled professionals in this field, NAVTTC, in collaboration with GIZ, has introduced Competency-Based Training and Assessment (CBT&A) programs, ensuring the development of a competent workforce aligned with industry needs.

| # Date of Development: | 25-29 August, 2025 |
| --- | --- |
| # Date of Review & Validation: | - |
| # Entry requirement: | Industrial Electrician Level-3, Or Equivalent qualification |
| # Trainer Qualification Requirement | BS/BSc/BE Engineering (Electrical/ Electronics) with 3 years of Experience OR B.Tech (Honour) / BS Technology (Electrical/ Electronics) with 3 years of Experience OR Diploma of Associate Engineers (DAE in Electrical/ Electronic) with 5 years’ experience |
| # Codes of Qualification (ISCED) | Code: 0713E&E43 Description: Transformer Technician |

# Summary of competencies

| Code | Competency standard | NVQF Level | Category | Estimated contact hours |  |  | Cr. Hr. |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Th | Pr | Tot. |  |
| 0713E&E4301 | Maintain Safe Working Environment of Transformer | 4 | Functional | 10 | 40 | 50 | 3 |
| 0713E&E4302 | Perform Installation and Commissioning of Transformer | 4 | Technical | 10 | 80 | 90 | 5 |
| 0713E&E4303 | Perform Preventive Maintenance of Transformer | 4 | Technical | 20 | 80 | 100 | 6 |
| 0713E&E4304 | Perform Corrective Maintenance of Transformer | 4 | Technical | 10 | 60 | 70 | 4 |
| 0713E&E4305 | Perform Transformer Winding operation | 4 | Technical | 10 | 100 | 110 | 6 |
| 0713E&E4306 | Fabricate and weld transformer components | 4 | Technical | 20 | 80 | 110 | 6 |
| 0713E&E4307 | Develop Entrepreneurship/ Business | 4 | Generic | 10 | 60 | 70 | 4 |
| Total Cr. Hr. Institute |  |  |  | 90 | 500 | 590 | 34 |
| 0713E&E4308 | On job training (OJT) | 4 | Technical | - | - | 240 | 06 |
| G.Total (%) |  |  |  | 830 |  |  | 40 |

# Qualification Levelling and Packaging

| S # | Occupations / Short Course | Modules/CS Codes | Level | Occupation Credit Hours | Training Duration |
| --- | --- | --- | --- | --- | --- |
| 1. | Microgrid Maintenance Technician | 701,702,710 | 3 | (55 + 74 + 74) = 203 | 9 weeks |
| 2. | Microgrid Operator | 703,704,705 | 3 | (71 + 51 + 53) = 175 | 8 weeks |
| 3. | Microgrid Inventory Personnel | 701,709 | 3 | (55 + 71) = 126 | 6 Weeks |

# Detail of Competency Standards

# 0713E&E4301: Maintain Safe Working Environment of Transformer

Overview

This competency standard pertains to establishing and upholding a safe environment within the operations of transformer technology. Specifically, it includes the evaluation and classification of workplace risks, the application of appropriate risk control measures, and the compliance with health and safety regulations. This responsibility also includes the enforcement of equipment health regulations, compliance with safety protocol inspections, and vigilant care of safety signs. In completing these activities, learners actively enhance and safeguard the personnel, equipment, and environmental risks within the workplace and advance safety culture. After completing the competency standard, student will be able to perform all the task (CU1 to CU6) in accordance with the essence of the Competency-Based Training System.

| Competency Units | Performance Criteria |
| --- | --- |
| - Identify hazards at work place | - Check workplace environment. - Assess unsafe conditions - Recognize workplace hazards |
| - Categorize the potential risks | - Assess potential risks - Categorize risks as immediate, high-priority, or tolerable. - Communicate categorization outcomes to management and workforce |
| - Mitigate The Potential Risks | - Apply hierarchy of controls - Safely isolate circuits using lock-out/tag-out procedures. - Install barriers, guards, and safety devices to minimize risk. - Ensure effective use of PPE/SPs for all personnel. - Perform safety drills/ T & P prade |
| - Monitor the Safety Protocols | - Verify safety protocol compliance with SOPs. - Record safety violations - Maintain compliance records for legal purposes |
| - Maintain the safety signage | - Place safety signage at standardized visible locations. - Implement national/international signage, symbol, codes, and color. - Update signage in line with changes in workplace layout. |
| - Document the reports | - Prepare clear, accurate on hazards, risks, and monitoring reports. - Maintain detailed logs of inspections, accidents, and corrective actions. - Submit reports in prescribed formats within required timelines. - Ensure documentation complies with audit and regulatory standards. - Maintain secure and retrievable records for future reference |

Knowledge & Understanding

- Identify sources and forms for workplace hazards.

- Define types of hazards.

- Define methods for risk evaluation.

- Define producers of risk mitigation and PPEs.

- Understand safe isolation, lock-out/tag-out, grounding, and electrical safety procedures.

- Explain safety barriers, signs, and devices in line with national/international standards.

- Explain safety drills

- Outline organizational SOPs, and standards.

Critical Evidence(s) Required

The candidate needs to produce the following critical evidence(s) to be declared competent in this competency standard:

- Identify workplace hazards.

- Assess Potential Risks

- Able to Categorize risks

- Implement risk control measures

- Carry out safety drill as well as tool & parts (T&P) parade.

- Comply with Safety Regulations

- Maintain national/international safety signage, symbol, codes, and color.

- Compile and format reports (hazard, risk, accident/incident, and monitoring, corrective actions) in line with standard requirements.

Tools and equipment required

The tools and equipment required for this competency standard are given below:

| Sr. No. | Tools / Equipment | Quantity Required (for 25 students) |
| --- | --- | --- |
| 1 | Safety Helmets | 25 |
| 2 | Safety Goggles | 25 |
| 3 | Safety Gloves | 25 pairs |
| 4 | Ear Protection | 25 |
| 5 | Safety Shoes | 25 pairs |
| 6 | Flame-Resistant Clothing / Aprons | 25 |
| 7 | Lock-out/Tag-out (LOTO) Kits | 5 sets (shared, 1 per 5 students) |
| 8 | Multimeters (Digital) | 10 (shared, 1 per 2–3 students) |
| 9 | Insulated Screwdriver Sets | 10 sets |
| 10 | Grounding Rods / Clamps | 5 sets |
| 11 | Fire Extinguishers | 5 (strategically placed) |
| 12 | First Aid Kits | 2 (1 per lab section) |
| 13 | Barriers, Guard Rails & Safety Cones | 20 cones + 5 rails |
| 14 | Safety Signage Boards | 20 |
| 15 | Labels, Paints & Tapes | 5 sets |
| 16 | Workplace Inspection Checklists | 25 copies (refillable) |
| 17 | Cameras / Mobile Devices | 5 (shared) |
| 18 | Sound Level Meter | 2 |
| 19 | Lux Meter | 2 |
| 20 | Thermal Scanner / IR Gun | 2 |
| 21 | Gas Detector | 1 |
| 22 | Computers with Reporting Software | 5 systems (shared) |
| 23 | Printers / Scanners | 1 set |
| 24 | Logbooks & Registers | 5 |
| 25 | Emergency Drill Materials | 5 sets |
| 26 | Communication Tools | 5 |

# 0713E&E4302: Perform Installation and Commissioning of Transformer

Overview:

This competency standard outlines the skills and knowledge required for installation and commissioning of transformer. It includes interpreting drawings, carrying out mechanical and electrical installation, conducting tests, energizing safely, and maintaining documentation, all in compliance with safety and industry standards. After completing the competency standard, student will be able to perform all the task (CU1 to CU6) in accordance with the essence of the Competency-Based Training System.

| Competency Units | Performance Criteria |
| --- | --- |
| - Interpret the transformer drawings and specifications | - Identify various types of transformer drawings and symbols - Interpret electrical and mechanical specifications of transformers - Verify ratings, configurations, and installation requirements as per manufacturer’s documentation - Verify site conditions with transformer design parameters |
| - Install the transformer | - Prepare installation site and readiness. - Perform correct alignment and positioning of the transformer. - Secure mechanical fittings and structural supports. - Perform grounding of the transformer as per standard requirements. - Connect auxiliary components including cooling fans, protection relays. - Implement physical clearances and ventilation as per safety guidelines |
| - Commission the transformer | - Conduct pre-commissioning checks including insulation, oil level, tap changer position, leaks, breather, gaskets - Conduct key mechanical functional tests, including the cooling system, Buchholz relay, temperature indicators, oil level indicators, and pressure relief valve - Conduct key electrical tests, including Insulation Resistance Test, Transformer Turns Ratio (TTR) Test, Capacitance and Dissipation Factor (C&DF) Test, Dissolved Gas Analysis (DGA), Open Circuit Test, and Short Circuit Test - Evaluate test results against manufacturer’s and industry standards - comply with commissioning procedures and safety protocols |
| - Connect the transformer | - Identify primary and secondary connections based on the wiring diagram. - Perform electrical connection/terminations using appropriate tools and techniques. - Carryout continuity test - Comply with phase sequence and polarity requirements |
| - Energize the transformer | - Perform final safety checks before energizing. - Coordinate with relevant departments for synchronization. - Energize the transformer following standard procedures. - Monitor operational parameters during energization. - Take corrective actions if abnormal conditions are observed |
| - Document the reports | - Maintain detailed records of installation and commissioning activities - Record all testing and inspection data accurately. - Generate a commissioning report as per organizational standards - Submit documentation for review and approval - Archive reports for future reference and regulatory compliance |

Knowledge & Understanding

- Define types, component and functions of transformers.

- Explain transformer electrical and mechanical specifications.

- Define transformer grounding and bonding.

- Understand Common electrical symbols.

- Explain necessary Tool and equipment for installation

- Understanding of Pre-commissioning checks and standard testing protocols.

- Understanding of Manufacturer legends and abbreviations

- Understanding ratings: voltage, current, impedance, frequency, cooling class (ONAN, ONAF).

- Describe various types of transformer in term of connections.

- Describe necessary test of transformer commissioning

- Understand basic IEEE/IEC standards

- Explain the importance of C& DF, TTR, DGA, Insulation resistance test of transformer.

- Describe different types of documentation necessary for transformer commissioning and installation

Critical Evidence(s) Required

The candidate needs to produce the following critical evidence(s) to be declared competent in this competency standard:

- Interpret transformer drawings and specifications

- Verify site and equipment readiness

- Install and aligned transformer with grounding

- Conduct pre-commissioning checks and tests

- Connect electrical terminals and auxiliaries

- Energize transformer safely and monitored parameters

Tools and equipment Required

The tools and equipment required for this competency standard are given below:

| S.No | Items | Quantity |
| --- | --- | --- |
|  | Insulated combination pliers | 25 |
|  | Insulated screwdrivers (sets) | 10 sets |
|  | Adjustable wrenches | 10 |
|  | Open-end & ring spanner sets | 5 sets |
|  | Wire stripper/cutter | 10 |
|  | Crimping tools (manual) | 10 |
|  | Hammer (ball peen, 1–2 lb) | 10 |
|  | Measuring tape (5m) | 10 |
|  | Spirit level | 5 |
|  | Cable cutter (medium duty) | 5 |
|  | Torque wrench | 3 |
|  | Digital multimeter (TRMS, CAT III/IV) | 10 |
|  | Insulation resistance tester (Megger) | 5 |
|  | Earth resistance tester | 2 |
|  | Clamp meter (AC/DC) | 5 |
|  | Transformer Turns Ratio (TTR) tester | 2 |
|  | Capacitance & Dissipation Factor (C&DF) tester | 1 |
|  | Oil Breakdown Voltage (BDV) tester | 1 |
|  | Infrared thermometer (IR gun) | 2 |
|  | Digital thermometer (probe type) | 3 |
|  | Continuity tester | 5 |
|  | Phase sequence indicator | 3 |
|  | Transformer training units (3-phase, LV safe setup) | 3 |
|  | Tap changer simulator / unit | 3 |
|  | Cooling fan (mock-up or real unit) | 2 |
|  | Breather (silica gel type) | 3 |
|  | Buchholz relay simulator | 2 |
|  | Pressure relief valve simulator | 2 |
|  | Grounding rod, clamp & cable set | 5 sets |
|  | Terminal blocks, lugs, connectors | Assorted |
|  | Cable trays / conduits (for wiring practice) | As needed |
|  | Synchronization panel / simulator | 1 |
|  | Electrical safety gloves (insulated) | 25 pairs |
|  | Safety shoes | 25 pairs |
|  | Safety helmets | 25 |
|  | Safety goggles | 25 |
|  | Fire extinguishers (CO₂ / Dry Powder) | 4 |
|  | First aid kits | 2 |
|  | Lockout/tagout kits | 5 |
|  | Insulated rubber mats | 5 large mats |
|  | Safety signage (danger/warning/caution) | Assorted |
|  | Computers (with Excel/Word for documentation) | 5 |
|  | Printer and scanner | 1 |
|  | Projector or LED display for instructor demonstrations | 1 |
|  | Transformer lifting tools(e.g. chain pulley, jack, slings) | 1 set |
|  | Labeling and tagging materials | 25 |

# 0713E&E4303: Perform Preventive Maintenance of Transformer

Overview:

This competency standard covers the skills and knowledge to perform preventive maintenance on transformers, including inspection, servicing, and safety checks. It focuses on identifying potential faults, ensuring reliability, and completing accurate maintenance records. After completing the competency standard, student will be able to perform all the task (CU1 to CU5) in accordance with the essence of the Competency-Based Training System.

| Competency Units | Performance Criteria |
| --- | --- |
| - Perform visual Inspection of transformer | - Check tank, conservator and joints for oil leaks or rust - Verify oil level and gauges - Inspect bushing for cracks, damage and leakage - Examine cooling system for cleanliness/operation - Check breather and silica gel conditions - Verify grounding connections - Inspect for unusual noise, vibration, smell and hot spots |
| - Plan schedule for the preventive maintenance | - Prepare plan for preventive maintenance and submit to concerned authority - Obtain final approval before execution - Coordinate timing with operations and maintenance team |
| - Conduct the preventive maintenance | - Get permit to work (PTW) - De-energize the transformer - Connect grounding for safety purpose - Perform tightening of joints, repair leaks, clean and repair rust - Perform refilling of oil, take sample of oil for testing and repair gauges - Clean, tighten replace bushings if cracked/damaged - Clean radiator, service/replace fans & pumps - Replace silica gel, clean/replace breather - Tight and clean earthing connections - Test and calibrate protection and monitoring devices - Perform basic electrical tests including IR, winding resistance, TTR, DGA,C&DF |
| - Analyze the preventive maintenance results | - Record preventive maintenance results. - Analyze results with standards/specifications. - Identify abnormal trends or deviations. - Follow Standard operating procedures (SOPs) |
| - Document the reports | - Compile all inspection and test results. - Use prescribed reporting format. - Highlight key findings and abnormal conditions. |

Knowledge & Understanding

- Describe the purpose and benefits of preventive maintenance.

- What tools & equipment are used for preventive maintenance?

- Describe common defects in the transformer.

- Describe transformer components requiring routine inspection and servicing.

- Describe maintenance schedules based on standards, environment, and load conditions.

- What type of maintenance needs for cooling systems, radiators, fans, and pumps?

- Knowledge of preparing preventive maintenance reports in required format.

Critical Evidence(s) Required

The candidate needs to produce the following critical evidence(s) to be declared competent in this competency standard:

- Able to differentiate between critical and non-critical defects of transformer

- Tightening of connections and inspection of earthing.

- Performance of basic electrical tests

- Restoration of system, safe disposal of materials, and site housekeeping.

- Completion of maintenance records and effective communication of findings.

Tools and equipment required

The tools and equipment required for this competency standard are given below:

| S.No | Items | Quantity |
| --- | --- | --- |
| 1 | Personal Protective Equipment (PPE) | 25 No. |
| 2 | Lock-out/tag-out kits | 2 Sets |
| 3 | Oil resistance gloves and rags | 25 No. |
| 4 | Insulated screwdrivers (set) | 5 sets |
| 5 | Insulated pliers (combination + cutter) | 5 sets |
| 6 | Adjustable spanners | 5 sets |
| 7 | Socket wrench set | 5 sets |
| 8 | Torque wrench | 5 Nos. |
| 9 | Wire brush & cleaning cloths | 25 No. |
| 10 | Digital multimeters | 5 Nos. |
| 11 | Insulation resistance tester (megger) | 5 Nos. |
| 12 | Clamp meter (AC/DC) | 05 Nos |
| 13 | Infrared thermometer | 05 Nos |
| 14 | Oil test kit (basic) | 2 Nos. |
| 15 | Breather servicing kit (funnels, containers) | 1 No. |
| 16 | Silica gel refill packs | 5 Packs |
| 17 | Oil sampling bottles | 25 Nos. |
| 18 | Lubricant (for tap changer, fans) | 2 bottles |
| 19 | Earthing rod and cables | 2 Nos, |
| 20 | Maintenance logbooks/record sheets | 25 Nos. |

# 0713E&E4304: Perform Corrective Maintenance of Transformer

Overview:

This competency standard outlines the foundational skills and knowledge needed for a trainee to accurately perform corrective maintenance on the transformers. Upon mastering the competency standard, the student is expected to appropriately document maintenance procedures, isolate and troubleshoot faulty transformers, diagnose the underlying issues, perform necessary repairs, and confirm proper alternate power supply arrangements have been made, all within the safety protocols of the Competency-Based Training System. After completing the competency standard, student will be able to perform all the task (CU1 to CU6) in accordance with the essence of the Competency-Based Training System.

| Competency Units | Performance Criteria |
| --- | --- |
| CU1: Isolate the Transformer | - Wear the required PPEs. - Isolate transformers from supply safely. - Ensure grounding and discharge residual charge. - Place warning signage, lock-out/tag-out (LOTO) at isolation points. - Verify isolation using line tester. - Confirm with supervisor before proceeding. |
| CU2: Perform Troubleshooting | - Carry out visual inspection of the transformer. - Identify common symptoms (noise, overheating, abnormal readings). - Apply diagnostic tools (multimeter, Megger, thermal scanner). - Perform tests to diagnose the faults. - Analyze test results to locate the fault. - Record preliminary fault observations. - Compare results with manufacturer’s standard values. |
| CU3: Categorize the Nature of Faults | - Identify the nature of faults. - Assess the severity of the faults. - Evaluate cost and downtime implications of the fault. - Record the data. |
| CU4: Carry Out Alternate Arrangements for Smooth Power Supply | - Provide temporary power backup (DG set or alternate transformer). - Coordinate with utility/grid for load transfer. - Verify alternate supply safety compliance. - Inform consumers/users about temporary arrangements. - Monitor performance of alternate supply during operation. |
| CU5: Repair/Replace Faulty Component | - Disassemble the transformer - Remove the faulty components - Repair/replace the faulty components - Apply proper torque and insulation techniques. - Conduct preliminary function test of replaced part. - Refill and test transformer oil (if applicable). - Reassemble and tighten all connections securely. - Perform post-repair safety and insulation resistance tests. - Perform tagging-in of the transformer after successful repair and testing. |
| CU6: Document the Reports | - Record type and cause of fault. - Note corrective actions taken. - Compile maintenance log for future reference. - Submit report to supervisor/concerned authority - Attach photographs and test reports for verification. - Maintain digital/ERP entry of maintenance activity. - Provide recommendations to avoid similar faults in future. |

### Knowledge & Understanding

- Describe the importance of corrective maintenance.

- Explain the types of transformer faults.

- Explain the safe isolation procedures.

- Understanding the repair and replacement techniques for transformer components.

- Describe the function of oil in transformer.

- Explain the documentation standards – maintenance logbooks.

Critical Evidence(s) Required

The trainee must demonstrate the following to be declared competent in Corrective Maintenance of Transformer:

- Safely isolate the transformer following LOTO procedures and confirm isolation.

- Able to use appropriate diagnostic tools to identify faults.

- Categorize the fault nature.

- Disassemble and assemble transformer and repair/replace faulty components using standard procedures.

### Tools and Equipment Required

| S.No | Items | Quantity |
| --- | --- | --- |
| 1 | Electrical Hand Tool Kit | 25 Nos |
| 2 | Insulation Resistance Tester (Megger) | 25 Nos |
| 3 | Digital Multimeter | 25 Nos |
| 4 | AC/DC Clamp Meter | 25 Nos |
| 5 | Thermal Imaging Camera | 05 Nos |
| 6 | Torque Wrench | 25 Nos |
| 7 | Oil Filtration Machine | 02 Nos |
| 8 | Tap Changer Toolkit | 10 Nos |
| 9 | HV Test Kit | 05 Nos |
| 10 | PPE (Gloves, Safety Helmet, Goggles, Shoes) | 25 Sets |
| 11 | Insulated Ladder | 05 Nos |
| 12 | Lockout/Tagout Kits | 10 Nos |
| 13 | Earthing Rods & Discharge Rods | 05 Sets |
| 14 | Oil Testing Kit (BDV Tester, Moisture Analyzer, Gas Analyzer) | 05 Sets |
| 15 | Documentation Kit (Forms, Logbooks, Camera, ERP access) | 25 Nos |
| 16 | Portable Load Bank (for testing under load) | 05 Nos |
| 17 | Partial Discharge Detector | 05 Nos |
| 18 | Chain block hoist (2 Ton) | 05 Nos |

# 0713E&E4305: Perform Transformer Winding Operation

Overview:

This competency standard covers the knowledge and skills required for a student/trainee will be able to disassemble the transformer, understand winding details, perform winding work, reassemble the parts, test the transformer, and safely reinstall and energize it. After completing the competency standard, student will be able to perform all the task (CU1 to CU6) in accordance with the essence of the Competency-Based Training System.

| Competency Units | Performance Criteria |
| --- | --- |
| - Dis-assemble the transformer | - Assess the condition of transformer - Drain transformer oil - Dis-assemble the component of the transformer - Label and document parts for proper re-assembly and record-keeping. |
| - Interpret Winding Drawings & Specifications | - Check transformer type, rating, and winding configuration from drawings. - Identify number of turns, wire gauge, layering, insulation type with clearances, tapping points as per specifications. - Interpret winding direction and coil arrangement accurately. - Check all data before starting winding to avoid errors during operation. |
| - Perform winding operation | - Prepare and setup the transformer - Allocate requisite material for transformer - Set up winding machine or jig with correct tension, guides, and alignment. - Anchor conductor securely before starting winding - Perform winding operation while maintaining correct tension and alignment - Apply interlayer insulation and spacers where required. - Label winding clearly as per phase sequence. - Ensure number of turns and layers meet design specifications. - Avoid overlaps, loose turns, or damaged conductors during winding. - Tie, tape, or secure winding according to standard practices. - Install and insulate terminals or leads correctly. - Perform required test as per SOPs |
| - Perform reassembling of transformer | - Clean and inspect components before assembly. - Place windings core as per design. - Connect leads, taps, and bushings securely according to wiring diagram. - Assemble and tighten clamping structures, tank covers, and fasteners with proper torque. - Refill transformer oil as per SOPs |
| - Perform Post-Winding Inspection and Testing for smooth functioning | - Prepare transformer for post winding inspection test - Conduct quality inspection tests as per SOP - Document the records |
| - Reinstall and energize the transformer | - Position transformer at designated site using proper handling and lifting tools. - Connect HV/LV terminals, bushings, and earthing as per wiring diagram. - Energize transformer on no-load and monitor voltage, current, and abnormal noise. |

Knowledge & Understanding

- Knowledge of transformer winding types.

- Understanding of winding materials.

- Understand the Use of winding machines, jigs, guides, and tension control methods.

- Techniques for uniform layering.

- Explain the application of interlayer insulation.

- Describe quality standards to prevent short circuits, overheating, or mechanical faults.

- Understand Safety precautions during winding operations.

Critical Evidence(s) Required

The candidate needs to produce the following critical evidence(s) to be declared competent in this competency standard:

- Correct selection of winding materials.

- Proper setup of winding machine.

- Wind coils with correct number of turns.

- Leads, tapping points, and terminations applied securely as per design.

Tools and equipment Required

The tools and equipment required for this competency standard are given below:

| Sr. No. | Item Name | Quantity |
| --- | --- | --- |
| 1 | Insulated Screwdriver Set | 25 sets |
| 2 | Combination Pliers | 25 |
| 3 | Nose Pliers | 25 |
| 4 | Adjustable Spanner (8"–12") | 25 |
| 5 | Ring Spanner Set | 25 sets |
| 6 | Open-End Spanner Set | 25 sets |
| 7 | Socket Wrench Set | 25 sets |
| 8 | Hammer (ball peen & rubber mallet) | 25 each |
| 9 | Insulation Resistance Tester (Megger, 500V/1000V) | 10 (shared) |
| 10 | Digital Multimeter (True RMS) | 10 (shared) |
| 11 | Coil Winding Machine (manual/electric) | 5 (shared, batch use) |
| 12 | Coil Former / Mandrel Set | 5 sets |
| 13 | Vernier Caliper | 25 |
| 14 | Micrometer (0–25 mm) | 10 (shared) |
| 15 | Measuring Tape (3m–5m) | 25 |
| 16 | Insulation Paper Cutter / Scissors | 25 |
| 17 | Wire Stripping Tool | 25 |
| 18 | Soldering Iron with Stand (40W–60W) | 10 (shared) |
| 19 | Soldering Wire & Flux | Adequate stock |
| 20 | Hot Air Gun / Heating Oven (for varnish curing) | 2–3 (shared) |
| 21 | Varnish Impregnation Tank (or container) | 1–2 |
| 22 | Safety Gloves (Electrical Grade) | 25 pairs |
| 23 | Safety Goggles | 25 |
| 24 | Earthing Rod with Cable | 2 sets |
| 25 | First Aid Kit | 2 (lab-level) |
| 26 | Fire Extinguisher (CO₂ type) | 2–3 (lab-level) |

# 0713E&E4306: Fabricate & Weld Transformer Components

Overview:

This competency standard covers the check, inspect, and verify the functionality, condition, and safety of welding equipment and tools prior to use, read, understand, and interpret fabrication and welding drawings, perform basic welding operations as part of transformer assembly, repair, or fabrication tasks, carry out basic fabrication operations relevant to transformer manufacturing and repair and perform essential post-welding processes on transformer components. After completing the competency standard, student will be able to perform all the task (CU1 to CU5) in accordance with the essence of the Competency-Based Training System.

| Competency Units | Performance Criteria |
| --- | --- |
| - Check Welding Equipment & Tools | - Ensure the work area is clean and free from flammable materials before inspection begins. - Check welding machine for physical damage, loose connections, or missing parts. - Verify input power and grounding connections are secure and safe. - Inspect welding cables, electrode holder, and ground clamp for cuts, burns, or loose fittings. - Test output voltage and amperage (if applicable) for proper function. - Check electrode holders, nozzles, and contact tips for cleanliness and wear. - Ensure that tools are clean, undamaged, and stored properly when not in use. - Identify and record any equipment or tool that is unsafe or not functioning correctly. |
| - Interpret Fabrication & Welding Drawing | - Recognize title block information including drawing number, title, scale, and revision. - Interpret drawing lines, notations, and general layout for fabrication. - Interpret dimensional and geometric tolerances - Identify datum points and baseline references from the drawing. - Recognize standard welding symbols - Interpret weld type, size, location, and length from drawings. - Identify material specifications such as type, grade, thickness, and quantity. - Use drawing to plan layout, cutting, fitting, and welding sequence |
| - Perform Welding Operation | - Select appropriate welding process (e.g., SMAW, MIG) based on material and job specification. - Inspect and set up welding equipment, cables, clamps, and accessories for operational readiness. - Identify and prepare welding materials (e.g., transformer tanks, brackets, enclosures). - Strike and maintain a stable arc during welding. - Perform welds using correct technique, electrode, and current settings as per job requirement. - Control heat input to avoid warping or damage to thin transformer sheets or oil tanks. - Maintain correct weld bead profile, overlap, and penetration in line with specifications - Clean weld joints using appropriate tools (wire brush, chipping hammer, grinder). |
| - Perform fabrication Operation | - Select appropriate materials, tools, and equipment for the fabrication process. - Measure work pieces accurately using appropriate tools (e.g., tape measure, steel rule, vernier caliper). - Mark lines and reference points according to drawings or templates. - Verify layout accuracy before proceeding to cutting or drilling operations. - Bend or form materials using appropriate equipment (e.g., press brake, manual bender). - Smooth cut edges and remove burrs using grinding or filing tools. |
| - Perform Post – Welding Processes | - Remove slag, spatter, and oxidation using appropriate tools (e.g., wire brush, chipping hammer, grinder). - Clean weld areas thoroughly to ensure readiness for inspection or finishing. - Handle and dispose of waste material safely and in compliance with workplace standards. - Perform visual inspection of welds for common defects (e.g., cracks, porosity, undercut, incomplete fusion). - Measure weld size, alignment, and bead consistency as per drawing or standard. - Mark and report any defective areas requiring repair. - Prepare welded tanks or enclosures for testing (e.g., sealing openings). - Perform leak test using air pressure or vacuum (according to standard test procedures). - Grind or gouge out defective welds using suitable equipment. - Re-weld affected area following standard welding practices. - Clean and inspect reworked welds to confirm defect has been removed. - Apply anti-corrosion coatings (e.g., primer, rust-proof paint) using appropriate tools (brush, spray). |

Knowledge & Understanding

- Define types and functions of welding equipment used in transformer fabrication

- Explain basic operating principles of welding machines (SMAW, MIG, TIG)

- Describe basic types of engineering drawings used in transformer fabrication

- Define types of welds and joints (fillet, groove, lap, butt)

- Basic math, geometry, and units of measurement in drawings.

- Define basic welding principles and arc characteristics.

- Explain types of welding joints and positions

- Describe potential welding defects and their causes.

- Explain basics of fabrication processes used in transformer manufacturing.

- Define common fabrication defects and prevention methods.

- Explain Air pressure or vacuum leak testing procedures for transformer tanks

Critical Evidence(s) Required

The candidate needs to produce the following critical evidence(s) to be declared competent in this competency standard:

- Check and adjust gas systems safely for MIG/TIG welding.

- Tag and report defective tools or machines following workplace protocols.

- Accurately interpret fabrication and welding symbols and dimensions on a given transformer-related drawing

- Identify material types, part references, and processes from drawings

- Perform a weld on a transformer part (e.g., tank, frame, bracket) using correct technique and process.

- Measure, mark, cut, and drill components as per specifications

- Assemble and fit metal parts for transformer casing or frame.

- Conduct a leak or pressure test on a welded transformer tank and enclosure.

- Identify and repair welding defects

Tools and equipment Required

The tools and equipment required for this competency standard are given below:

| S.No | Items | Quantity |
| --- | --- | --- |
| 1 | SMAW/MIG/TIG welding machines | 2 Each |
| 2 | Ground cables | 10 No. |
| 3 | Electrode holders | 10 No. |
| 4 | MIG torches | 10 No. |
| 5 | Gas regulators and flow meters | 5 No. |
| 6 | Multimeter or clamp meter | 5 No. |
| 7 | Gas leak detector (soap solution) | 2 No. |
| 8 | Flashlight / Weld Inspection Light | 2 No. |
| 9 | Chipping hammer | 10 No. |
| 10 | Wire brush | 10 No. |
| 11 | Angle grinder | 4 No. |
| 12 | Welding clamps | 10 No. |
| 13 | Screwdrivers | 5 Set |
| 14 | Combination Pliers | 10 No. |
| 15 | Cutter plier | 10 No. |
| 16 | Nose Plier | 10 No. |
| 17 | Welding gloves | 15 No. |
| 18 | Safety glasses/face shield | 15 No. |
| 19 | Safety Shoes | 15 No. |
| 20 | Flame-resistant clothing (Apron) | 15 No. |
| 21 | Ear Plug | 15 No. |
| 22 | Respirator | 10 No. |
| 23 | Electrodes | 10 Box |
| 24 | Filler wires | 5 No. |
| 25 | Shielding gas cylinders | 10 No. |
| 26 | Scriber | 15 No. |
| 27 | Steel Ruler | 15 No. |
| 28 | Measuring Tape | 15 No. |
| 29 | Vernier Caliper | 15 No. |
| 30 | Combination Square | 15 No. |
| 31 | Protractor | 15 No. |
| 32 | Angle Grinder | 15 No. |
| 33 | Metal Shears | 15 No. |
| 34 | Hacksaw with Blade | 15 No. |
| 35 | Manual Bender | 5 No. |
| 36 | Cutting Torch | 5 No. |
| 37 | Hand drill / Pedestal Drill Machine | 3 No. |
| 38 | Grinding Machine | 3 No. |
| 39 | Drill Bit (Variable size) | 10 No. |
| 40 | Center punch | 10 No. |
| 41 | Bench Vise | 5 No. |
| 42 | Rivet Gun | 5 No. |
| 43 | Files | 10 No. |
| 44 | Sand paper | 10 No. |
| 45 | Paintbrush or spray gun | 10 No. |

# 0713E&E4307: Develop Entrepreneurship/Business

Overview:

This competency standard covers the underpinning knowledge and skills required for a student/trainee to be competent in developing entrepreneurial skills and business operations within the energy sector. After completing this competency standard, the Trainee/student will be able to successfully perform all the tasks related to communication, business structuring, financial management, customer engagement, and regulatory compliance in accordance with the essence of the Competency-Based Training System. After completing the competency standard, the student will be able to perform all the tasks (CU1 to CU11) in accordance with the essence of the Competency-Based Training System.

| Competency Units | Performance Criteria |
| --- | --- |
| - Assess market opportunities | - Identify market demand for transformer installation, maintenance, repair, and monitoring in a specific region or niche. - Analyze the competitive landscape, including established companies and independent technicians. - Research pricing models and customer service gaps in the current market. |
| - Develop a business plan | - Create a business plan that outlines the vision, mission, and objectives of the transformer service business. - Define the target market, service offerings, and unique value proposition. - Develop a marketing strategy to attract and retain clients.. |
| - Manage business finances | - Prepare and manage a budget for business operations. - Maintain accurate financial records of income and expenses. - Understand financial statements like cash flow and profit-and-loss reports |
| - Implement risk management strategies | - Identify potential business risks, such as liability, client issues, and economic downturns. - Evaluate insurance needs for the business and personal liability. - Develop contingency plans to minimize business disruption. |
| - Communicate effectively with clients | - Communicate clearly and confidently with clients to understand their needs. - Provide detailed quotes and transparent explanations of work to be performed. - Handle client inquiries, complaints, and negotiations professionally. |
| - Promote business services | - Create and manage a professional online presence, such as a website or social media profile. - Market services through various channels, including digital marketing, local directories, and industry partnerships. - Develop a strong customer service approach to generate repeat business and positive referrals. |
| - Plan for business growth. | - Assess opportunities for business expansion, such as hiring employees or expanding service lines. - Develop strategies for scaling operations while maintaining quality and efficiency. - Prepare for business succession or an eventual exit strategy. |

Knowledge & Understanding

- Fundamentals of effective oral and written communication in a technical environment.

- Report writing techniques for documentation, maintenance logs, and incident reports.

- Customer relationship management (CRM) for energy sector professionals.

- Basic principles of entrepreneurship, including market analysis, financial planning, and risk assessment.

- Energy sector regulations related to business operations and compliance.

- Business ethics and professionalism in customer interactions and negotiations.

- Financial management essentials such as cost estimation, budgeting, and revenue tracking.

- Safety and environmental considerations in energy operations.

- Strategies for scaling energy businesses and identifying investment opportunities.

- Methods to attract and retain customers in the energy sector.

- Understanding of market research, business structuring, and promotional strategies in the energy sector.

Critical Evidence(s) Required

The candidate needs to produce the following critical evidence(s) to be declared competent in this competency standard:

- Write and submit a sample daily operation log or technical report.

- Demonstrate oral communication in a team discussion or customer meeting simulation.

- Prepare a basic financial plan for an energy project.

- Identify market opportunities through a brief business proposal or case study.

- Develop a structured business model for energy services.

- Handle a simulated customer complaint resolution.

- Demonstrate professional behavior during role-play scenarios.

- Present marketing and outreach strategies for energy services.

- Identify legal and compliance aspects for an energy operation.

- Complete a safety assessment checklist for an energy facility.

- Comply with energy sector standards and policies.

Tools and equipment Required

The tools and equipment required for this competency standard are given below:

| S.No | Items | Quantity |
| --- | --- | --- |
|  | Directories of existing businesses | 25 |
|  | Examples of business plans | 25 |
|  | Sample of financial plans | 25 |
|  | Business planner templates | 25 |
|  | Start-up-costs estimator | 25 |

# 0713E&E4308: On-Job Training/Project

Overview:

The on-job training component of this qualification provides learners with the opportunity to apply their acquired skills and knowledge in real world environment. During this phase, students must take on entry level or support roles such as microgrid technician. This role span across diverse industries including hydel, wind, and solar power generation systems or any other relevant industry that enable learners to contribute to power generation while fulfilling the requirements of the qualifications.

As alternate arrangement, in case of non-availability of the concerned industry, the trainees may fulfill requirements of the qualification through conduct of project on the pattern of final year students of Diploma of Associate Engineers (DAEs) or Engineering Universities. This would, no doubt, cover industrial aspect of the qualification.

# List of Tools and Equipment Required for the Qualification:

| S.No | Items | Quantity |
| --- | --- | --- |
| 1 | Personal Protective Equipment’s (PPEs) (Safety Gloves (upto rated 2kV&18kV), Safety Helmets, Safety Glasses, Arc Flash Suit, Safety Shoes, Full Body Harness, Safety Belt, Ear Plugs, Ear Moff, Apron, Safety Jacket) | 25 Sets |
| 2 | Fire Extinguishers (CO2, DCP) | 01 each |
| 3 | Fire Hydrants | 01 Nos |
| 4 | Fire Ball Extinguisher | 02 Nos |
| 5 | Fire Blankets | 10 Nos |
| 6 | Sand Buckets | 06 Nos |
| 7 | First Aid Kit | 02 Nos |
| 8 | Safety Mask N95 | 02 Nos |
| 9 | Portable Temporary Ground | 02 Nos |
| 10 | Grounding Rods & Cables | 02 Nos |
| 11 | Lockout/Tagout (LOTO) Kits | 02 Nos |
| 12 | Safety Barriers & Cones | 02 Nos |
| 13 | Smoke & Gas Detectors | 02 Nos |
| 14 | Emergency Alarm Systems | 02 Nos |
| 15 | Digital Multimeter | 02 Nos |
| 16 | DC/AC Clamp Meter | 02 Nos |
| 17 | Power Quality Analyzer | 02 Nos |
| 18 | Infrared Thermometer | 02 Nos |
| 19 | Motor Generator Set | 02 Nos |
| 20 | Fuel Flow Meter (For Diesel Generators) | 02 Nos |
| 22 | Solar Irradiance Meter (For Renewable Systems) | 02 Nos |
| 23 | Lockout/Tagout (LOTO) Kit | 06 Nos |
| 24 | Grounding Rods & Clamps | 06 Nos |
| 25 | Insulation Resistance Tester | 06 Nos |
| 26 | Circuit Breaker Analyzer | 06 Nos |
| 27 | Synchroscope | 06 Nos |
| 28 | Magnetic Contactor 220V | 06 Nos |
| 30 | Magnetic Contactor 400V | 06 Nos |
| 31 | On-Off Push Buttons | 06 Nos |
| 32 | Rev-Stop-For Push Button | 06 Nos |
| 33 | Thermal Overload | 06 Nos |
| 34 | Phase Sequence Relay | 06 Nos |
| 35 | Current Transformer (CTs) | 06 Nos |
| 36 | Potential Transformers (PTs) | 02 Nos |
| 37 | Galvanometer | 02 Nos |
| 38 | Exciters | 02 Nos |
| 40 | Automatic Voltage Regulator | 02 Nos |
| 41 | Frequency Meter | 02 Nos |
| 42 | Single Phase Wattmeter | 02 Nos |
| 43 | Three Phase Wattmeter | 02 Nos |
| 44 | DC Wattmeter (100W) | 02 Nos |
| 45 | Digital Lux Meter | 02 Nos |
| 46 | Analog Lux Meter | 02 Nos |
| 47 | Solar Panels (180W, 585W) | 02 Nos |
| 48 | Inverters (1000W, 2kW, 5kW) | 02 Nos |
| 49 | Controller Trainer | 04 Nos |
| 50 | Charge Controller PWM (20A, 30A) | 03 each |
| 51 | Charge Controller MPPT (40A) | 04 Nos |
| 52 | Battery 100Ah | 05 Nos |
| 53 | Battery 200Ah | 05 Nos |
| 54 | Single Phase Energy meters (Analog and Digital) | 05 each |
| 55 | Three Phase Energy meters (Analog and Digital) | 05 each |
| 56 | Testing Board | 25 Nos |
| 57 | Single Pole Circuit Breaker (C6, C13, C63) | 02 each |
| 58 | Two Pole Circuit Breaker (C6, C13, C63) | 02 each |
| 59 | Three Pole Circuit Breaker (C6, C13, C63) | 02 each |
| 60 | Power Factor meter | 05 Nos |
| 61 | kVAR meter | 02 Nos |
| 62 | Four Pole Circuit Breaker (C6, C13, C63) | 02 each |
| 63 | Barcode Scanners (For Equipment Tagging & Tracking) | 01 Nos |
| 64 | RFID Tags & Readers (For Asset Management) | 01 Nos |
| 65 | Handheld Label Printers (For Equipment & Component Labelling) | 01 Nos |
| 66 | Digital Weighing Scales (For Measuring Components & Materials) | 02 Nos |
| 67 | Microsoft Office 2024 | 01 Nos |
| 68 | Computer | 25 Nos |
| 69 | Frequency Telephone Set | 02 Nos |
| 70 | kVARs Meters | 05 Nos |

# List of Consumable items Required for the Qualification:

| S. No. | Items | Quantity |
| --- | --- | --- |
|  | Cable (various gauges: 1.5mm², 2.5mm², 4mm², etc.) | 90m per type |
|  | Log Books | 25 Nos |
|  | Microsoft Office 2024 | 01 Nos |
|  | Safety googles, helmets, high voltage gloves. | 25 each |
|  | Connectors & terminals (lug connectors, ring terminals) | 1000 pcs |
|  | Fuses (various ratings: 5A, 10A, 15A, 20A) | 100 each |
|  | Circuit breakers (MCB, MCCB, RCD) | 50 each |
|  | Batteries (for meters & analyzers, AA, AAA, 9V, lithium-ion) | 24 each |
|  | Insulation tape (red, black, yellow, green, blue) | 5 roll each |
|  | Heat shrinks tubing (assorted sizes) | 100m |
|  | Cable glands (assorted sizes) | 100 pcs |
|  | Cable lugs & ferrules | 1000 pcs |
|  | Safety gloves (electrical insulated, cut-resistant, nitrile) – | 50 pairs |
|  | Helmets | 50 pcs |
|  | Safety glasses | 50 pcs |
|  | Arc flash suits | 5 sets |
|  | Face masks (N95, surgical) | 300 pcs |
|  | Earplugs | 200 pairs |
|  | Face shields | 10 pcs |
|  | High-visibility vests | 50 pcs |
|  | Respirators | 10 pcs |
|  | Safety shoes (optional if required) | 50 pairs |
|  | Cable ties (various sizes) | 2000 pcs |
|  | Marking labels (self-adhesive, cable labels) | 500 pcs |
|  | Lockout/Tagout tags | 100 pcs |
|  | Industrial-grade lubricants & grease | 20 Liters |
|  | Contact cleaner spray | 10 cans |
|  | Rust removers | 5 Liters |
|  | Wire strippers & cutters (extra consumable blades) | 10 pcs |
|  | Calibration stickers & logbooks | 10 set |
|  | Ethernet cables (Cat 6, Cat 5e) | 1000m roll |
|  | RJ45 connectors | 500 pcs |
|  | Fiber optic cables | 500m |
|  | Fiber optic connectors (SC, LC, ST) | 100 pcs |
|  | Network switch replacement modules | 5 pcs |
|  | Power strips & surge protectors | 20 pcs |
|  | BNC connectors (for oscilloscopes) | 10 pcs |
|  | Fire extinguishers (CO₂, dry chemical, foam) | 2 pcs |
|  | Fire extinguisher refills | 5 sets |
|  | Fire blankets | 10 pcs |
|  | First aid kits | 10 kits |
|  | Emergency exit sign | 10 pcs |
|  | Emergency lights (batteries included) | 10 pcs |
|  | Eye wash station solution | 5 Liters |
|  | Safety cones & barriers | 20 sets |
|  | Multimeter probes & leads | 50 sets |
|  | Clamp meter accessories (flexible CT coils, extra clamps) | 10 sets |
|  | Oscilloscope probes | 20 sets |
|  | Pressure gauge calibration kits | 5 sets |
|  | Infrared thermometer lens cleaning wipes | 50 packs |
|  | Battery analyzer test leads | 20 sets |
|  | Earth tester auxiliary electrodes | 10 sets |
|  | Whiteboard Markers | 50 sets |
|  | Whiteboard Cleaner | 10 bottles |
|  | Projector bulbs | 5 pcs |
|  | Presentation boards & flip charts | 5 pcs |
|  | Printed training manuals & datasheets | 25 copies |
|  | USB flash drives (for software & reports) | 50 pcs |
|  | Ethernet patch cables (for network devices) | 100 pcs |
|  | Barcode labels (for scanner testing) | 1000 pcs |

# Members of Qualifications Development Committee

The following members participated in the qualification’s development and validation process:

| Qualification Development Committee |  |  |  |
| --- | --- | --- | --- |
| S. No. | Name |  | Organization |
|  |  | Engr. Dr. Mian Khurram Ahsan | Assistant Professor GPI Mardan |
|  |  | Engr. Fawad Ahmad | Assistant Professor GCT Peshawar |
|  |  | Engr. Arshad Iqbal | Lecturer GCT Peshawar |
|  |  | Engr. Waqas Niaz | SDO NTDC |
|  |  | Miss. Ayesha Sumer Usmani | Lab Assistant NFC Multan |
|  |  | Zia ud din | Team Lead (PTCL) PTCL |
|  |  | Engr. Umar Hayat | Instructor (ET) GCT Railway Road LHR |
|  |  | Ms. Zunaira Naeem | Assistant Director (Electrical Tarbela Station) |
|  |  | Engr. Abdul Maqsood | DACUM Facilitator KP-TEVTA |
|  |  | Mr. Atif Bashir | ERP Consultant GNS Solutions PVT CO-DACUM Coordinators: |
| Qualification Review & Development Committee |  |  |  |
|  |  | Engr. Waqas Niaz | SDO NTDC |
|  |  | Engr. Umar Hayat | Instructor (ET) GCT Lahore |
|  |  | Engr. Muhammad Jehangir Khan | Assistant Professor, GCT Nowshera |
|  |  | Engr. Hafiz Muhammad Asad | A. E.E, Tarbela Dam |
|  |  | Engr. Zain ul Abidin, | Asstt. Dy. Dir, NPCC Islamabad |
|  |  | Engr. Ahmad Wisal | A.E.E,Tarbela Dam |
|  |  | Engr. Abdul Maqsood | DACUM Facilitator (KP-TEVTA) |