National Diploma Level 5 in (Water Quality and Resource Management)- Supervisor-Water Treatment Technician

National Vocational and Technical Training Commission (NAVTTC),

Government of Pakistan

ACKNOWLEDGEMENT

National Vocational and Technical Training Commission (NAVTTC) extends its gratitude and appreciation to many representatives of business, industry, academia, government agencies, Provincial TEVTAs, Sector Skill Councils and trade associations who speared their time and expertise to the development and validation of these National Vocational Qualifications (Competency Standards, Curricula, Assessments Packs and related material). This work would not have been possible without the financial and technical support of the TVET Sector Support Programme co-funded by European Union, Norwegian and German Governments implemented by GIZ Pakistan. NAVTTC is especially indebted to Dr. Muqeem ul Islam, who lead the project from the front. The core team was comprised on:

- Dr. Muqeem ul Islam, Director General (Skills,Standards and Curricula) NAVTTC

- Mr. Muhammad Naeem Akhtar, Senior Technical Advisor TSSP-GIZ,

- Mr. Muhammad Yasir, Deputy Director (SS&C Wing) NAVTTC

- Mr. Muhammad Ishaq, Deputy Director (SS&C Wing) NAVTTC

- Mr. Muhammad Fayaz Soomro, Deputy Director (SS&C Wing) NAVTTC

NAVTTC team under the leadership of Dr. Muqeem ul Islam initiated development of CBT & A based qualifications of diploma level-5 as a reform project of TVET sector in November 2018 and completed 27 NVQF diplomas of Level-5 in September, 2019. It seems worth highlighting that during this endeavor apart from developing competency standards/curricula in conventional trades new dimensions containing high-tech trades in TVET sector in the context of generation IR 4.0 trades have also been developed which inter alia includes Robotics, Mechatronics, artificial intelligence, industrial automation, instrumentation and process control. Moreover, trades like entrepreneurship, green/environmental skills and variety of soft/digital skill have also been developed to equip the Pakistani youth with skills set as per requirement of the global trends. These skills have been made integral part of all the 27 diplomas.

Nobody has been more important in the pursuit of this project than Dr. Nasir Khan, Executive Director, NAVTTC, whose patronage and support remain there throughout the development process and lastly to thanks especially to Syed Javed Hassan, Chairman NAVTTC and Raja Saad Khan, Deputy Team Lead TSSP-GIZ who made it happened in this challenging time.

- Table of Contents

1.	Introduction	6

2.	Purpose of the Qualification	7

3.	Date of Validation	8

4.	Date of Review	8

5.	Codes of Qualifications	8

6.	Members of Qualification Development Committee	10

7.	Members of Qualification Validation Committee	11

8.	Entry Requirements	12

9.	Regulation of the Qualification and schedule of units	12

10.	Summary and Levelling of Competency Standards	13

LEVEL 5	18

1.	Water Supply Scheme (Urban & Rural)(Surface Water & Ground Water)	18

1021CS-01.	Develop Water Supply Scheme (Rural and Urban) (Surface & Ground Water)	18

1021CS-02.	Estimate demand for Water Supply	19

1021CS-03.	Perform civil work	22

1021CS-04.	Plan water treatment (Clarification)	23

1021CS-05.	Plan water treatment (Filtration)	25

1021CS-06.	Draw sketches of intakes	27

1021CS-07.	Perform Distribution system of WSS	29

2.	Water and Waste Water Testing (Physico-chemical Parameter)-III	30

1021CS-08.	Perform Testing/Determination of Sodium (Na) by Flame-photometric Method	30

1021CS-09.	Perform Testing/Determination of Potassium (K) by Flame-photometric Method	33

1021CS-010.	Perform Testing/Determination of Nitrate (N) by Spectrophotometric Method	35

1021CS-011.	Perform Testing/Determination of Sulphate (SO4) by Spectrophotometric Method (Turbidity metric)	37

3.	Water Quality Testing( Heavy metals)	39

1021CS-012.	PerformTesting/Determination of Arsenic by Atomic Absorption Spectrometer	39

1021CS-013.	Perform Testing/Determination of Copper (Cu) by Atomic Absorption Spectrometer	42

1021CS-014.	Perform Testing/Determination of Zinc (Zn) by Atomic Absorption Spectrometer	45

1021CS-015.	Perform Testing/Determination of Manganese (Mn) by Atomic Absorption Spectrometer	48

4.	Operations and Maintenance of Water Supply Scheme	51

1021CS-016.	Use Maps, Plans, Drawings and Specifications for Water Works	51

1021CS-017.	Maintain and Repair Water Distribution Network	52

1021CS-018.	Perform Leak Detection	54

5.	Water Filtration and Treatment	55

1021CS-019.	Design Water Treatment Plant (Surface and Groundwater)	55

1021CS-020.	Operate and Control Coagulation and Flocculation Process	58

1021CS-021.	Operate and control of sediment process	60

1021CS-022.	Operate and control Water Filtration processes (Membrane Straining)	62

1021CS-023.	Operate and Control Chlorination Disinfection processes	64

1021CS-024.	Operate and Control UV Disinfection Process	67

1021CS-025.	Operate and Control Ozonation Process in Water Treatment Plant	69

1021CS-026.	Monitor the Performance of Water Treatment Plant	71

1021CS-027.	Maintain Record of Water Treatment Plants Assets	73

6.	Waste Water Assessment and Treatment	74

1021CS-028.	Demonstrate Sewage Treatment Plant	74

1021CS-029.	Demonstration of wastewater treatment process in constructed wetland	77

1021CS-030.	Determine Flow Discharge Measurement of Wastewater	80

1021CS-031.	Perform Testing of Dissolved Oxygen in waste water	84

1021CS-032.	Perform Testing of Chemical Oxygen Demand (COD) by Colorimeter/Dichromate Digestion Method	86

1021CS-033.	Perform Testing of Biochemical Oxygen Demand (BOD) by Monometric Pressure Measurement Method	89

1021CS-034.	Perform Testing/Determination of Oil and Grease in Wastewater	92

1021CS-035.	Perform Testing/Determination of Total Suspended Soilds	95

7.	Entrepreneur	98

1021CS-036.	Develop entrepreneurial skills	98

1021CS-037.	Apply management and communication techniques	100

1021CS-038.	Create human resource management plan	102

1021CS-039.	Develop project management plan	104

1021CS-040.	Develop sales plan	106

1021CS-041.	Conduct research for customer needs and satisfaction	108

1021CS-042.	Manage finances	110

1021CS-043.	Identify and resolve problems	112

8.	Hydraulics and Irrigation Engineering	115

1021CS-044.	Determine Hydrostatic pressure	115

1021CS-045.	Apply Hydro kinematic Principles	117

1021CS-046.	Produce sketches of canals and head works	120

1021CS-047.	Design Canals	124

1021CS-048.	Produce sketches of Hydraulic structures	126

- Introduction

Water quality and treatment is process that improves the quality of water to make it more acceptable for a specific end-use. The end use may be drinking, industrial water supply, irrigation, river flow maintenance, water recreation or many other uses, including being safely returned to the environment. Water treatment removes contaminants and undesirable components, or reduces their concentration so that the water becomes fit for its desired end-use. This treatment is crucial to human health and allows humans to benefit from both drinking and irrigation use.

In fact, no sphere of life may be identified that does not include the contribution of water technology. Thus, the importance of this diploma may be determined according to its usefulness in our daily life. Therefore, industry expectations for skilled workforce are also dynamic which can only be managed through setting relevant competency standards in collaboration with the leading industries. Being cognizant of this fact, National Vocational & Technical Training Commission (NAVTTC) developed competency standards for water quality and treatment Technology under National Vocational Qualifications Framework (NVQF). These competency standards have been developed by a Qualifications Development Committee (QDC) and validated by the Qualifications Validation Committee (QVC) having representation from the leading department of water industry (WASA, PCSIR, PHED) of the country.

- Purpose of the Qualification

The purpose of these qualifications is to set high professional standards for Water Quality and Resource Management. The specific objectives of developing these qualifications are as under:

1.	Improve the professional competence of the trainees

2.	Provide opportunities for recognition of skills attained through non-formal or informal pathways

3.	 Improve the quality and effectiveness of training and assessment for automobile industry

4.	 Enable the existing workforce to capacitate themselves in new water technologies and method

- Date of Validation

The level 5 of National DAE qualification on Water Quality and Resource Management has been validated by the Qualifications Development Committee (QDC) members on 10-12th June, 2019 and will remain valid for ten years i.e. 12th June, 2029

- Date of Review

The level 5 of National DAE qualification on Water Quality and Resource Management has been validated by the Qualifications Development Committee (QDC) members on 10-12th June, 2019 and shall be reviewed after three years i.e. 12th June, 2022

- Codes of Qualifications

The International Standard Classification of Education (ISCED) is a framework for assembling, compiling and analyzing cross-nationally comparable statistics on education and training. ISCED codes for these qualifications are assigned as follows:

| ISCED Classification |  |
| --- | --- |
| Code | Description |
| 1021CS (1) | National Vocational Certificate Level-I & II in “Water Quality and Resource Management” (Assistant) |
| 1021CS (2) | National Vocational Certificate Level-III in “Water Quality and Resource Management” (Water Quality Surveyor) |
| 1021CS (3) | National Vocational Certificate Level-IV in “Water Quality and Resource Management” (Lab Analyst) |
| 1021CS (4) | National Vocational Certificate Level-V in “Water Quality and Resource Management (Supervisor/ Water Treatment Technician) |

- Members of Qualification Development Committee

| S# | Name - Designation | Organization |
| --- | --- | --- |
|  | Dr.Lubna | PRCWR,Islamabad |
|  | Dr.Hifza Rasheed | PRCWR,Islamabad |
|  | Engr.Ahmed Shamsher, Deputy Secretary | PHED,KPK |
|  | Muhammad Adnan, Deputy Director | IMC,Islamabad |
|  | Dr.Asad Ghufran | IIUI,Islamabad |
|  | Azizullah Khan | WASA Rawalpindi |
|  | Dr.Anwer Baig | NUST |
|  | Miss Saiqa | PRCWR,Islamabad |
|  | Mr.Shafiq | PRCWR,Islamabad |
|  | Mr.Ali | PHED,Balochistan |
|  | Mr.Abdul Latif | PHED,Sindh |
|  | Tanveer Malik | Bin Qutab,Islamabad |
|  | Muhammad Yasir, Assistant Director | SS&C NAVTTC,Islamabad |
|  | Saba Sadiq, DACUM Facilitator, | University of Lahore, Lahore |

- Members of Qualification Validation Committee

| S# | Name - Designation | Organization |
| --- | --- | --- |
|  | Dr.Muhammad Aslam Tahir, Chairman | PRCWR,Islamabad |
|  | Dr.Manzoor Ahmed Malik, Director | PRCWR,Islamabad |
|  | Engr.Faizan-ul-Hasan, Director | PRCWR,Islamabad |
|  | Dr.Hifza Rasheed, Director | PRCWR,Islamabad |
|  | Dr.Muhammad Arshad Malik, Assistant Professor | IIUI,Islamabad |
|  | Syed Musstjab Akbar Shah Eqani, Assistant Professor | COMSATS Islamabad |
|  | Engr.Ahmed Shamsher, Deputy Secretary | PHED,KPK |
|  | Muhammad Adnan, Deputy Director | IMC,Islamabad |
|  | Muhammad Zaheer, Assistant Director | NTB,Islamabad |
|  | Muhammad Yasir, Assistant Director | SS&C NAVTTC,Islamabad |
|  | Samreen Iqbal, Senior Scientist officer | Qarshi Industries, Islamabad |
|  | Saba Sadiq, DACUM Facilitator | University of Lahore, Lahore |

- Entry Requirements

The entry requirements for this qualification are:

National Vocational Certificate Level 4 (Water Quality and Resource Management)- Supervisor/ Water Treatment Technician

- Regulation of the Qualification and schedule of units

Not Applicable

- Summary and Levelling of Competency Standards

| NVQF (Competency Standards) | Level | Category | Estimated Hours |  |  | CH |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Th. | Pr. | T H |  |
| Level 5 |  |  |  |  |  |  |
| 16. Water Supply Scheme (Urban & Rural) (Surface Water & Ground Water) Water Works Supervisor |  |  |  |  |  |  |
| Develop Water Supply Scheme (Rural and Urban) | 5 | Technical | 3 | 18 | 21 | 2.1 |
| Estimate demand for Water Supply | 5 | Technical | 5 | 20 | 25 | 2.5 |
| Perform civil works | 5 | Technical | 5 | 20 | 25 | 2.5 |
| Plan water distribution system | 5 | Technical | 5 | 20 | 25 | 2.5 |
| Perform distribution network of WSS | 5 | Technical | 5 | 20 | 25 | 2.5 |
| Draw sketch of Intake | 5 | Technical | 5 | 20 | 25 | 2.5 |
| Plan water treatment (Clarification) | 5 | Technical | 5 | 20 | 25 | 2.5 |
| Total |  |  | 33 | 138 | 171 | 17.1 |
| 17. Water and waste water Testing (Physico-chemical Parameter)-III Water Testing Sr. Technician (Chemical) |  |  |  |  |  |  |
| Testing/Determination of Sodium (Na) by Flame-photometric Method | 5 | Technical | 15 | 45 | 60 | 6.0 |
| Testing/Determination of Potassium (K) by Flame-photometric Method | 5 | Technical | 15 | 45 | 60 | 6.0 |
| Testing/Determination of Nitrate (N) by Spectrophotometric Method | 5 | Technical | 15 | 45 | 60 | 6.0 |
| Testing/Determination of Sulphate (SO4) by Spectrophotometric Method (Turbidity metric) | 5 | Technical | 15 | 45 | 60 | 6.0 |
| Total |  |  | 60 | 180 | 240 | 2.4 |
| 18. Water Quality testing(Heavy metals) Water Testing Senior Technician (Heavy Metal) |  |  |  |  |  |  |
| Testing/Determination of Arsenic by Atomic Absorption Spectrometer | 5 | Technical | 15 | 35 | 50 | 5.0 |
| Testing/Determination of Copper (Cu) by Atomic Absorption Spectrometer | 5 | Technical | 15 | 33 | 48 | 4.8 |
| Testing/Determination of Zinc (Zn) by Atomic Absorption Spectrometer | 5 | Technical | 15 | 33 | 48 | 4.8 |
| Testing/Determination of Manganese (Mn) by Atomic Absorption Spectrometer | 5 | Technical | 15 | 33 | 48 | 4.8 |
| Total |  |  | 60 | 134 | 194 | 19.4 |
| 19. Operation and Maintenance of Water Supply Scheme Water Supply Technician |  |  |  |  |  |  |
| Use Maps, Plans, Drawings and Specifications for Water Works | 5 | Technical | 6 | 18 | 24 | 2.4 |
| Maintain and Repair Water Distribution Network | 5 | Technical | 12 | 24 | 36 | 3.6 |
| Perform Leak Detection | 5 | Technical | 12 | 22 | 34 | 3.4 |
| Total |  |  | 30 | 64 | 94 | 9.4 |
| 20. Water Filtration and Treatment Water Treatment Technologist |  |  |  |  |  |  |
| Design water treatment plant (Surface and Ground water) | 5 | Technical | 12 | 12 | 24 | 2.4 |
| Operate and Control Coagulation and Flocculation Process | 5 | Technical | 3 | 9 | 12 | 1.2 |
| Operate and control of sediment process (Surface Water) | 5 | Technical | 3 | 9 | 12 | 1.2 |
| Operate and maintain water filtration process( Membrane Straining) | 5 | Technical | 3 | 9 | 12 | 1.2 |
| Operate and Control Chlorination disinfection process | 5 | Technical | 3 | 9 | 12 | 1.2 |
| Operate and Control Ultraviolet (UV)disinfection process | 5 | Technical | 3 | 6 | 9 | 0.9 |
| Operate and Control Ozonation process in Water Treatmen Plant | 5 | Technical | 6 | 24 | 30 | 3 |
| Monitor the Performance of Water Treatment Plant | 5 | Technical | 6 | 12 | 18 | 1.8 |
| Maintain Record of Water Treatment Plants Assets | 5 | Technical | 6 | 12 | 18 | 1.8 |
| Total |  |  | 45 | 102 | 147 | 14.7 |
| 21. Waste water Assessment and Treatment Waste Water Testing Technician |  |  |  |  |  |  |
| Demonstrate Sewage Treatment Plant (STP) | 5 | Technical | 6 | 12 | 18 | 1.8 |
| Demonstration of wastewater treatment process in constructed wetland | 5 | Technical | 6 | 12 | 18 | 1.8 |
| Determine Flow Discharge Measurement of Wastewater | 5 | Technical | 6 | 12 | 18 | 1.8 |
| Perform Testing of Dissolved Oxygen in waste water | 5 | Technical | 6 | 12 | 18 | 1.8 |
| Perform Testing of Chemical Oxygen Demand (COD) by Colorimeter/Dichromate Digestion Method | 5 | Technical | 6 | 12 | 18 | 1.8 |
| Perform Testing of Biochemical Oxygen Demand (BOD) by Monometric Pressure Measurement Method | 5 | Technical | 6 | 12 | 18 | 1.8 |
| Perform Testing of Oil and Grease in waste water | 5 | Technical | 6 | 12 | 18 | 1.8 |
| Perform Testing of TSS in waste water | 5 | Technical | 6 | 12 | 18 | 1.8 |
| Total |  |  | 48 | 96 | 144 | 14.4 |
| 22. Entrepreneur |  |  |  |  |  |  |
| Develop entrepreneurial skills | 5 | Generic | 4 | 6 | 10 | 1 |
| Apply management and communication techniques |  |  |  |  |  |  |
| Create human resource management plan | 5 | Generic | 4 | 6 | 10 | 1 |
| Develop project management plan | 5 | Generic | 4 | 6 | 10 | 1 |
| Develop sales plan | 5 | Generic | 4 | 6 | 10 | 1 |
| Conduct research for customer needs and satisfaction | 5 | Generic | 4 | 6 | 10 | 1 |
| Manage finances | 5 | Generic | 4 | 6 | 10 | 1 |
| Identify and resolve problems | 5 | Generic | 4 | 6 | 10 | 1 |
| Develop Teams and Individuals | 5 | Generic | 4 | 6 | 10 | 1 |
| Apply Problem solving techniques in the workplace using critical thinking | 5 | Generic | 4 | 6 | 10 | 1 |
| Total |  |  | 36 | 54 | 90 | 9 |
| 23. Hydraulics and Irrigation Associate |  |  |  |  |  |  |
| Determine Hydrostatic pressure | 5 | Technical | 12 | 12 | 24 | 2.4 |
| Apply Hydro kinematic Principles | 5 | Technical | 12 | 12 | 24 | 2.4 |
| Produce sketches of canals and head work | 5 | Technical | 12 | 12 | 24 | 2.4 |
| Design Canals | 5 | Technical | 12 | 12 | 24 | 2.4 |
| Produce sketches of Hydraulic structures | 5 | Technical | 12 | 12 | 24 | 2.4 |
| Total |  |  | 60 | 60 | 120 | 12 |
| Grand Total |  |  | 372 | 828 | 1200 | 120 |

LEVEL 5

## Water Supply Scheme (Urban & Rural)(Surface Water & Ground Water)

### Develop Water Supply Scheme (Rural and Urban) (Surface & Ground Water)

Overview: This unit describes the skills and knowledge required to understand various components of surface water based water supply scheme.

| Unit of Competency | Performance Criteria |
| --- | --- |
| Perform reconnaissance survey | Design and prepare survey forms/questionnaire for various aspects Prepare check list of conducting survey Pre-testing of survey questionnaire Conduct survey |
| Develop groundsurface levels and layout plan | Prepare layout plan Find out surface levels using dumpy level and GPS |
| Differentiate types of water supply systems | Study and recognize different types of water supply systems Recognize components of water supply systems Recognize components of surface treatment plants |
| Develop critical points in water supply systems | Find out key factors affecting water supply systems Carryout remedial measures for the critical points |
| Demonstrate basic hydraulics of water supply systems | Demonstrate basic concepts of hydraulics Carryout basic calculations |

### Estimate demand for Water Supply

Overview: This competency standard covers the skills and knowledge required to interpret Demand estimation in a water distribution network provides crucial data for monitoring and controlling systems. There is a need to estimate water demand from a limited number of sensor measurements. The demand estimation problem is underdetermined because of the limited sensor data and the implicit relationships between Demands and pressure heads.

| Competency Units | Performance Criteria |
| --- | --- |
| CU-1. Evaluate demand of water supply | - Calculate number of people - Identify people habits. - Calculate per capita consumption. - Check temperature. - Identify Losses - Identify quality & quantity of water - Identify rate of water supply |
| CU-2. Identify Water Layout Standards | P1. Calculate quantity of water P2. Identify number of hydrants P3. Suggest Spacing between Hydrants P4. Select supply of water by (gravity / pumping) P5. Suggest spacing between main line valves P6. Check flushing and maintenance procedures P7. Identify Standard Construction Specification |
| CU-3. Identify Rate of Demand for water | P1. Identify Seasonal variation P2. Calculate daily variation P3. Identify hourly variation |
| CU-4. Optimizing water supply network | P1. Identify Single-objective optimization P2. Identify Multi-objective optimization P3. Identify Sensitivity analysis P4. Check Operational constraints |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes the knowledge of:

K1.  Use graphical methods to solve hydrological problems such as hydrographs, flood prediction and extreme events.

K2.  Describe and explain the essential features of installations for the abstraction of water for Public consumption.

K3.  Describe and explain the essential features of installations for the treatment of water for public Consumption.

K4.  Describe and explain the essential features of installations for the distribution of water for Public consumption.

K5. Explain demand of water per capita rate

K6. Explain variation in demand of water

K7. Optimizing water supply network

K8. Explain safety precautions

K9. Explain demand of water for hilly & plain area

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Prepare layout of water standards

- Preparation is done according to area and standards

- Supply water procedures continuations

- Apply water maintenance procedures.

- Check construction specification for residential and commercial areas.

- Apply variation in demand of water supply

- Apply safety precautions

TOOLS AND EQUIPMENT’S

- Pipes

- Calculator

- Thermometer

- Valves

- Pipe repairs,

- Plungers,

- Pressure testing kits,

- Radiator tools

- Spirit level

- PPEs

### Perform civil work

Overview: This competency standard covers the skills and knowledge required to performe civil works in a water supply scheme

| Competency Units | Performance Criteria |
| --- | --- |
| - Pumping chamber | - Perform excavation. - Construct DPC. - Costruct super structure. - Install doors and window, - Perform flooring. - Execute finishing( painting) |
| - Storage tank | - Perform Soil investigation. - Carry out Excavation in foundation. - Construct Foundation. - Construct Superstructure. - Install fixtures |

Knowledge and understanding

- K1. Basic knowledge of civil work

- K2. Iron work

- Bearing capacity of soil.

- Types of Soil

Tools & Equipment

  - Measuring Tape

  - Masonry tool kit

  - Steel fixer tools

  - Measuring Tape

  - Masonry tool kit

### Plan water treatment (Clarification)

Overview: This competency standard covers the skills and knowledge required for basics of water Clarifiers and settling tanks built with mechanical means for continuous removal of solids being deposited by sedimentation. A clarifier is generally used to remove solid particulates or suspended solids from liquid.

| Competency Units | Performance Criteria |
| --- | --- |
| CU-1. Draw water treatment Plan | P1. Identify quantity of water P2. Show Grits removal chamber P3. Indicate Screens P4. Identify pumps P5. label settling tank P6. Label filtration stage P7. Indicate disinfection stage |
| CU-2. Plan Screening for water treatment | P1. Identify quantity of water P2. Identify quality of water. P3. indicate Screens operation |
| CU-3. Plan Clarifier for water treatment | P1. Identify quantity of water P2. Mark Primary Clarifier. P3. Mark secondary Clarifier |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes the knowledge of:

K1- Define water treatment process

K2- Define fundamentals steps for water treatment

K3- Explain Types of water

K4- Describe applications stages for water treatment

K5- Knowledge of repair and maintenance for treatment plant

K6- Knowledge of Market requirements of domestic and commercial water supply

K7. Explain filtration process in water treatment

K8. Explain different type of screens used for treatment of water

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Study of different stages of water treatment

- Installation of water treatment plant

- Plan a water treatment plant

- Plan stages for treatment plant

- Plan aeration method for treatment of water

- Indicate screens in treatment plant

- Identify clarifier in water treatment plant

TOOLS AND EQUIPMENT’S

- Drawing sheet

- Drawing instruments

- Pencils

- Eraser

- Compass

- Sprit level

- Calculator

- Umbrella (Optional)

- PPEs

### Plan water treatment (Filtration)

Overview: This competency standard covers the skills and knowledge required to prepare for water flows through a filter designed to remove particles in the water. The filters are made of layers of sand and gravel, and in some cases, crushed anthracite. Filtration collects the suspended impurities from water and enhances the effectiveness of disinfection work.

| Competency Units | Performance Criteria |
| --- | --- |
| CU-1. Draw water filtration process | P1. Identify source of water P2. Calculate quantity of water P3. indicate sand beds P4. Check filtration Rate P5. Select reducing Factor P6. indicate inlet & outlet |
| CU-2. Interpret Plan (Slow Sand Filter) at water treatment plant | P1. Identify water treatment plant P2. identify sand beds P3. Identify slow sand filters P4. Check filter media P5. Identify sand removal need |
| CU-3. Interpret Plan (Pressure Sand Filter) at water treatment plant | P1. Identify source of water P2. identify sand beds P3. Identify Rapid / Pressure filters P4. Check filter media P5. Identify back wash results P6. Check associated symptoms |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes the knowledge of:

K1- Knowledge of Safety requirements for drinking water after treatment

K2- Knowledge of water treatment process

K3- Explain different stages for water treatment process

K4- Explain filter media and it types

K5. Explain change of filter media at water treatment plant

K6. Describe slow and rapid sand filters at water treatment plant

K7. Explain reducing factor

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Perform safety requirements at water treatment plant

- Prepare plan for installation pumps at water treatment plant

- Performing repair and maintenance at plant

- Preform media replacement at water treatment plant

- Identify rapid & slow sand filters

- Identify working of sand filters

- Use of PPEs

- Set reducing factor

TOOLS AND EQUIPMENT’S

- Drawing sheet

- Drawing instruments

- Pencils

- Eraser

- Compass

- Sprit level

- Calculator

- Umbrella (Optional)

- PPEs

### Draw sketches of intakes

Overview: This competency standard covers the skills and knowledge required to Collection and Distribution of Water By providing a structure on the bank of River and Canals. The basic function of intake structure is to help in safely withdrawing water from the source and then to discharge this water in to the withdrawal conduit, through which it reaches the water treatment plant.

| Competency Units | Performance Criteria |
| --- | --- |
| CU-1. Draw Intake | P1. Identify equipment P2. Fix sheet P3. Select scale P4. Draw proposed sketch |
| CU-2. Conduct Design for Intake | P1. Select site selection P2. Check water quality condition P3. Check place for openings P4. Construct well upstream P5. Indicate flow system P6. Install pump to treatment plant |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes the knowledge of:

K1-Describe intakes and its type.

K2- Explain Marking out intakes.

K3- Explain procedure to take out water from intakes.

K4. Describe design procedure for intakes

K5. Explain safety precaution for task

K6. Describe fixing of pump method for intake

K7. Explain PPEs

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Mount pipe for intakes

- Install pump for intake properly

- Design the intake

- Execute intake plan

- Maintain connection from intakes

- Maintain pressure for pipes

TOOLS AND EQUIPMENT’S

- Pipes

- Calculator

- Thermometer

- Valves

- Pipe repairs,

- Plungers,

- Pressure testing kits,

- Radiator tools

- Spirit level

- PPEs

- Drawing sheet with drawing instruments

- Sealant

- Gasket

- Threading die

- Pipe Vice

- Flanges

- Pipe cutter

- Wrench set

- Scale card

- Spanner set

- Clamps

- Nuts, Bolts & Spring Washers

### Perform Distribution system of WSS

Overview: This competency standard covers the skills and knowledge required to perform the activites involved in the destributiion network water supply scheme (urban/rural ).

| Competency Units | Performance Criteria |
| --- | --- |
| - Laying jointing of pipe | - Carry out excavation in trenches. - Join pipes. |
| - Testing and disinfecting | - Perform pressure test. - Perform leakage test. |

Knowledge of understanding

- Laying jointing of pipes.

- Types of jointing and welding

- Hydraulics

Tools & Equipment’s

- Jointing solution.

- Pipe wrench

- Chain wrench

- Pump and motor

- Pressure gauge

## Water and Waste Water Testing (Physico-chemical Parameter)-III

### Perform Testing/Determination of Sodium (Na) by Flame-photometric Method

Overview: This competency standards covers the skill and knowledge required topreparesamples for testing, Prepare for laboratory testing, Perform tests on samples, Quality Control Checks, Record the results/ Finalize work and adopt the precautions during testing work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of analysis of Sodium. - keeps the sample at room temperature for few minutes. - Check for the availability of Sodium Standard solution of required concentration otherwise prepare as per standard procedure from reference stock solution of 1000 ppm as per requirement - Identify appropriate test method, Glassware, Equipment and safety requirements. |
| - Prepare for laboratory testing | - Set up test equipment Flam-photometer and/or reagents in accordance with the specified work instructions. - Conduct pre-use and safety checks. - Check the calibration status of equipment. Perform calibration if required. |
| - Perform tests on samples | - Turned on The fuel supply at the source. - turned “ON the Flam Photometer - Pressed on the ignition switch of Flam and adjust the flam from rotating knob of fuel adjuster - Select the sodium filter for the determination of sodium. - check the aspirating of photometer through suction of 10 ml deionized water per minute. If it is 2-6 ml then it is OK. - aspire the standard solution and adjust to obtain the positive reading. - Aspire the sample and note the results. - analyze three replicate for each sample. - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and store equipment. |
| - Quality Control Checks | - Method blank is analyzed after every 10 samples - Analyze Laboratory Control samples with every batch of 10 samples. - check repeatability by reanalysing a pre-analyzed sample once a day - Daily quality control data is recorded in QC Data sheet-I. - Results of laboratory control sample are regularly displayed in the form of control charts. |
| - Record the results/ Finalize work | - Note down the Results on analyst workbook. - Calculate uncertainty of theresults - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt the precautions during testing work | - Do not leave the instrument running unattended while the flame is alight. - The top of instrument chimney unit becomes very hot when running don’t touch it. Never attempt to look down the chimney whilst the flame is running. Always use the inspection window. - If high concentration salt solution is aspirated for longer periods then deionized water aspirate prior to shut down. - Take care when preparing standards. - Always take sample from top half of the sample. The bottom half may contain sediments that could block fine tubing. - Never use glass container to store calibration standards. |

Knowledge and Understanding

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

  - Understanding the basic principle of Flam-photometric sodium measurement i.e. determination of sodium concentration through thermally dissociation of sodium atoms further excited to high energy level, returning to ground state energy, the emit radiation are proportional to sodium concentration

  - Identifying sodium conc. In accordance to the requirement and hazards in water samples

  - Planning and organizing testing assignment

  - Using appropriate testing equipment and personal protective clothing and equipment

  - Understanding and applying procedures for testing

  - Determining and reporting accurate and relevant results from testing

Tools & Equipment

- Flam-photometer

- Auto Pipette 10 ml

- Sodium Standard (20-100 ppm)

- Deionized water

- Glass Beakers (Class A)

- Volumetric Flask 100 ml

### Perform Testing/Determination of Potassium (K) by Flame-photometric Method

Overview: This competency standards covers the skill and knowledge required to	Prepare samples  for testing, Prepare for laboratory testing, Perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt the precautions during testing work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of analysis of Potassium. - keeps the sample at room temperature for few minutes. - Check for the availability of Potassium Standard solution of required concentration otherwise prepare as per standard procedure from reference stock solution of 1000 ppm as per requirement - Identify appropriate test method, Glassware, Equipment and safety requirements. |
| - Prepare for laboratory testing | - Set up test equipment Flam-photometer and/or reagents in accordance with the specified work instructions. - P2: Conduct pre-use and safety checks. - P3: Check the calibration status of equipment. Perform calibration if required. |
| - Perform tests on samples | - The fuel supply is turned on at the source. - The meter is turned “ON” by pressing power switch. - The ignition switch is pressed to on the Flam and adjust the flam from rotating knob of fuel adjuster - For the determination of sodium select the sodium filter. - The suction of photometer is checked by aspirating 10 ml deionized water per minute. If it is 2-6 ml then it is OK. - Standard solution is aspirated and adjusted to obtain the positive reading. - When blank and standard are set. Unknown samples aspirated and the results noted. - Analyzed Three replicate for each sample. - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and store equipment. |
| - Quality Control Checks | - Method blank is analyzed after every 10 samples - Analyze Laboratory Control samples with every batch of 10 samples. - check repeatability by reanalysing a pre-analyzed sample once a day - Daily quality control data is recorded in QC Data sheet-I. - Results of laboratory control sample are regularly displayed in the form of control charts. |
| - Record the results/ Finalise work | - P1: Note down the Results on analyst workbook. - P2; Calculate uncertainty of theresults - P3: Record the results on result record form and submit to reporting section - P4: Clear and restore work area. |
| - Adopt the precautions during testing work | - P1: Do not leave the instrument running unattended while the flame is alight. - P2: The top of instrument chimney unit becomes very hot when running don’t touch it. Never attempt to look down the chimney whilst the flame is running. Always use the inspection window. - P3: If high concentration salt solution is aspirated for longer periods then deionized water aspirate prior to shut down. - P4: Take care when preparing standards. - P5: Always take sample from top half of the sample. The bottom half may contain sediments that could block fine tubing. - P6: Never use glass container to store calibration standards. |

Knowledge and Understanding

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

  - Understanding the basic principle of Flam-photometric potassium measurement i.e. determination of potassium concentration through thermally dissociation of potassium molecules in to atoms further excited to high energy level, returning to ground state energy, the emit radiation are proportional to potassium concentration

  - Identifying potassium conc. in accordance to the requirement and hazards in water samples

  - Planning and organizing testing assignment

  - Using appropriate testing equipment and personal protective clothing and equipment

  - Understanding and applying procedures for testing

  - Determining and reporting accurate and relevant results from testing

Tools & Equipment

- Flam-photometer

- Auto Pipette 10 ml

- Potassium Standard (5 &-10 ppm)

- Deionized water

- Glass Beakers (Class A)

- Volumetric Flask 100 ml

### Perform Testing/Determination of Nitrate (N) by Spectrophotometric Method

Overview: This competency standards covers the skill and knowledge required toPrepare samples  for testing, Prepare for laboratory testing, Perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt the precautions during testing work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of analysis of Nitrate. - keeps the sample at room temperature for few minutes. - Check for the availability of Nitrate Standard solution of 5-15 ppm otherwise prepare as per standard procedure from reference stock solution of 1000 ppm - Identify appropriate test method, Glassware and safety requirements. |
| - Prepare for laboratory testing | - Set up test equipment Turbidity meter and/or reagents in accordance with the specified work instructions. - Conduct pre-use and safety checks. - Check the calibration status of equipment. Perform calibration if required. - Conduct pre-use and safety checks. |
| - Perform tests on samples | - Take 10ml deionized Water in beaker and add 0.2 ml of 1N HCL in it - Apply special correction or blank correction - Now take 10ml standard or sample in cuvet and add HCL to it - Take absorbance reading at 220nm to measure nitrate concentration in the sample and at 275nm to determine organic interference - Subtract two times absorbance reading at 275nm from the reading at 220nm to obtain corrected reading - Determine the concentration from equation - Conc. of sample= Abs. of sample x Conc. of standard - Abs. of standard - If Spectrophotometer is set for concentration determination, directly measure concentration from calibration curve. - analyzed Three replicate for each sample. - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and store equipment. |
| - Quality Control Checks | - Method blank is analyzed after every 10 samples - Laboratory Control samples of 5 ppm analyzed with every batch of 10 samples. - check repeatability by reanalysing a pre-analyzed sample once a day - Daily quality control data is recorded in QC Data sheet-I. - Results of laboratory control sample are regularly displayed in the form of control charts. |
| - Record the results/ Finalise work | - Note down the Results on analyst workbook. - Calculate uncertaintyof theresults - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt the precautions during testing work | - Wash the reaction cell properly before analysis - Apply special correction and standard adjust features to eliminate variation of reagents - Acidification with 1N HCL is designed to prevent interferences from hydroxide or carbonate concentrations - If corrected value is more than 10% of the reading at 220nm then use other method. |

Knowledge and Understanding

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

- Understanding the basic principle of spectrometric Nitrate measurement i.e. determination of intensity of Nitrate by Measurement of UV absorption at 220nm enables rapid determination of nitrate while UV absorption at 275nm give indication of organic interferences. This is UV screening technique on spectrophotometer follow Beer’s Lambert Law.

  - Identifying Nitrate conc. In accordance to the requirement and hazards in water samples

  - Planning and organizing testing assignment

  - Using appropriate testing equipment and personal protective clothing and equipment

  - Understanding and applying procedures for testing

  - Determining and reporting accurate and relevant results from testing

Tools & Equipment

- Spectrophotometer

- Auto Pipette 10 ml

- Nitrate Standard (5-15 ppm)

- HCl   I N

- Glass Beaker (Class A)

- Volumetric Flask 100 ml

### Perform Testing/Determination of Sulphate (SO4) by Spectrophotometric Method (Turbidity metric)

Overview: This competency standards covers the skill and knowledge required toPrepare samples  for testing, Prepare for laboratory testing,	Perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt the precautions during testing work

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of analysis of Sulphate. - keeps the sample at room temperature for few minutes. - Check for the availability of Sulphate Standard solution of required concentration otherwise prepare as per standard procedure from reference stock solution of 1000 ppm as per requirement - Identify appropriate test method, Glassware, Equipment and safety requirements. |
| - Prepare for laboratory testing | - Set up test equipment Spectrophotometer and/or reagents in accordance with the specified work instructions. - Conduct pre-use and safety checks. - Check the calibration status of equipment. Perform calibration if required. - Conduct pre-use and safety checks. |
| - Perform tests on samples | - Take 10ml of deionized water in cuvet and add 2 ml of Sulphate Buffer (Use Buffer solution B for samples having concentration >10ppm and Buffer solution A for other). - Add one pinch of Barium chloride crystals in the above solution, stir it vigorously and take absorbance reading after 5 minutes reaction time at wavelength of 420nm. - perform testing with actual water samples and determine the concentration from equation - Conc. of sample= Abs. of sample x Conc. of standard - Abs. of standard - Directly measure concentration from calibration curve, if Spectrophotometer is set for concentration determination - analyzed Three replicate for each sample. - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and store equipment. |
| - Quality Control Checks | - Method blank is analyzed after every 10 samples - Laboratory Control samples of 10 ppm analyzed with every batch of 10 samples. - check repeatability by reanalyzing a pre-analyzed sample once a day - Daily quality control data is recorded in QC Data sheet-I. - Results of laboratory control sample are regularly displayed in the form of control charts. |
| - Record the results/ Finalize work | - Note down the Results on analyst workbook. - Calculate uncertainty of theresults - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt the precautions during testing work | - Apply wavelength and special correction before start of sample analysis - Verify the reliability of the already prepared curve by running number of known standards. - The pH of the buffer solution must be in the range (2.50-3.50) to avoid decomposition of BaSO4. - Accuracy of the calibration curve decreases at concentration greater than 40 ppm due to decomposition of BaSO4, therefore, it is recommended to make dilution if the concentration is higher than 40 ppm. |

Knowledge and Understanding

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

- Understanding the basic principle of spectrometric Sulphate measurement i.e. determination of intensity of SO4 by  the measurement  process when Sulphate ion (SO4-2) is precipitated in an acidic (pH 2.50-3.50) medium with barium chloride (BaCl2) so as to form barium sulphate crystals of uniform size. Measurement as absorbance of the barium sulphate suspension on spectrophotometer is based on Beer’s Lambert Law

  - Identifying sulphate conc. In accordance to the requirement and hazards in water samples

  - Planning and organizing testing assignment

  - Using appropriate testing equipment and personal protective clothing and equipment

  - Understanding and applying procedures for sulphate testing

  - Determining and reporting accurate and relevant results from testing

Tools & Equipment

- Spectrophotometer

- Auto Pipette 10 ml

- Sulphate Standards Solutions

- Sulphate Buffer

- Barium Chloride Crystals

- Spatula

- Glass Beaker (Class A)

- Volumetric Flask 100 ml

## Water Quality Testing( Heavy metals)

### PerformTesting/Determination of Arsenic by Atomic Absorption Spectrometer

Overview: This competency standards covers the skill and knowledge required to prepare samples  for testing, Prepare for laboratory testing,	Perform tests on samples, Quality Control Checks, Record the results/ Finalise work and Adopt the precautions during testing work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of analysis of Arsenic. - keeps the sample at room temperature for few minutes. - Check for the availability of Arsenic Standard solution 5-25 ppb otherwise prepare as per standard procedure from reference stock solution of 1000 ppm - Identify appropriate test method, Glassware equipment and safety requirements. |
| - Prepare for laboratory testing | - Set up test equipment AAS and/or reagents in accordance with the specified work instructions. - Conduct pre-use and safety checks. - Check the calibration status of equipment. Perform calibration if required. - Conduct pre-use and safety checks. |
| - Perform tests on samples | - Open the AAS Software, select Hydride Generation Mode. - Load Method for Arsenic or draw new calibration curve. - Adjust the parameter (energy of the lamp and heating temperature of quartz cell). - Click on the option “Sample” and insert the sample codes in sample table. - Wash the sample cup and sampling tip with deionized water. - Take 10ml of sample in Reaction cup. - Add 1ml concentrated. HCl in reaction cup and mount on batch module. - Click on the “Run Sample” option from software. - analyzed Three replicate for each sample. - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and store equipment. |
| - Quality Control Checks | - analyze Blank and Certified Reference Standard after every ten samples. - Analyze pre-analyzed sample with every analytical batch. - Analyze Spiked Matrix sample after every two months - Analyze the Control Sample and display data is regularly on control charts. - Record the daily quality control data in QC Data sheet. |
| - Record the results/ Finalise work | - Note down the Results on analyst workbook. - Calculate uncertainty of theresults - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt the precautions during testing work | - All the glassware should be washed with 1:1 HCl before preparation of standard solution and samples. - Auto-pipettes should be used carefully to take accurate volume during the analysis. - Deionized water used should be of high quality having EC <1.5µS/cm. |

Knowledge of Understanding

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

- Understanding the basic principle of Arsenic measurement i.e. Arsenic present   in the sample react with sodium borohydride in acidic medium and form Arsine gas (AsH3) which is carried by argon gas to the heated quartz cell. Where atomization of As. takes place at 950oC.

- The radiation (λ max 193.7 nm) coming from Arsenic lamp passes through the quartz cell where these are absorbed by As atoms and this absorption of radiation is measured by the instrument. Principal of absorbance is according to Beer Lambert Law i.e. absorbance of radiation is directly proportional to concentration or no. of particles and path length of the medium

- Identifying Arsenic conc. in accordance to the requirement and hazards in water samples

- Planning and organizing testing assignment

- Using appropriate testing equipment and personal protective clothing and equipment

- Understanding and applying procedures for testing

- Determining and reporting accurate and relevant results from testing.

Tools & Equipment

- Atomic Absorption Spectrometer (AAS)

- Auto Pipette 1- 10 ml

- Arsenic Standard (5-25 ppb)

- 3% Sodium borohydride Solution

- Conc. Hydrochloric Acid.   (HCl)   37%

- Glass Beakers (Class A)

- Volumetric Flask 100 ml

- Volumetric Flask 250 ml

- Volumetric Flask 1000 ml

### Perform Testing/Determination of Copper (Cu) by Atomic Absorption Spectrometer

Overview: This competency standards covers the skill and knowledge required toPrepare samples  for testing, Prepare for laboratory testing,	Perform tests on samples, Quality Control Checks, Record the results/ Finalise work and Adopt the precautions during testing work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of analysis of Copper. - keeps the sample at room temperature for few minutes. - Check for the availability of Copper Standard solution 0.2-1 ppm otherwise prepare as per standard procedure from reference stock solution of 1000 ppm - Identify appropriate test method, Glassware equipment and safety requirements. |
| - Prepare for laboratory testing | - Set up test equipment AAS and/or reagents in accordance with the specified work instructions. - Conduct pre-use and safety checks. - Check the calibration status of equipment. Perform calibration if required. - Conduct pre-use and safety checks. |
| - Perform tests on samples | - Open the AAS Software select Flam Mode. - Load Method for Copper or draw new calibration curve. - Adjust the parameter (energy of the lamps, auto sampler parameters and adjustment of air acetylene flam parameter according to the manufacturer instructions). - Insert the sample codes in sample table along with giving the sample cup positions as in autosampler. - Take sample in sample cup of autosampler up to the mark and put in specific position of sample tray of auto sampler. - Ignite the flam by clicking on the ignition option in main option “Flam”. - Run Sample from software or click on option “Start Conc.” after selecting the range of samples in table by giving working area in case of autosampler used. - Feed each sample one by one manually in case of working without autosampler - analyze three replicate for each sample. - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and store equipment. |
| - Quality Control Checks | - analyze Blank and Certified Reference Standard after every ten samples. - Analyze pre-analyzed sample with every analytical batch. - Analyze Spiked Matrix sample after every two months - Analyze the Control Sample and display data is regularly on control charts. - Record the daily quality control data in QC Data sheet-I. |
| - Record the results/ Finalise work | - Note down the Results on analyst workbook. - Calculate uncertainty of theresults - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt the precautions during testing work | - All the glassware should be washed with 1N HNO3 before preparation of standard and samples. - Auto-pipettes should be used carefully to take accurate volume during the analysis. - Deionized water used should be of high quality having EC <1.5µS/cm. |

Knowledge of Understanding

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

- Understanding the basic principle of copper measurement i.e. Sample is aspirated in burning flam of air-Acetylene Through nebulizer. Copper present in the sample is atomized in burning flam.. The radiation (λmax324.8 nm) coming from copper lamp passes through the Burning flam where these are absorbed by copper atoms and this absorption of radiation is measured by the Instrument. Principal of absorbance is according to Beer Lambert Law i.e. absorbance of radiation is directly proportional to concentration or no. of particles and path length of the medium.

- Identifying copper conc. in accordance to the requirement and hazards in water samples

- Planning and organizing testing assignment

- Using appropriate testing equipment and personal protective clothing and equipment

- Understanding and applying procedures for testing

- Determining and reporting accurate and relevant results from testing.

Tools & Equipment

- Atomic Absorption Spectrometer (AAS)

- Auto Pipette 1- 10 ml

- Copper Standard (0.2-1 ppm)

- 0.2% HNO3

- 1N HNO3

- Glass Beakers (Class A)

- Volumetric Flask 100 ml

- Volumetric Flask 250 ml

- Volumetric Flask 1000 ml

### Perform Testing/Determination of Zinc (Zn) by Atomic Absorption Spectrometer

Overview: This competency standards covers the skill and knowledge required toPrepare samples for testing, prepare for laboratory testing,	perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt the precautions during testing work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of analysis of Zinc. - keeps the sample at room temperature for few minutes. - Check for the availability of Zinc Standard solution as per requirement otherwise prepare as per standard procedure from reference stock solution of 1000 ppm - Identify appropriate test method, Glassware equipment and safety requirements. |
| - Prepare for laboratory testing | - Set up test equipment AAS on Flam Mode and/or reagents in accordance with the specified work instructions. - Conduct pre-use and safety checks. - Check the calibration status of equipment. Perform calibration if required. - Conduct pre-use and safety checks. |
| - Perform tests on samples | - Open the AAS Software selects Flam Mode. - Load Method for Zinc or draw new calibration curve. - Adjust the parameter (energy of the lamps, auto sampler parameters and adjustment of air acetylene flam parameter according to the manufacturer instructions). - Insert the sample codes in sample table along with giving the sample cup positions if autosampler is used. - Take sample in sample cup of autosampler up to the mark and put in specific position of sample tray of auto sampler. - Ignite the flam by ignition option in main option in software - Run Sample from software or click on option “Start Conc.” after selecting the range of samples in table by giving working area in case of autosampler. - feed each sample one by one manually in case of working without autosampler - analyzed three replicate for each sample. - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and store equipment. |
| - Quality Control Checks | - analyze Blank and Certified Reference Standard after every ten samples. - Analyze pre-analyzed sample with every analytical batch. - Analyze Spiked Matrix sample after every two months - Analyze the Control Sample and display data is regularly on control charts. - record the daily quality control data in QC Data sheet-I. |
| - Record the results/ Finalise work | - Note down the Results on analyst workbook. - Calculate uncertainty of theresults - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt the precautions during testing work | - All the glassware should be washed with 1N HNO3 before preparation of standard and samples. - Auto-pipettes should be used carefully to take accurate volume during the analysis. - Deionized water used should be of high quality having EC <1.5µS/cm. |

Knowledge and Understanding

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

- Understanding the basic principle of zinc measurement i.e. Sample is aspirated in burning flam of air-Acetylene through nebulizer. Zinc present in the sample is atomized in burning flam. The radiation (λ max 213.9 nm) coming from Zinc lamp passes through the flam where these are absorbed by zinc atoms and this absorption of radiation is measured by the instrument. Principal of absorbance is according to Beer Lambert Law i.e. absorbance of radiation is directly proportional to concentration or no. of particles and path length of the medium.

- Identifying zinc conc. in accordance to the requirement and hazards in water samples

- Planning and organizing testing assignment

- Using appropriate testing equipment and personal protective clothing and equipment

- Understanding and applying procedures for testing

- Determining and reporting accurate and relevant results from testing.

Tools & Equipment

- Atomic Absorption Spectrometer (AAS)

- Auto Pipette 1- 10 ml

- Zinc Standard Solution

- 0.2% HNO3

- 1N HNO3

- Glass Beakers (Class A)

- Volumetric Flask 100 ml

- Volumetric Flask 250 ml

- Volumetric Flask 1000 ml

### Perform Testing/Determination of Manganese (Mn) by Atomic Absorption Spectrometer

Overview: This competency standards covers the skill and knowledge required toPrepare samples  for testing, Prepare for laboratory testing, Perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt the precautions during testing work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of analysis of Manganese. - keeps the sample at room temperature for few minutes. - Check for the availability of Manganese Standard solution as per required concentration otherwise prepare as per standard procedure from reference stock solution of 1000 ppm - Identify appropriate test method, Glassware equipment and safety requirements. |
| - Prepare for laboratory testing | - Set up test equipment AAS on Flam Mode and/or reagents in accordance with the specified work instructions. - Conduct pre-use and safety checks. - Check the calibration status of equipment. Perform calibration if required. - Conduct pre-use and safety checks. |
| - Perform tests on samples | - Open the AAS Software and selects Flam Mode. - Load Method for Manganese or draw new calibration curve. - Adjust the parameter (energy of the lamps, auto sampler parameters and adjustment of air acetylene flam parameter according to the manufacturer instructions). - Insert the sample codes in sample table along with giving the sample cup positions as in autosampler. - Take sample in sample cup of autosampler up to the mark and put in specific position of sample tray of auto sampler. - Ignite the flam by clicking on the ignition option in main option “Flam”. - Run Sample from software or click on option “Start Conc.” after selecting the range of samples in table by giving working area in case of autosampler. - Feed each sample one by one manually in case of working without autosampler. - Analyzed three replicate for each sample. - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and store equipment. |
| - Quality Control Checks | - Analyze Blank and Certified Reference Standard after every ten samples. - Analyze pre-analyzed sample with every analytical batch. - Analyze Spiked Matrix sample after every two months - Analyze the Control Sample and display data is regularly on control charts. - Record the daily quality control data in QC Data sheet-I |
| - Record the results/ Finalise work | - Note down the Results on analyst workbook. - Calculate uncertainty of theresults - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt the precautions during testing work | - All the glassware should be washed with 1N HNO3 before preparation of standard and samples. - Auto-pipettes should be used carefully to take accurate volume during the analysis. - Deionized water used should be of high quality having EC <1.5µS/cm. |

Knowledge and Understanding

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

- Understanding the basic principle of manganese measurement i.e. Sample is aspirated in burning flam of air-Acetylene Through nebulizer. Manganese present in the sample is atomized in burning flam of air acetylene.

- The radiation (λmax279.5 nm) coming from Manganese lamp passes through the burning flam where these are absorbed by Manganese atoms and this absorption of radiation is measured by the instrument. Principal of absorbance is according to Beer Lambert Law i.e. absorbance of radiation is directly proportional to concentration or no. of particles and path length of the medium.

- Identifying Manganese conc. in accordance to the requirement and hazards in water samples

- Planning and organizing testing assignment

- Using appropriate testing equipment and personal protective clothing and equipment

- Understanding and applying procedures for testing

- Determining and reporting accurate and relevant results from testing.

Tools & Equipment

- Atomic Absorption Spectrometer (AAS)

- Auto Pipette 1- 10 ml

- Manganese Standard (0.2-1 ppm)

- 1N HNO3

- Glass Beakers (Class A)

- Volumetric Flask 100 ml

- Volumetric Flask 250 ml

- Volumetric Flask 1000 ml

## Operations and Maintenance of Water Supply Scheme

### Use Maps, Plans, Drawings and Specifications for Water Works

Overview: This competency standards covers the skill and knowledge required to Interpret maps, plans, drawings and specifications.

| Competency Units | Performance Criteria |
| --- | --- |
| - Interpret maps, plans, drawings and specifications | - Identify types of maps, plans, drawings and specifications required to undertake work tasks. - Identify parts of the water system and their inter-relationship on a range of drawing types. - Interpret commonly used symbols and abbreviations. - Interpret and apply the function of the legend. - Verify latest version. - Identify natural and man-made features on maps, plans and drawings. - Relate specifications to maps, plans and drawings and identify quality standards. - Identify types of details from works specifications. |

Knowledge of Understanding

Required skills:

  - locating maps, plans, drawings and specifications for work tasks

  - locating work sites

  - using information provided in maps, plans and drawings to complete a task

  - preparing a simple map or plan that represents an actual or simulated work environment

  - applying problem solving strategies

Required knowledge

- the range of maps, plans and drawings to different assignment situations

- basic formulae of volumes, area and mass

- features of maps, plans and drawings including:

- contours

- datum points

- planes

- gradients

- sections

- orthographic projections

- symbols

- dimensions

- Terminology

### Maintain and Repair Water Distribution Network

Overview: This competency standards covers the skill and knowledge required to plan and prepare for work, conduct maintenance and repairs and review, report and record work

.

| Competency Units | Performance Criteria |
| --- | --- |
| - Plan and prepare for work | - Conduct risk assessment for environmental, safety and water quality factors. - Determine work requirements, materials and configuration from plans, specifications, instructions and/or organizational procedures. - Check coordination issues with relevant personnel, including isolations, licences and permits to work. - Identify networks system operation requirements. - Arrange appropriate site protection. - Identify and notify customers of supply interruption. |
| - Conduct maintenance and repairs | - Isolate the work area. - Determine appropriate repair method from job specifications and instructions. - Ensure materials, pipes and fittings are clear of any contaminants before installing. - Sterilize fittings and repair materials. - Check maintenance and repairs to assets to ensure specifications are met. - Restore work site to meet environmental and organisational requirements. |
| - Review, report and record work | - Check, tag and report faulty equipment and tools. - Store equipment, tools and materials. - Complete workplace records. |

Knowledge of Understanding

Required skills:

- planning work site including personnel, equipment, materials

- requesting permits, approvals, other utilities diagrams and maps

- implementing appropriate controls

- using tools and specific water equipment

- selecting and applying appropriate PPE

- performing work-related calculations

- applying disinfection to tools and materials

- using communication tools including phones and laptops

- interpreting plans, instructions and procedures

- ensuring system hygiene and water quality

- determining location, size, utilities, services from plans, specifications and organizational procedures

- applying excavation techniques

- maintaining and repairing assets

- maintaining and repairing tanks by monitoring and operating flow-regulating devices to isolate tanks

- maintaining and repairing minor structures by laying concrete

- system hydraulics basics

- environmental aspects of maintenance

- relevant legislation, policies and procedures

- material safety data sheets (SDS)

- landscape and ground structure of work area

- risk factors and potential hazards of maintenance processes

- equipment operation, capacity and limitations

- control systems

- disinfection of systems and chemical usage

- pipe systems and installation requirements

- characteristics of pipe materials

- testing and sampling systems

- corrosion principles applicable to service pipes and fittings

- operation of water meters

- formwork preparation and positioning

- methods of repairing concrete, brick and stone structures

- concrete placement techniques, including compaction

- relevant utilities and service bodies to identify allocation of road reserve

- effects of weather and conditions on construction site or plan

- requirements around excavation

### Perform Leak Detection

This unit describes the outcomes required to plan leak detection activities and to locate, identify and report leaks in water distribution networks (pressure mains).

| Competency Units | Performance Criteria |
| --- | --- |
| - Plan for leak detection | - Determine work site boundaries and leak detection requirements from plans, specifications and instructions. - Select and check equipment. - Plan for leak detection using site inspection and service search diagrams according to work site requirements. |
| - Operate leak detection equipment and report work | - Determine and mark work site boundaries from plans and service search diagrams. - Select, fit and use personal protective equipment. - Operate leak detection equipment. - Mark the location of leaks. - Expose leaks and arrange repair according to testing outcomes and organizational and statutory requirements. - Review, record and report work. |

Knowledge of Understanding

Required Skills

  - analysing data to take remedial action

  - interpreting plans, specifications, policies and procedures

  - providing maintenance records for equipment

  - identifying safety risks and hazards

  - planning leak detection activities

  - locating, identifying and reporting leaks in water distribution networks

  - operating leak detection equipment

  - locating and marking leaks and arranging repair activities

  - completing documentation

  - basic calculation

  - identification, repair, lock out procedures

  - system hydraulics

  - system layout

  - environmental aspects

  - relevant utilities and service bodies

## Water Filtration and Treatment

### Design Water Treatment Plant (Surface and Groundwater)

Overview: This competency standard covers the skill and knowledge required to identify, plan and design water treatment needs, prepare and maintain supporting documentation.

| Competency Units | Performance Criteria |
| --- | --- |
| - Determine water filtration and treatment design requirements | - Determine the quality of water to be treated and level of treatment required - Determine Input and output water quality and quantity requirement - Select treatment process and combination of technologies required - Determine plant size to meet site requirements for water quantity and quality - Determine plant layout and land requirements reviewed - Prepare design drawings. - Prepare construction specification |
| - Define pumping and power systems | - Select pumps to treat water as required and to enable supply at the flow and the pressure required to operate the distribution system - Confirm that the pump motor combinations are effective and the pumps are reliable, functional, serviceable for the required application - Calculate energy requirements and determine the layout of electricity lines - Selectstructures, valves and accessories and integrate into a functional system |
| - Design a water treatment system | - Evaluate and design treatment systems with respect to target contaminants - Size pipes, valves and fittings according to design system specifications - Calculate and document flows, water levels and pressures to be within the acceptable tolerances for optimum performance - Confirm that flows, water levels and pressures are achievable by the pumps operating at optimum efficiency - Include mechanisms for controlling and adjusting pressure |
| - Estimate the cost of components of plant | - Make a list of all required items and services for installation of water treatment plant - Estimate market cost of all items and services required |
| - Install the water treatment plant | - Arrange tools and equipment for installing water treatment equipment, including personal protective equipment. - Prepare work area to support efficient installation of water treatment equipment - Installand assemble plant as per design and manufacturespecifications, and organizational requirements. - Check the Connections to water treatment equipment Installation is pressure tested for leaks. - Identify the service and maintenance requirements for water filters and pumps - Check replacement components and their fittings according to specification. - Conduct maintenance operations as per standards - Clear the work area according to legislation, regulations, codes of practice and job specification. - Clear and check the tools and equipment and store according to manufacturer recommendations and workplace procedures. - Complete the documentation according to workplace requirements. |
| - Monitor water treatment process | - Conduct routine inspections of treatment equipment - Collect water samples and conduct standard tests or send samples for analysis where required by the biosecurity and food safety codes - Collect data on treatment process and record and report in appropriate manner - Monitor water and waste water treatment processes to maintain parameters of operation - Identify and report process faults and operational conditions of treatment equipment - Initiate basic equipment and process adjustments to enhance performance |

Knowledge and Understanding

  - Water treatment system hydraulics basics

  - environmental aspects of maintenance

  - relevant legislation, policies and procedures

  - landscape and ground structure of work area

  - risk factors and potential hazards of maintenance processes

  - equipment operation, capacity and limitations

  - control systems

  - disinfection of systems and chemical usage

  - pipe systems and installation requirements

  - characteristics of pipe materials

  - corrosion principles applicable to service pipes and fittings

  - operation of water meters

  - effects of weather and conditions on construction site or plan.

  - principles and practices of water treatment system design

  - developments in water treatment technology

  - environmental impacts of water treatment

  - environmental protection agency regulations

  - waste management and environmental issues

Tools & Equipment

- Water Analysis report

- Site drawings

- Soil Investigation report

- Designing software

- CAD software

### Operate and Control Coagulation and Flocculation Process

Overview: This competency standard covers the skill and knowledge required to undertake coagulation and flocculation processes, control chemical use, operate and control coagulation and flocculation systems and maintains records.

| Competency Units | Performance Criteria |
| --- | --- |
| - Monitor coagulation and flocculation processes | - Monitor water quality test results and processes to understand need of surface water treatment. - Collect and test samples to report turbidity and chemical contaminants. - Conduct jar tests and determine dosages of flocculent/coagulants. |
| - Control chemical use | - Use, handle and store chemicals as per manufacturer’s instructions. - Determine and apply chemical dosing according to plant processes based on jar testing calculated dose. - Maintain chemical supply and usage records. |
| - Operate and control coagulation and flocculation processes | - Carry out routine plant inspections. - Collect process samples and conduct standard tests such as jar testing. - Add the calculated dose of flocculent/coagulants. - Carry out system adjustments and process calculations to improve system performance whenever water quality changes or process performance deteriorates. - Identify and report process faults and the operational condition of plant. |
| - Complete Documentation | - Compile reports from plant and system data. - Report observations outside defined parameters for further action. |

Knowledge of Understanding

- process layout

- chemicals used i.e. polymers, coagulants, flocculants and pH correction

- features and components of coagulation and flocculation systems

Process operations including:

- chemical addition

- flash mixing

- flocculation

- risk factors and potential hazards related to coagulation and flocculation systems including:

- pH adjusting chemicals such as lime, soda ash, caustic soda

- risk control requirements including safety equipment and safety data sheets (SDS)

- operation of pumping and valving systems

- water testing procedures

- procedures for storing and handling dangerous goods and chemicals

### Operate and control of sediment process

Overview:This competency standard covers the skill and knowledge required to undertake and monitor sedimentation processes and report the process.

| Competency Units | Performance Criteria |
| --- | --- |
| - Plan and prepare for work. | - Determine work requirements according to legislative and water treatment objectives. - Select and check equipment required to meet safety requirements of task and site. - Select, fit and use personal protective equipment. |
| - Monitor and operate sedimentation processes | - Carry out sedimentation process inspections according to type of plant. - Collect process samples and conduct standard tests. - Collect and report process data. - Monitor processes to maintain parameters of operation. - 2Identify and report process faults and operational condition of plant - Carry out basic system adjustments to enhance system performance according to treatment standards and objectives |
| - Report sedimentation processes. | - Compile records from plant and system data to meet water treatment standards. - Report observations outside defined parameters for further action. |

Knowledge and Understanding

- principles that form the basis of sedimentation processes

- system layout

- lock-out procedures for mechanical and electrical installations

- policies, procedures and legislation relating to water treatment

- risk factors and potential hazards

- basic system calculations, equipment operation, capacity  and limitations effects of changes  in hydraulic load on sedimentation processes

- identify and respond to operational problems

- produce reports and logs

- use safety equipment and personal protective equipment

- follow plans, charts and instructions

- perform system calculations

- apply procedures and standards

- identify control system faults

Tools & Equipment

  - electronic monitoring and metering systems

  - recording systems

  - basic hand and power tools

  - sampling and laboratory testing equipment

  - personal protective equipment

### Operate and control Water Filtration processes (Membrane Straining)

Overview: this competency standard covers the skill and knowledge required to select and operate water filters, monitor filtration system performance, manipulate and apply low and high pressure dosing and maintain record.

| Competency Units | Performance Criteria |
| --- | --- |
| - Rapid/Pressure Sand Filtration (RSF) and Specifications of media | - Identify physical and hydraulic specifications of commercial sand vessels - Recognize the various particle sizes of media and demonstrate laboratory scale preparation of sand bed - Sketch a flow diagram of RSF plant to achieve drinking water standards. - Select, fit, operate and back-wash RSF. - Prepare Performa for daily and monthly O&M records |
| - GAC Filtration and Specifications of medium | - Identify the principles of adsorption and specifications of GAC medium - Sketch a flow diagram to show position of GAC vessel to achieve its effectiveness. - Select, install, operate and back-wash GAC filter. |
| - Membrane Water Treatment Technologies | - Identify the principles of Osmosis and Reverse Osmosis. - Sketch a flow diagram of UF/RO plant showing main components and controlling devices. - Demonstrate operations of start, stop and membrane separation of the UF/ RO plant - Identify pretreatment module, feed line, permeate line, retentate outlet, and anti-scalent inlet line in RO. |
| - Documentation | - Compile reports from plant and system data. - Report observations outside defined parameters for further action. |

Knowledge of Understanding

- identify and respond to operational problems

- Identify the objective of filtration

- use safety and personal protective equipment

- follow plans, charts and instructions

- Identify good hydraulic qualities, effective sizes and good filtration characteristics

- Recognize differences between slow, rapid and pressure sand filtration processes

- Identify limitations of reducing filter area by increasing the rate of filtration

- Identify flow control online devices in membrane filtration

- Identify online quality control devices in membrane process

- Make a start up and shut down checklist and follow these instruction

- Identify high pressure pumping in RO system

- operation, capacity and limitations of RO system

- Recognize butterfly, pressure release valve and scaling of RO membrane

- Identify relation between membrane sizes and consequent effects on flow rating of product water and power rating of high pressure pump

Tools & Equipment

  - Filter opening keys

  - Pipe cutter

  - Levels

  - Flow meter

  - Pressure gauges

  - Pipe wrenches

  - Screw drivers

  - Dosing pupmps

  - Water Storage Reservoirs

  - Electrical control system

  - basic hand and power tools

  - sampling and laboratory testing equipment

  - personal protective equipment

  - online measurements devices like flow meter, TDS meter

### Operate and Control Chlorination Disinfection processes

Overview: This competency standard covers the skill and knowledge required toapply chlorination dosing and reporting the chlorination processes.

| Competency Units | Performance Criteria |
| --- | --- |
| - Plan and prepare for work. | - Determine work requirements from job specifications and plans - Select and check equipment and hypochlorite supplies to meet safety requirements of task and worksite - Select, fit and use required safety equipment, including personal protective equipment (PPE) - Handle and store hypochlorite chemicals to maximise shelf life and reduce loss of available chlorine |
| - Monitor process performance | - Conduct the percentage available chlorine test - Monitor hypochlorite disinfection processes as per standards - Collect process samples and conduct standard tests according to water treatment procedures - Make process adjustments to maintain effectiveness of hypochlorite disinfection - Monitor chlorination processes according to agreed schedule and procedures. - Collect treated water samples and test total and free chlorine as per standards. - Maintain and monitor relevant OHS requirements. - Collect test data, perform calculations and report according to organizational and chlorination process requirements. |
| - Prepare and apply chlorine dosing. | - Calculate chlorine dose as per volume of water to be treated. - Prepare and apply hypochlorite chemicals in the water as per calculated dose manually or using chlorinator - Control hypochlorite dosing to maintain required chlorine residual - Handle, use and store chlorine chemicals according to organizational requirements. |
| - Prepare and operate chlorinators |  |
| - Report on chlorination processes | - Maintain information relating to hypochlorite supply and usage - Collect, record and complete process data according to workplace procedures and process requirements - Produce information relating to maintenance and operation according to organizational requirements. - Identify data outside of normal operational parameters and report to relevant personnel for further action |

Knowledge and Understanding

- properties of chlorination chemicals

- Chlorine disinfection and its relationship to public health

- Total and free chlorine sampling and record keeping

- Chlorinator types and operation

- lock-out procedures for mechanical and electrical installations

- policies and standard operating procedures for chlorination

- safe handling and disposal of chlorine chemicals

- risk factors and potential hazards associated with chlorination

- work-related chlorine calculations

- Chlorine dosing processes

- Chlorination equipment operation, capacity and limitations

- Pumping and valving systems

- Automatic feed rate control system.

- identify and respond to operational problems

- produce reports and logs

- use safety and personal protective equipment

- follow plans, charts and instructions

- perform chemical dosing calculations

- prepare and apply chlorine dosing

- identify and report control system faults

- identify and report hazards

- perform chlorine residual sampling and testing

- effects of pH, time, temperature, UV exposure and impurities on hypochlorite breakdown

- hypochlorite dosing system layout for sodium hypochlorite or calcium hypochlorite dosing systems

- impact of pH

- microbiological guidelines

- properties and chemistry of hypochlorite chemicals

- reactions with water to produce hypochlorous acid/hypochlorite ion

- relevant legislation, regulations and workplace procedures

- risk factors and potential hazards associated with hypo chlorination

Tools & Equipment

  - identify and respond to operational problems

  - produce reports and logs

  - use safety and personal protective equipment

  - follow plans, charts and instructions

  - perform chemical dosing calculations

  - prepare and apply chlorine dosing

  - identify and report control system faults

  - identify and report hazards

  - perform chlorine residual sampling and testing

### Operate and Control UV Disinfection Process

Overview: This competency standard covers the skill and knowledge required to plan and prepare for work., monitor UV disinfection system performance, maintain and operate UV irradiation disinfection system and complete related records/documentation.

| Competency Units | Performance Criteria |
| --- | --- |
| - Plan and prepare for work. | - Determine treatment and disinfection work requirements according to legislative and organizational requirements. - Select and check equipment and tools required to meet safety requirements of task and site. - Select, fit and use personal protective equipment. |
| - Monitor system performance | - Monitor UV irradiation disinfection systems according to agreed schedule and procedures. - Collect process samples and conduct standard microbiological tests as required. - Maintain and monitor relevant OHS requirements. - Collect and report process data according to organizational and disinfection system requirements. |
| - Maintain and operate UV irradiation disinfection system. | - Carry out routine inspections of system components according to organizational requirements. - Clean and replace system components as required. - Operate UV lamp sequencing according to organizational requirements. |
| - CompleteDocumentation | - Produce information relating to UV irradiation disinfection system maintenance and operation, according to organizational requirements. |

Knowledge of Understanding

- properties of UV irradiation

- microbiological water quality guidelines

- UV irradiation disinfection system layout, including components

- lock-out procedures for mechanical and electrical installations

- policies, standard operating procedures and legislation

- safe use of cleaning chemicals and prevention of associated hazards

- risk factors and potential hazards associated with UV irradiation systems

- UV irradiation generation equipment operation, capacity and limitations

- effects of weather and conditions on operation of site or plant

- identify and respond to operational problems

- produce reports and logs

- use safety equipment

- use UV-absorbent personal protective equipment

- follow plans, charts and instructions

- identify control system faults

- identify hazards

- perform microbiological sampling

### Operate and Control Ozonation Process in Water Treatment Plant

Overview: This competency standard covers the skill and knowledge required to plan and prepare water treatment work, monitor Ozonation system performance, prepare and apply ozone dosing and maintain record.

| Competency Units | Performance Criteria |
| --- | --- |
| - Plan and prepare for work | - Determine work requirements according to legislative and organizational requirements. - Select and check equipment and tools required to meet safety requirements of task and site. - Select, fit and use personal protective equipment. |
| - Monitor system performance | - Understand the objective of ozone disinfection for different applications - Monitor ozone treatment systems according to agreed schedule and procedures. - Collect process samples and conduct standard tests. - perform microbiological and ozone residual sampling in the workplace - Maintain and monitor relevant OHS requirements. - Collect and report process data according to organizational and disinfection system requirements. |
| - Prepare and apply ozone dosing. | - Generate and dose ozone according to ozone generating system specifications and disinfection objective. - Perform work-related ozone calculations - Maintain information related to ozone generation and dosing according to organizational requirements. |
| - Complete - Documentation | - Compile reports from plant and system data. - Report observations outside defined parameters for further action. |

Knowledge of Understanding

- identify and respond to operational problems

- produce reports and logs

- use safety and personal protective equipment

- follow plans, charts and instructions

- risk factors and potential hazards associated with ozonation

- ozone dosing processes

- properties and chemistry of ozone

- pH

- microbiological water quality guidelines

- ozone system layout

- lock-out procedures for mechanical and electrical installations

- operation, capacity and limitations of ozone generation equipment

- effects of weather and conditions on operation of site or plant

- pumping and valving systems

- automatic feed rate control systems

Tools & Equipment

  - electronic monitoring and metering systems

  - basic hand and power tools

  - sampling and laboratory testing equipment

  - personal protective equipment

  - ozone-generation system

  - pH meter

### Monitor the Performance of Water Treatment Plant

Overview: This competency standard covers the skill and knowledge required to identify characteristics of water quality, reasons of water quality treatment, monitoring and reporting water quality, safety requirements in a water treatment plant.

| Competency Units | Performance Criteria |
| --- | --- |
| - Identify characteristics of water quality and reasons for treatment of potable water. | - Identify characteristics of water affecting its physical, chemical and microbiological acceptability. - Identify reasons and requirements for treatment of water. |
| - Monitor and report on water quality. | - Clearly identify water treatment processes and determine their application. - Identify requirement of water quality parameters in accordance with objective and check characteristics of water quality according to relevant legislation and organizational procedures. - Record and report water quality to evaluate compliance to drinking water standards and objectives of the organization. |
| - Follow safety requirements for work in a water treatment plant. | - Identify and record hazards of working in a water treatment plant. - Identify and record operational requirements for safe and effective use of equipment. - Select, fit and use safety equipment, including personal protective equipment. |
| - Monitor and report on water treatment. | - Identify operating principles used in water treatment processes. - Complete records required for effective operation of a water treatment plant. - Identify, record and report range of data routinely collected. - Identify data that falls outside normal operating range and report for further action. |

Knowledge of Understanding

Required skills:

- apply policies, procedures and standards

- recognise and report operational problems

- use safety equipment and personal protective equipment

- select, collect and test samples

- interpret material safety data sheets (MSDS)

- receive and apply instructions

- use literacy skills in regard to verbal and written communication in the workplace

- communicate with other employees and people that interact within the work environment

- operating principles of water treatment processes

- basic water chemistry

- water uses and demands, both domestic and industrial

- physical, chemical and microbiological characteristics of water within the water treatment process

- water quality guidelines

- reasons for water treatment

- types of treatment plants and processes

- major chemicals and equipment used

- physical and chemical hazards

- reasons for data and information collection

### Maintain Record of Water Treatment Plants Assets

Overview: this competency standard covers the skill and knowledge required to maintain stock registers, assets record, maintenance and troubleshooting log record of flow measurement and gauging.

| Competency Units | Performance Criteria |
| --- | --- |
| - Maintain Stock Registers | - Develop assets registers - Develop the tool register - Develop Chemicals record register |
| - Maintain assets maintenance History | - Develop inspection and maintenance schedule of plant - Record the blockage, leakage and fault and its solution. |
| - Maintain the record of flow measurement and gauging | - Maintain the record of flow measurement - Maintain record of calibration gauges, meters and valves. |

Knowledge of Understanding

  - Record keeping

  - Report writing

  - Lock out/ tag out

## Waste Water Assessment and Treatment

### Demonstrate Sewage Treatment Plant

Overview: This competency standard covers the skill and knowledge required to operate Sewage treatment system, maintain items or equipment used in wastewater treatment processes, follow safety requirements for work in a wastewater treatment plant and record wastewater treatment plant data.

| Competency Units | Performance Criteria |
| --- | --- |
| - Plan and prepare work to operate Pump station | - Determine pump station work requirements - Enlist equipment to meet safety requirements of task |
| - Maintain and monitor pump station performance | - Identify the routine security inspections and cleaning duties to operate pump station - Demonstrate pump station components and identify the maintenance tasks. - Enlist pump station faults and carry out minor repairs. - Enumerate the pump station required adjustments, where necessary, to maintain operational parameters. |
| - Operation of Sewage treatment plant | - Identify major components and processes of sewage treatment system. - Understand the chemistry and microbiology of treatment process - Demonstrate the role of screeners, grit chambers, and skimming tanks, employed in preliminary screening. - Categorize the primary treatment of wastewater into three important stages. - Identify the purpose of coagulants and flocculants during primary treatment of wastewater. - Ensure to focus on the purpose of primary treatment. - Specify the role of aerobic and anaerobic bacteria in secondary time. - Define the working principle of activated sludge process - Identify the role of trickling filters and factors affecting the performance of trickling factor - Define the role of bacteria in secondary treatment - Sketch a flow diagram of primary treatment of wastewater. |
| - Maintain items of equipment used in Treatment plant | - Enlist maintenance requirements of different parts of equipment used in treatment process - Enumerate maintenance and cleaning requirements of equipment. - Analyze and interpret monitoring and test results and report according to regulatory requirements |
| - Identify the health and safety risks | - Identify the hazards of working in a wastewater treatment plant. - Identify the operational requirements for safe and effective use of equipment. - Use safety equipment, including personal protection - Identify and apply safe work practices when handling chemicals and working in a wastewater treatment plant. |
| - Estimate the treatment Efficiency by testing the influent and effluents | - Perform collection of influents before pre-treatment and effluents to analyze for wastewater parameters (pH, DO, BOD, COD, TSS, Nitrate and Phosphates etc.) to check the efficiency of treatment plant. - Compare the results with permissible limits defined by National Environmental Quality Standards (NEQS, 1999). - Develop an understanding of repair and maintenance of parts of treatment plant. |
| - Maintain items of equipment used in wastewater treatment process | - Identify maintenance and cleaning requirements as per organizational requirements. - Enlist the desludging, maintenance, operation, emergency services and equipment refurbishment for all types of treatment plant and pumping equipment, |

Knowledge and understanding

  - Process involved in sewage treatment

  - physical, chemical and microbiological characteristics and basic principles related to wastewater treatment

  - Types of screening for coarse, medium and suspended particles

  - Stages involved in primary treatment, secondary treatment

  - Role of microbes in waste degradation

  - wastewater treatment plant hazards

  - safety equipment

  - recognize and report operational problems

  - apply policies, procedures and standards

  - use safety equipment and personal protective equipment

### Demonstration of wastewater treatment process in constructed wetland

Overview: This competency standard covers the skill and knowledge required to understand the Waste Water Fundamentals, process and operation of waste water treatment systems, evaluation of local waste water treatment system, design and installation of prototype system.

| Competency units | Performance Criteria |
| --- | --- |
| - Understand the design and operation of the constructed wetlands | - Sketch the design of constructed wetlands - Define the role of plants in pollutant removal. - Demonstrate the process of screening and sedimentation - Explain the process of filtration and aeration used in the constructed wetlands. - Demonstrate on the laboratory model of the constructed wetlands |
| - Operate and Process control of DAF in wastewater Treatment | - Define Dissolved Air Floatation process, a separation process to remove tiny suspended solids that density close to the water, colloid, oil and grease etc. - Enlist the stages involved in DAF process - Define the working principle of Air flotation separation technology. - Identify the parts of dissolved air flotation equipment (Flocculation chamber, flotation tank, dissolved air system, reflux pipe, dissolved air released system, skimmer) - Name the chemical added to enhance the flocculation before floating - Enlist the application of treated wastewater by identifying the process in below diagram - Understand equipment maintenance and safety precautions. |
| - Conventional wastewater treatment process | - Identify major components and processes of wastewater treatment system. - Understand the chemistry and microbiology of treatment process - Identify the chemical processes involved during treatment - Define the role of chemicals applied - Enlist maintenance requirements of parts of treatment system - Identify safe work practices when handling chemicals and working in a wastewater treatment plant |
| - Estimate the treatment Efficiency by testing the influent and effluents | - Perform collection of influents before pre-treatment and effluents to test for wastewater parameters (pH, DO, BOD, COD, TSS, Nitrate and Phosphates etc.) to check the efficiency of treatment plant. - Compare the results with permissible limits defined by NEQS, standards and report the test results. |
| - Maintain items of equipment used in wastewater treatment processes. | - Identify maintenance and cleaning requirements as per standards - Understands the health and safety risks and adopt good practices during dealing with sewage. - Enlist the disposal of removed sludge |

Knowledge and Understanding

- aerobic and anaerobic treatments and critical design parameters for communal treatment systems

- Bioremediation process

- Role of vegetation in nutrient removal

- features and components of dissolved air flotation systems, including:

valves, recycle pumps, compressor, saturator

- float removal mechanism, dispersion valves

- air loading, recycle flow rates, saturated pressure, detention time, float removal frequency, Intended plant configuration

- types of dissolved air flotation processes, including:

- dissolved air flotation, dissolved air flotation filtration (DAFF) dissolved air flotation sludge thickening

- chemicals used for coagulation and flocculation or thickening

- theory of process operations, including: dissolved air flotation/clarification, filtration, Sludge thickening

Tools & Equipment

  - Waste water sampling bottles

  - Insulated samples boxes

  - Waste water testing laboratory equipment

  - Sewage treatment plant site

  - Wetlands

### Determine Flow Discharge Measurement of Wastewater

Overview: After completion of this competency standard the trainee will be able to collect the quality field data for water flow and discharge measurement of open channel drains, critical for predicting the water availability and load of the channels. Trainee will be able to demonstrate the flow discharge measurement of drains, streams, brooks and open channels.

| Competency Units | Performance Criteria |
| --- | --- |
| - Ideal site for most accurate surface water discharge measurement. | - Identify the criteria for site selection as, reasonably straight for the greater of either 300 feet or 5 to 10 times the channel’s width both upstream and downstream from the gage site Free from rocks, weeds, and other obstructions with Flow is parallel to the bank, avoiding cross flow or reverse flow. - Identify source and type of waste water - Perform physical test and assess EC, pH and DO etc. - Fill out the preforma for site visit to note the background information. |
| - Measure cross section area of open channel | - Divide the cross section of open channel or wastewater drain into smaller 20 0r 30 sub-sections to adequately characterize their shape. - Measure the area of each sub-section by directly measuring its width and depth. - Measure the depths by marks on a wading rod of current meter and stream width, by using a measuring tape stretched across the stream. |
| - Measure Velocity of each subsection | - Estimate the velocity of each subsection by use of appropriate method and instrument. For wading measurements, use Mechanical current meters and Acoustic Doppler meters (ADVs velocimeters). - Identify the manual method in case of unavailability of velocity meter. |
| - Adopt the float method to measure velocity. | - Adopt procedure for length measurement and select a neutrally-buoyant object (a ball or an orange) for place or toss the object into the stream, allowing it to reach full velocity before it passes the upstream end of the sub reach. - Record the time with a stopwatch taken by an orange (or some other object) to float from the upstream to the downstream transect. - Perform the float test at least three times, and calculate the average of the object’s velocity. - Calculate the object’s velocity, depending on its weight and immersion and multiply by about 0.85 to obtain the average stream velocity. - Multiply the average stream velocity by the average cross-sectional area of streamflow in the subreach used for the float test, giving an estimate of stream discharge ± 25% - Identify the correction factor based on stream type.For rocky and bottom stream it is 0.8 and for sandy /muddy bottom stream 0.9. - Apply a float test for each partial section of the total stream width, obtaining volumetric discharges for each partial section that can be averaged, giving an estimate. |
| - Calculate discharge of each subsection | - Calculate Discharge of each subsection by multiplying subsection area (Ai) by average velocity in the subsection. - Qi = Vi x Ai where; qi; is the stream discharge of the subsection i,. vi; is the average stream velocity in the subsection i,. Ai; is the subsection cross-sectional area... |
| - Computation of the total discharge for the total cross section | - Identify the equation to calculate flow at each partial section (Qi, cfs or ft3/sec) by multiplying the calculated area Ai (Wi, ft and depthDi, ft) with velocity (Vi, ft/s) measured at the midpoint, or Qi = Wi × Di × Vi. - Calculate total discharge. - Total discharge is the sum of discharges in all subsection - Qi = q1+q2+q3………qi - Develop an understanding to calculate the total flow by adding flow for each partial section, Qw = [(A1 × V1) + (A2 × V2) + ...... + (An × Vn)], for n sections. - Depending on the final value of total flow, round it to a reporting value. |
| - Adopt Alternate measurement method with Weirs and flumes | - Identify the needed equipment to measure the amount of time taken to fill a container of known volume. - Identify to use the stage method, install a weir plate across the stream flow such that none of the water flows around the weir but all water flows through the weir opening. - Adopt method to measure the height of water as it passes over the notch in the weir opening and calibrate this height to a pressure transducer. - Identify conversion of the depth measurements to flow volumes based on the geometry of the weir opening (45º, 60 º, and 90º v-notches are common),. - Adopt the procedure for Parshall flume installation by finding a straight area of the stream to ensure all flow in the stream should be going through the flume. - Perform calculations by Determining discharge of the stream within the flume and take water flow data seasonally. |
| - Quality Assurance of the measurement procedure | - Perform equipment maintenance in clean and working condition, per manufacturer instruction - Ensure that During the measurement of stream discharge, no more than 10% of the flow is contained within any one partial section. The more partial section readings that can be made, the more accurate the calculated stream discharge will be. |
| - Adopt proper safety precautions | - Ensure familiarization with sampling protocols and calibrated to sampling standards. - Adopt all safety precautions. - Identify the health and safety risked during the experiment. |
| - Analyze the data | - Take Discharge flow data periodically - Record data in specified performs and Generate graphs/figures and share the recorded data with authorities & stakeholders |

Knowledge of Understanding

- Awareness about  most appropriate site selection to gather the accurate and reliable data

- Capable of dividing the stream into subsections according to length.

- Able to height and width of the subsections of stream to calculate cross sectional area

- Adoption of method for velocity measurement of the flow

- Knowledge about measurement of discharge flow of the subsection and recording of total discharge of stream

- Adoption of quality control along with safety precautions

- Able to take periodic data of discharge flow and analyze it.

- use Health Safety Personal Protection Equipment during sampling.

Tools &Equipment’s

- Measuring tape

- Wading rod

- Stopwatch

- Buoyant object

- Manual / handheld Wastewater sampler

- Automatic sampler

- Flow measuring devices

- Flow measuring devices

- Concerned departments reports and previous data

- Consult available manuals for performing tests as SoP

- Portable testing equipment for onsite tests turbidity meter, pH, EC meter etc.

- Demonstrate through models, Multimedia or in field (on site) by visits to domestic wastewater streams, treatment plants & industrial areas

- Concerned departments reports and previous data

- Consult available manuals for performing tests as SoP

### Perform Testing of Dissolved Oxygen in waste water

Overview: This competency standards covers the skill and knowledge required to Prepare samples  for testing, Prepare for laboratory testing, Perform tests on samples, Quality Control Checks, Record the results/ Finalise work, Adopt the precautions during testing work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of analysis of DO. - keeps the sample at room temperature for few minutes. - Identify appropriate test method, Glassware, Equipment and safety requirements. |
| - Prepare for laboratory testing | - Set up test equipment DO Meter and/or reagents in accordance with the specified work instructions. - Conduct pre-use and safety checks. - Check the calibration status of equipment. Perform calibration if required. |
| - Perform tests on samples | - Wash the electrode of DO meter with deionized water before analysis. - Switched on the instrument and run an internal self-check until normal operating mode is activated. - The DO electrode is then dipped in reagent bottle in such a way in order to avoid entrance of air. - The sample is allowed to stir by means of magnetic stirring system to assure certain agitation of the sample. - The DO of the sample is noted when the reading on the screen of DO meter become stable. - analyzed Three replicate for each sample. - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and store equipment. |
| - Quality Control Checks | - Method blank is analyzed after every 10 samples - check repeatability by reanalysing a pre-analyzed sample once a day - Daily quality control data is recorded in QC Data sheet-I. - Results of laboratory control sample are regularly displayed in the form of control charts. |
| - Record the results/ Finalise work | - Note down the Results on analyst workbook. - Calculate uncertainty of theresults - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt the precautions during testing work | - Follow manufacturer’s calibration procedure exactly to obtain guaranteed precision and accuracy. - Care should be taken in changing membrane to avoid contamination of sensing elements. - Stopper the bottles with care to avoid entrapping air bubbles - Samples should be analyzed within 24 hours after collection. - P5: Use of magnetic stirrer is recommended to ensure a certain agitation of the fluid. This will reduce the errors due to the presence of air bubbles on the membrane surface. |

Knowledge and Understanding

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

- Understanding the basic principle of DO Meter for Dissolved Oxygen measurement i.e. determination of dissolved oxygen concentration through membrane covering the prob. The thin permeable membrane isolates the sensor elements from the testing solution, but allows oxygen to enter, oxygen that passes through membrane causes a current to flow from which the oxygen concentration is determined.

- Identifying the DO conc. in accordance to the requirement and hazards in water samples

- Planning and organizing testing assignment

- Using appropriate testing equipment and personal protective clothing and equipment

- Understanding and applying procedures for testing

- Determining and reporting accurate and relevant results from testing

Tools & Equipment

- DO Meter

- Zero Solution of Sodium Sulphite (Na2SO3) for Calibration

- Deionized water

- Glass Beakers (Class A)

### Perform Testing of Chemical Oxygen Demand (COD) by Colorimeter/Dichromate Digestion Method

Overview: This competency standards covers the skill and knowledge required toPrepare samples  for testing, Prepare for laboratory testing, Perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt the precautions during testing work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of analysis of COD. - keeps the sample at room temperature for few minutes. - Identify appropriate test method, Glassware, Equipment and safety requirements. |
| - Prepare for laboratory testing | - Set up test equipment COD Digester & Colorimeter and/or reagents in accordance with the specified work instructions. - Conduct pre-use and safety checks. - Check the calibration status of equipment. Perform calibration if required. |
| - Perform tests on samples | - Before analysis 500 ml of sample is homogenized for 30 seconds in a blender OR by magnetic stirring. - Turn ON the COD reactor and the temperature is adjusted at 150oC. - Place the plastic safety shield in front of the reactor. - The ranges for COD in then selected according to location of the sample (river, nullah, tanneries, sewage etc.). - 6-150 mg/l - Low - 6-1500 mg/l - High - 6-15000 mg/l - High Plus - The sample is added to vial by keeping it at the angle of 45 degree. The sample is not introduced directly rather by keeping pipette with the walls of the vials. - Sample volume for different ranges is as follows Volume of the sample; Ranges for COD. 2.0mL; 6-150. 2.0mL; 6-1500. 0.2mL; 6-15000. - Select one tube from each reagent box of every reagent range is selected as REFERENCE and deionized water is taken as sample and this reference is fixed until box is emptied. - put the tubes in block digester when temperature is stable. - After 2 hours, turn off reactor; wait for 120 minutes .The vials are allowed to cool to 12oC or less. - Each vial is inverted several times and placed in a rack until it comes to room temperature and measure COD is measured by selecting saved program on colorimeter. - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and store equipment. |
| - Quality Control Checks | - Analyze Method blank after every 10 samples - check repeatability by reanalysing a pre-analyzed sample once a day - Record the daily quality control data in QC Data sheet-I. - Results of laboratory control sample are regularly displayed in the form of control charts. |
| - Record the results/ Finalize work | - Note down the Results on analyst workbook. - Calculate uncertainty of the results - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt the precautions during testing work | - Collect samples in glass bottles. Use plastic bottles only if the sample is known to be free of organic contamination. - Analyze sample within 24 hours after sampling if it is delayed then preserve samples by acidification to pH<2 using conc.H2SO4. - Shake the sample for at least 30 seconds for homogenization. - Wear appropriate eye protection and clothing for protection. - The reagent mixture is light sensitive. Keep unused vials in opaque container. |

Knowledge and Understanding

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

- Understanding the basic principle of COD measurement i.e. determination of COD concentration through refluxed in strongly acid solution with a known excess of potassium dichromate (K2Cr2O7) in selected glass ampoules or capped culture tube. Oxygen consumed is measured against standards at with colorimeter.

- Identifying the COD conc. in accordance to the requirement and hazards in water samples

- Planning and organizing testing assignment

- Using appropriate testing equipment and personal protective clothing and equipment

- Understanding and applying procedures for testing

- Determining and reporting accurate and relevant results from testing

Tools & Equipment

- COD Digester

- Colorimeter

- Digestion solutions of the following range

0-150 ppm (Commercially available)

0-1500ppm (Commercially available)

0-15000ppm (Commercially available)

- Deionized water

- Glass Beakers (Class A)

### Perform Testing of Biochemical Oxygen Demand (BOD) by Monometric Pressure Measurement Method

Overview: This competency standards covers the skill and knowledge required toPrepare samples  for testing, Prepare for laboratory testing, Perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt the precautions during testing work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of analysis of BOD. - keeps the sample at room temperature for few minutes. - The optimum pH value for BOD measurement is between 6.5 and 7.5.The high or lower pH value can be readjusted by adding (1M) HCl or NaOH. - homogenized the sample or filtered before analysis. - Use Ally Thio Urea ATH as nitrification inhibitor if required. (When checking discharges from effluent treatment plant. - Clean BOD bottles and stirring rods with teepol (detergent) and rinsed with hot water and finally rinsed with deionized water. - Identify appropriate test method, Glassware, Equipment and safety requirements. |
| - Prepare for laboratory testing | - Set up test equipment BOD Incubator and/or reagents in accordance with the specified work instructions. - Conduct pre-use and safety checks. - Check the calibration status of equipment. Perform calibration if required. |
| - Perform tests on samples | - Set the Temperature of the thermostat cabinet at 20oC. - Carry out the Pre-treatment of the sample if required (e.g. Setting of pH, Filtering). - Select themeasurement range for the sample under test and take the volume as per standard. Generally following volume and ranges are used Range BOD mg/L; Sample volume in mL; Drops ATH; Drops KOH. 5-40; 428; 10; 3. 5-80; 360; 10; 3. 5-200; 244; 5; 3. 5-400; 157; 5; 3. 5-800; 94; 3; 3. 5-2000; 56; 3; 3. 5-4000; 21.7; 1; 3. - measure the volume of the sample precisely by using the overflow measurement flask and transferred to BOD bottle. If necessary, add nitrification inhibitor. - add Seeding in order to provide microbial growth if required. - Insert cleaned magnetic stirring rods in the BOD bottle. - Place drops of KOH solution into the seal gasket as per standard. Then insert the gasket in the rack of the bottle. - Screw the BOD sensors are tightly to sample bottles and properly place sample bottles are in the bottle rack. - Select the required range by from instrument program - To check accuracy of the measuring unit incubate the CRM by same upper Mentioned procedure. - The incubation time of unit is for 5 days - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and store equipment. |
| - Quality Control Checks | - CRMs are analyzed in order to check the calibration of the measuring system with every badge of samples. - Check the quality of dilution water by incubation. The DO uptake in 5 days at 20oC should not be more than (0.2 mg/l) preferably not more than 0.1/lit). - Measure the BOD of the seeding material and dilution water to check the quality of seed and dilution water. - display the results of laboratory control sample regularly in the form of control charts. |
| - Record the results/ Finalise work | - Note down the Results on analyst workbook. - Calculate uncertainty of theresults - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt the precautions during testing work | - The sample must never come in contact with the potassium Hydroxide solution. - Never use grease or any other lubricant as an additional sealing agent, for the BOD sensors or for the seal gasket. - BOD sensors must be tightening carefully otherwise it will not detect the generated pressure. - Before measurement begins, the prepared sample must be brought to desired temperature (20oC). - Once the measurement has started never disturb the position of bottles otherwise you will lose the stored data. |

Knowledge and Understanding

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

- Understanding the basic principle of BOD measurement i.e. determination of BOD concentration through the consumption of dissolved oxygen in the sample. This is replaced by oxygen out of the air within the bottle, above the sample. The carbon dioxide released at the same time is chemically bonded by the potassium hydroxide in the seal gasket. This generates a decrease in pressure which is measured by BOD sensor and displayed as BOD value.

- Identifying the BOD conc. in accordance to the requirement and hazards in water samples

- Planning and organizing testing assignment

- Using appropriate testing equipment and personal protective clothing and equipment

- Understanding and applying procedures for testing

- Determining and reporting accurate and relevant results from testing

Tools & Equipment

- BOD Incubator

- 45% KOH

- Allyl Thio Urea (ATH)

- 1N HCl

- 1N NaOH

- BOD Seeds

- Seeding Solution

- Deionized water

- Glass Beakers (Class A)

### Perform Testing/Determination of Oil and Grease in Wastewater

Overview: This competency standard covers the skill and knowledge required to Prepare samples for testing, prepare for laboratory testing, perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt the precautions during testing work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Identify appropriate test method, Glassware, Equipment and safety requirements. - Check the sample label for the requirement of analysis of Oil and Grease. - Collect the sample in 1L glass bottle with Teflon lined inner lid. - keeps the sample at room temperature for few minutes. - Maintain the pH to <=2 by adding Hydrochloric acid - Shake the glass sample bottle to assure good mixing of sample. - Prepare Zero liquid, span liquid and OCB Standard for Calibration - Pure Solvent S-315 is used as zero solvent. |
| - Prepare for laboratory testing | - Set up test equipment OCMA-350 and reagents in accordance with the specified work instructions. - Perform calibration, zero, span and measurement of zero solvent in terms of mg/L. - Select mg/L on OCMA-350 for oil in water analysis. |
| - Perform tests on samples | - Accurately pipette 10ml sample in a 40ml vial. The sample volume may be varied and a dilution factor applied to the results to measure a broad range from lower or higher concentration samples. - Accurately pipette 10ml of the solvent S-316 (Infrared Spectroscopy Grade) into the 40ml vial. The sample volume may be varied and a dilution factor applied to the results to measure a broad range from lower or higher concentration samples. - Cap the vial and shake it vigorously to extract oil in water in solvent. - Place the vial in an upright position and allow the air bubbles to come out of the solvent.; normally 30 sec. - There should be an abrupt break between the solvent on bottom and water on the top. There shouldn’t be any emulsion layer. - In case of emulsion treat the extract to break it. Carefully pipette the as much solvent/extract as possible without taking the water layer in a beaker. - Add 1 or more grams of anhydrous Sodium Sulfate, Na2SO4, to break the emulsion by stirring it with glass rod. The extract should appear as non-turbid but may be colored - Put a conditioned 11cm No. 40 whatman filter paper into a glass funnel and filter the extract to remove the Na2SO4 - If less than 6ml of solvent/extract are recovered, add a measured amount of solvent, and account for dilution in the results. - After pipetting 6ml of solvent/extract fill and place the OCMA-350 cell into equipment for measurement. - Read the concentration or press measure to start the stability check. This reading obtained in terms of Total Recoverable Oil and Grease. - For measurement of Total Petroleum Hydrocarbon (TPH). Treat the extract with conditioned Silica Gel, filtered with No. 40 Whatman filter paper and premeasure. - The difference, Oil and Grease minus Total Petroleum Hydrocarbon, is the non-petroleum Hydrocarbon. - Remove the cell from OCMA-350 and empty for next measurement. |
| - Quality Control Checks | - The zero and span calibration before the measurement is necessary when the measuring background has any changes of replacing the measuring cell, change of Lot No. of Solvent etc. |
| - Record the results/ Finalise work | - Note down the Results on analyst workbook. - Calculate uncertainty of the results - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt the precautions during testing work | - Discharge the solvent in the cell, Clean it and store it carefully. - Close the Cover on the unit to avoid dust. - When filling the cell, make sure there are no bubbles in the cell. - Do not touch the ends of a cell. - Do not spill the solvent on the measuring unit during cell insertion. - For accurate measuring results, calibration and measurement should be started after the “warmup” lamp off. - Solvent can be absorbed through the skin, wear gloves when handling it. - Avoid inhaling of vapors or ingest liquid. |

Knowledge and Understanding

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

- Understanding the basic principle of Oil and Grease measurement i.e. Determination of Oil and grease by Solvent extraction with an organic solvent and Infrared spectroscopic analysis on OCMA-350. The oil after mixing with organic solvent gets absorbed in organic solvent and settle at bottoms and water layer at top. After careful extraction of the solvent, it is subjected to measure Recoverable oil in mg/L. The Infrared absorption measurement principle reflects the chemical structure of the molecule and a characteristic absorption pattern is shown by chemical structure of the substance. Therefore, the absorption of various wavelengths is measured, and position and strength of the absorption bands enable us to make a qualitative and quantitative analysis.

- Identifying the oil and grease conc. in accordance to the requirement Total Petroleum Hydrocarbons

- Planning and organizing testing assignment

- Using appropriate testing equipment and personal protective clothing and equipment

- Understanding and applying procedures for testing

- Determining and reporting accurate and relevant results from testing

Tools & Equipment

- OCMA-350

- Cell with Cap

- Microsyringe (25µl)

- Syringe (10ml)

- B- Heavy Oil (specific gravity 0.895)

- Volumetric Flask (250 ml)

- Glass sampling bottle with Teflon inner lid

### Perform Testing/Determination of Total Suspended Soilds

Overview: This competency standard covers the skill and knowledge required to Prepare samples for testing, Prepare for laboratory testing, Perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt the precautions during testing work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of analysis of TSS. - Identify appropriate test method, Glassware equipment and safety requirements. - Keeps the sample at room temperature for few minutes. - Stir sample with a magnetic stirrer at a speed to shear larger particles, to obtain a more uniform (preferably homogeneous) particle size. |
| - Prepare for laboratory testing | - Set up the apparatus and/or reagents in accordance with the specified work instructions. - Conduct pre-use and safety checks. - Sample volume is taken to yield between 2.5 and 200 mg dried residue. - If volume filtered fails to meet minimum yield, increase sample volume to 1L. - Place filter disks onto the filtration apparatus. Apply vacuum and rinse each with three successive 20-mL volumes of deionized water. - Draw air through the filters until it appears that all water has been drawn off. Store filters in a desiccator until use. |
| - Perform tests on samples | - Assemble filtering apparatus and filter and begin suction, - Wet filter with a small volume of reagent-grade water to seat it. - After homogenizing the sample with vigorous shaking or blending - Pipet from the approximate midpoint of container but not in vortex. - Wash filter with three successive 10-mL volumes of reagent-grade water, allowing complete drainage between washings, and continue suction for about 3 min after filtration is complete. - Samples with high dissolved solids may require additional washings. - Carefully remove filter from filtration apparatus and transfer to an aluminum weighing dish as a support. Alternatively, remove the crucible and filter combination from the crucible adapter if a Gooch crucible is used. - Dry for at least 1 h at 103 to 105°C in an oven, cool in a desiccator to balance temperature, and weigh. - Repeat the cycle of drying, cooling, desiccating, and weighing until a constant weight is obtained or until the weight change is less than 4% of the previous weight or 0.5 mg, whichever is less. - Analyze at least 10% of all samples in duplicate. Duplicate determinations should agree within 5% of their average weight. - Perform calculation to determine TSS mg total suspended solids/L = (A - B) X 1000 sample volume, mL |
| - Quality Control Checks | - Analyze one method blank with every batch. - Analyze ≥5% of all samples in duplicate or at least one duplicate sample with each batch of ≤20 samples |
| - Record the results/ Finalise work | - Note down the Results on analyst workbook. - Calculate uncertainty of the results - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt the precautions during testing work | - Use resistant-glass or plastic bottles, provided that the material in suspension does not adhere to container walls. - Refrigerate sample at 4°C up to the time of analysis to minimize microbiological decomposition of solids. - Limit the sample size to yield no more than 200mg residue. - For samples high in dissolved solids thoroughly wash the filter to ensure removal of dissolved material. - Filter paper after drying must be stored in desiccator in order to avoid moisture absorbance - Verify the Calibration of weighing balance to avoid fluctuation of measurement - Sampling and sub sampling may introduce serious error, so in order to avoid it make sample homogenous during transfer - Take the suspended sample with wide bore pipette.in case of graduated cylinder. |

Knowledge and Understanding

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

- Understanding the basic principle of TSS measurement i.e. A well mixed sample is filtered through a weighed standard glass fibre filter and the residue retained on the filter is dried to a constant weight at 103oC to 105oC.The increase in the weight of the filter represents the Total Suspended Solids. If the suspended material clogs the filter and prolongs filtration, it may be necessary to increase the diameter of the filter or decrease the sample volume. To obtain an estimate of total suspended solids, calculate the difference between Total Suspended solids and Total Solids.

- Identifying the TSS conc. in accordance to the requirement and hazards in water samples

- Planning and organizing testing assignment

- Using appropriate appartus and personal protective clothing and equipment

- Understanding and applying procedures for testing

- Determining and reporting accurate and relevant results from testing

Tools & Equipment

- Analytical Balance

- Drying Oven

- Filtration assembly

- Desiccator

## Entrepreneur

### Develop entrepreneurial skills

Overview: This Competency Standard identifies the competencies required to develop entrepreneurial skills by Hotel manager, in accordance with the organization’s approved guidelines and procedures. You will be expected to develop a business plan, collect information regarding revenue generation, develop a marketing plan and develop basic business communication skills. Your underpinning knowledge regarding entrepreneurial skills will be sufficient to provide you the basis for your work.

| Competency Unit | Performance Criteria |
| --- | --- |
| 1. Develop a business plan | P1. Conduct a market survey to collect following information - Business Model - Financials - Equipment Estimation - Revenue Generation Sources - Marketing strategy - Market Trends - Overall Expenses P2. Select the best option in terms of cost, service, quality, sales, operational expenses P3. Compile the information collected through the market survey, in the business plan format |
| 2. Develop a marketing plan | P1. Make a marketing plan for the service products, price, placement, promotion, people, packaging and positioning P2. Include the information of marketing plan in the business plan |
| 3. Develop basic business communication skills | P1. Communicate with guests using effective communication skills P2. Use different modes of communication to communicate effectively e.g.: presentation, speaking, writing, listening, visual representation, reading etc. P3. Use specific business terms used in the market |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes:

- 7Ps of marketing including product, price, placement, promotion, people, packaging and positioning

- 7Cs of business communication

- Different modes of communication and their application in the industry

- Specific business terms used in the industry

- Available funding sources

- Low interest loans to start a new business

- Market survey and its tools e.g. : questionnaire, interview, observation etc,.

- Market trends for specific product offering

- State the main elements of business plan

- Business plan format

Critical Evidence(s) Required

The candidate needs to produce following Critical Evidence(s) in order to be competent in this competency standard:

- List 7Ps of marketing

- List 7Cs of business communication

### Apply management and communication techniques

Overview: This unit describes the skills and knowledge required to provide a critical link between people, ideas and information at all stages in the project life cycle. It involves assisting the project team to plan communications, communicating information related to the project, and reviewing communications. It applies to individuals who are project practitioners working in a project support role.

| Competency Unit | Performance Criteria |
| --- | --- |
| - Contribute to communications planning | P1. Identify, source and contribute relevant information requirements to initial project documentation P2. Contribute to developing and implementing the project communications plan and communications networks |
| - Conduct information-management activities | P1. Act on and process project information according to agreed procedures as directed, to aid decision-making processes throughout project life cycle P2. Maintain information to ensure data is secure and auditable |
| - Communicate project information | P1. Communicate with clients and other stakeholders during project using agreed networks, processes and procedures to ensure flow of necessary information P2. Ensure reports are prepared and released according to authorization, or produced for release by others P3.Seek information and advice from appropriate project authorities as required |
| - Contribute to assessing effectiveness of communication | P1. Assist in ongoing review of project outcomes to determine effectiveness of communications-management activities P2. Report communications-management issues and responses to higher project authorities for application of lessons learned to future projects |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes:

    - Summarize models and methods of communications management in context of project life cycle and other project management functions

    - Importance of managing risk by treating information securely

    - Methods of reviewing outcomes

    - Organizational policies and procedures relevant to this role in a specific context.

Critical Evidence(s) Required

The candidate needs to produce following Critical Evidence(s) in order to be competent in this competency standard:

- Demonstrate managerial and communications plan for IoT product

- Elaborate decision-making processes throughout project life cycle

### Create human resource management plan

Overview: This unit describes the skills and knowledge required to assist with aspects of human resources management of a project. It involves establishing human resource requirements, identifying the learning and development needs of people working on the project, facilitating these needs being met, and resolving conflict in the team. It applies to individuals who are project practitioners working in a project support role.

| Competency Unit | Performance Criteria |
| --- | --- |
| Assist in determining human resource requirements | P1. Analyze work breakdown structure to determine human resource requirements P2. Prepare a skills analysis of project personnel against project task requirements P3. Assist in assigning responsibilities for achieving project deliverables |
| Contribute to establishing and maintaining productive team relationships | P1. Actively seek views and opinions of team members during task planning and implementation P2. Promote cooperation and effective activities, goals and relationships within team P3. Communicate with others using styles and methods appropriate to organizational standards, group expectations and desired outcomes P4. Communicate information and ideas to others in a logical, concise and understandable manner P5. Regularly seek feedback on nature and quality of work relationships, and use feedback as basis for own improvement and development |
| Assist with human resource monitoring | P1. Monitor work of project personnel against assigned roles and responsibilities within delegated authority levels P2. Monitor and control actual effort against project plan P3 Review skill levels against allocated tasks and recommend solutions, where required, to others P4. Advise others within delegated authority when assigned responsibilities are not met by project personnel P5. Undertake work in a multi-disciplinary environment according to established human resource management practices, plans, guidelines and procedures P6. Resolve conflict within delegated authority according to agreed dispute-resolution processes P7. Assist in offering human resource development opportunities to individuals with skill gaps |
| Contribute to evaluating human resource practices | P1. Contribute to assessing effectiveness of project human resources management P2. Document lessons learned to support continuous improvement processes |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes:

- Alternative project personnel engagement options

- Job design principles and work breakdown structures

- Learning and development approaches that can be incorporated into project life cycle

- Methods for skills analysis

- Project roles, responsibilities and reporting requirements for human resources.

Critical Evidence(s) Required

The candidate needs to produce following Critical Evidence(s) in order to be competent in this competency standard:

- Produce the assigned roles and responsibilities of your team within delegated authority levels

- Provide dispute-resolution procedures for an organizations

### Develop project management plan

Overview: This unit describes the skills and knowledge to develop a plan for a hotel management plan, including assessing project requirements and planning for all stages to completion and final documentation.

| Competency Unit | Performance Criteria |
| --- | --- |
| - Prepare project management plan | P1. Evaluate and assess project brief and related documents P2. Produce document on project tasks and associated timelines, including installation processes and test requirements P3. Assess and produce document on resource requirements to assist allocation of appropriate resources P4. Produce training plan assessing training needs and associated timelines for efficient project implementation P5. Determine and document budgetary requirements P6. Discuss roles of all identified parties associated with project to ensure their involvement P7. Produce project verification document, including monitoring and control processes, and review processes such as quality audits P8. Consult with all relevant parties prior to finalizing draft plan and make changes as appropriate |
| - Develop and evaluate management plan | P1. Produce preliminary plan for consultation, including identified factors that may impact on realization of project and observance of relevant legislation, codes, regulation and standards P2. Consult with client and clarify any amendments P3. Develop final plan with recommendations |
| - Communicate project information | P1. Produce and document final plan to include implementation details and training needs P2. Present plan to client and obtain sign off |
| - Contribute to assessing effectiveness of communication | P1. Assist in ongoing review of project outcomes to determine effectiveness of communications-management activities P2. Report communications-management issues and responses to higher project authorities for application of lessons learned to future projects |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes:

- Key attributes of common telecommunications applications and related equipment

- Evaluate the connections to carrier infrastructure or equipment

- Current legislation relating to the design of installation of telecommunications equipment and connection to carrier services

- Advantages of leasing and purchase options to assist in delivering cost effective solutions

- Evaluate network and transmission equipment

- Network topologies, and interface and interconnect solutions

- Workplace health and safety (WHS) issues that need to be built into a plan, with consideration of:

  - electrical safety

  - materials handling

  - physical hazards

  - confined spaces

  - heights

  - lifting

- Evaluate the power requirements and electrical safety aspects of the installation plan

- Performance parameters and typical faults that may be encountered in client equipment and related connection and transmission media

- Various test equipment types suitable for tests to be made

- Warranty information for equipment supplies and contractor work guarantees.

Critical Evidence(s) Required

The candidate needs to produce following Critical Evidence(s) in order to be competent in this competency standard:

- Produce training plan assessing training needs and associated timelines for efficient project implementation

- Determine and document budgetary requirements

- Produce project verification document, including monitoring and control processes, and review processes such as quality audits

- Produce and document final plan to include implementation details and training needs

- Present plan to client and obtain sign off

### Develop sales plan

Overview: This unit describes the skills and knowledge required to develop a sales plan for a product or service for a team covering a specified sales territory based on strategic objectives and in accordance with established performance targets. It applies to individuals working in a supervisory or managerial sales role who develop a sales plan for a product or service.

| Competency Unit | Performance Criteria |
| --- | --- |
| - Identify organizational strategic direction | P1. Obtain and analyze assessment of market needs and strategic planning documents P2. Review previous sales performance and successful approaches to identify factors affecting performance P3. Analyze information on market needs, new opportunities, customer profiles and requirements as a basis for decision making P4. Carry out competitor analysis for rate structure |
| - Establish performance targets | P1. Determine practical and achievable sales targets P2. Establish realistic timelines for achieving targets P3. Determine measures to allow for monitoring of performance P4 .Ensure objectives of the sales plan and style of the campaign are consistent with organizational strategic objectives and corporate image |
| - Develop a sales plan for a product | P1. Determine approaches to be used to meet sales objectives P2. Identify additional expertise requirements and allocate budgetary resources accordingly P3. Identify risks and develop risk controls P4. Develop advertising and promotional strategy for product P5. Identify appropriate distribution channels for product P6. Prepare a budget for the sales plan P7. Present documented sales plan to appropriate personnel for approval |
| - Identify support requirements | P1. Identify and acquire staff resources to implement sales plan P2. Develop an appropriate selling approach P3. Train staff in the selling approach selected P4. Develop and assess staff knowledge of product to be sold |
| - Monitor and review sales plan | P1. Monitor implementation of the sales plan P2. Record data measuring performance versus sales targets P3. Make adjustments to sales plan as required to ensure required results are obtained |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes:

- Outline principles and techniques for selling

- Outline methods for monitoring sales outcomes

- Statistical techniques for analyzing sales and market trends

- Internal and external sources of information that are relevant to identifying organizational strategic direction and developing a product sales plan.

- Competitors intelligence

Critical Evidence(s) Required

The candidate needs to produce following Critical Evidence(s) in order to be competent in this competency standard:

- Identify the risks of the product i.e., sale/deployments

- Produce a sales plan for the product

- Demonstrate marketing and selling approach

- Demonstrate advertising and promotional strategy for product

### Conduct research for customer needs and satisfaction

Overview: This unit describes the skills and knowledge required to manage an ongoing relationship with a customer over a period of time. This includes helping customers articulate their needs and managing networks to ensure customer needs are addressed. It applies to individuals who are expected to have detailed product knowledge in order to recommend customized solutions. In this role, individuals would be expected to apply organizational procedures and be aware of, and apply as appropriate, broader factors involving ethics, industry practice and relevant government policies and regulations.

| Competency Unit | Performance Criteria |
| --- | --- |
| 1. Assist customer to articulate needs | P1. Ensure customer needs are fully explored, understood and agreed P2. Explain and match available services and products to customer needs P3. Identify and communicate rights and responsibilities of customers to the customer as appropriate |
| 2. Satisfy complex customer needs | P1. Explain possibilities for meeting customer needs P2. Assist customers to evaluate service and/or product options to satisfy their needs P3. Determine and prioritize preferred actions P4. Identify potential areas of difficulty in customer service delivery and take appropriate actions in a positive manner |
| 3. Manage networks to ensure customer needs are addressed | P1. Establish effective regular communication with customers P2. Establish, maintain and expand relevant networks to ensure appropriate referral of customers to products and services from within and outside the organization P3. Ensure procedures are in place to ensure that decisions about targeting of customer services are based on up-to-date information about the customer and the products and services available P4. Ensure procedures are put in place to ensure that referrals are based on the matching of the assessment of customer needs and availability of products and services P5.Maintain records of customer interaction in accordance with organizational procedures |
| 4. Convert customer enquiries into sales | P1. Use information provided by customers or accessed from the customer relationship management (CRM) system to identify any needs P2. Identify suitable products/services to meet needs P3. Make convincing sales pitches to customers following standard scripts P4. Handle customer queries, objections and rebuttals following standard scripts P5. Adapt your approach and style to customer preferences, within the limits of your competence and authority P6. Refer issues outside your area of competence and authority to appropriate people, following your organization’s procedures P7. Identify and act on opportunities to up-sell or cross-sell other products/services to customers P8. Confirm customer wishes and needs in order to close sales P9. Obtain required financial information from customers, following your organization’s procedures P10.Complete your organization’s post-sales procedures in order to complete/ fulfill sales P11. Comply with relevant standards, policies, procedures and guidelines when converting customer enquiries into sales |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes:

- Organizational procedures and standards for establishing and maintaining customer service relationships

- Consumer rights and responsibilities

- Ways to establish effective regular communication with customers

  - Outline details of products or services including with reference to:

  - possible alternative products and services

  - Variations within a limited product and service range

Critical Evidence(s) Required

The candidate needs to produce following Critical Evidence(s) in order to be competent in this competency standard:

- Gather customer needs and requirements

- Analyse customer needs and requirements

- Enlist communication rights and responsibilities of customers

- Handle customer relationship management (CRM) model to identify suitable products/services to meet customer needs

### Manage finances

Overview: This unit of competency describes the outcomes required to develop, implement and monitor a personal budget in order to plan regular savings and manage debt effectively.

| Competency Unit | Performance Criteria |
| --- | --- |
| 1. Develop a personal budget | P1. Calculate current living expenses using available information to prepare a personal budget. P2. Keep a record of all income and expenses for a short period of time to help estimate ongoing expenses. P3. Subtract total expenses from total income to determine a surplus or deficit budget for the specified period. P4. Find reasons for a deficit budget and ways to reduce expenditure identified. P5. Identify ways to increase income, if possible |
| 2. Develop longer term personal budget | P1. Analyze income and expenditure and set longer term personal, work and financial goals. P2. Develop a longer-term budget based on the outcomes of short-term budgeting, and adjust to meet living, work and future career requirements. P3. Identify obstacles that might affect finances such as job loss, sickness or unexpected expenses contingency savings P4. Formulate a regular savings plan based on budget, using secure savings products and services. P5. Monitor expenditure against budget and identify areas of possible expenditure saving |
| 3. Identify ways to maximize future finances | P1. Determine sources and ways to maximize personal income, including from work, investments or available government payments/allowances. P2. Get further education or training to maintain or improve future income. P3. Identify the need for debt to finance living and other expenses, and determine the appropriate levels of debt and repayment. P4. Consolidate existing debt, where possible, to minimize interest costs and fees. P5.Seek professional money management services, where available, to ensure financial plans are effective and achievable |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes:

- Abilities to plan and organize to keep records and monitor a personal budget

- Abilities to set and review goals

- Basic financial management and record keeping to enable development and management of a personal budget

- Benefits of financial goal setting and personal budgeting to enable effective management of personal finances

- Numeracy skills to compare income and expenditure

Critical Evidence(s) Required

The candidate needs to produce following Critical Evidence(s) in order to be competent in this competency standard:

- Produce a longer-term budget based on the outcomes of short-term budgeting

- Develop and report the need for debt to finance living and other expenses,

- Determine the appropriate levels of debt and repayment

- Demonstrate the ways to increase finances and income

### Identify and resolve problems

Overview:

This unit is focus on negotiation in critical incidents and the development of strategic responses designed to resolve threatening incidents.

| Competency Unit | Performance Criteria |
| --- | --- |
| 1. Identify a problem | P1. Form a problem statement and analyze root cause. P2. Take initiative in tackling problems rather than relying solely on directives P3. Follow logic steps in understanding root cause and analyzing potential solutions. |
| 2. Determine strategies for a required solution | P1. Analyze all aspects of the incident for degree of hazard, priorities, optional outcomes and appropriate strategies P2. Analyze and determine strategies and priorities on the incident sought from a range of sources P3. Assess long term objectives against resources and priorities P4. Apply a range of communication techniques to make and maintain contact with the key people P5. Provide clear and factual information to enable an honest and realistic assessment of the interests of the key people and their positions P6. Resolve the conflict and express their likely consequences clearly and do an analysis of the benefits P7. Reassess points of disagreements for common positive Positions |
| 3. Coordinate support services | P1. Assess the need for support services in terms of the determined strategies and priorities P2. Negotiate the resources of support services according to established procedures and availability P3. Provide information on strategies to support services and maintain the communication P4 .Delegate roles and responsibilities according to expertise and resources |
| 4. Restore order | P1 Assess the incidents for degree of risk and take appropriate action to reduce and remove the impact of the incident and restore order P2 Take action designed to minimize risk and the preserve the safety and security of all involved P3 Take action to prevent the escalation of the incident appropriate to the circumstances and agreed procedures. P4 Carry out the use of force for the restoration of control and the maintenance of security in the least restrictive manner. P5 Complete reports accurately and clearly provided to the appropriate authority promptly P6 Review, evaluate and analyze the incident and the organizational response to it and report it promptly and accurately. |
| 5. Provide leadership. direction and guidance to the work group | P1. Link between the function of the group and the goals of the organization P2 .Participate in decision making routinely to develop, implement and review work of the group and to allocate responsibilities where appropriate P3 .Give opportunities and encouragement to others to develop new and innovative work practices and strategies P4. Identify conflict and resolve with minimum disruption to work group function P5.Provide staff with the support and supervision necessary to perform work safely and without risk to health P6 .Allocate tasks within the competence of staff and support with appropriate authority, autonomy and training P7 .Supervise appropriately the changing priorities and situations and takes into account the different needs of individuals and the requirements of the task |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes:

- Organization’s policies, guidelines and procedures related to control and surveillance, safety and preventing and responding to incidents and breaches of orders covered in the range of variables.

- Organization’s management and accountability systems

- Teamwork principles and strategies

- Principles of effective communication

- Guidelines for use of equipment and technology

- Code of conduct

Critical Evidence(s) Required

The candidate needs to produce following Critical Evidence(s) in order to be competent in this competency standard:

- Identify problem statement

- Build team

- Identify your target community for the proposed product/solution

- Analyze product sale and marketing plan

- Provide your strategy to execute entrepreneurial plan

- Provide three solutions (A, B, C) of your business plan

- Present complete portfolio of entrepreneurial plan as an evidence

- Provide clear and factual information to enable an honest and realistic assessment of the interests of the key people and their positions

- Provide information on strategies  to support after sale services

- Provide a complete entrepreneurial plan

## Hydraulics and Irrigation Engineering

### Determine Hydrostatic pressure

Overview: This competency standard covers the skills and knowledge required to find pressure by pressure gauges, Hydrostatic pressure and center of pressure of vertically immersed surface,

| Competency Units | Performance Criteria |
| --- | --- |
| - Find pressure by Piezometer | - Identify pressure gauge - Measure pressure by Piezometer |
| - Find pressure by manometer | - Identify pressure gauge - Measure pressure by Manometer |
| - Find out Hydrostatic pressure and center of pressure on vertically Immersed surface. | - Identify apparatus - Immerse apparatus in water tank - Identify the formulae for hydrostatic pressure and center of pressure. - Find the area of immersed surface - Find moment of inertia of the figure - Calculate hydrostatic pressure on surface - Find position of centre of pressure |
| - Find out discharge through a pipe with Pitot tube | - Identify the instrument - Fix the Pitot tube with pipe - Measure height of liquid in the tube - Find the velocity by using formula. - Find the discharge by using formula |
| - Find the Metacentric height of a floating body in Lab. | - Identify the apparatus. - Put apparatus in water tank. - Place jokey weight to make the ship symmetrical. - Place the ship in water and adjust the plumb to zero mark. - Move jokey weight across deck to a specified distance. - Measure the angle of inclination. - Calculate the metacentric height of ship by formula. |

Knowledge & understanding

- State development, scope and significance of Hydraulics in civil engineering.

- Define density, specific weight, specific volume, specific gravity, surface tension, viscosity compressibility, cohesion, and adhesion.

- State pressure, intensity of pressure, pressure head, Pascal's law and its simple applications.

- Distinguish among atmospheric pressure, gauge pressure and absolute pressure.

- Describe measurement of fluid pressure by Piezometer tube and different manometers.

- Define Hydrostatics

- State pressure on immersed surface.

- Define centre of pressure and resultant pressure.

- Calculate the total pressure and centre of pressure on a horizontal vertical and inclined surface immersed in a liquid (i.e. water)

- Define the terms, buoyancy, floatation, buoyant force and center of buoyancy

- Define metacentre and metacentric height.

- State the kinds of equilibrium of a floating body.

Critical Evidence(s) Required

The candidate needs to produce following critical evidences in order to competent in this competency standard.

- Observation and calculations of piezometer.

- Observation and calculations of piezometer.

- Observation and calculations of hydrostatic apparatus.

- Calculation sheet for pitot tube.

- Observations and calculation for finding metacentric height.

Tools and Equipment

- Piezometer.

- Manometer

- Hydrostatic apparatus.

- Water tank.

- Pilot tube.

- Metacentric height appara

### Apply Hydro kinematic Principles

Overview: This competency standard covers the skills and knowledge required to determine coefficient of discharge using venture meter, to calculate energy losses in pipe flow Determine hydraulic Co-efficient for circular orifices Calculate hydraulic and energy gradient for pipelines. Calculate flow in open channels. Calculate flows through notch Calculate flows through weirs.

| Competency Units | Performance Criteria |
| --- | --- |
| - Determine coefficient of discharge using venture meter. | - Check dimensions of venture meter and water tank. - Calculate at inlet and throat - Open inlet valve and take piezometer readings - Measure the head. - Calculate actual discharge. - Calculate theoretical discharge. - Calculate the coefficient of discharge using formulae. |
| - Calculate energy losses in pipe flow. | - Identify the apparatus. - Open valve and pass water through pipe. - Check piezo metric readings - Draw hydraulic grade line. |
| - Determine hydraulic Co-efficient for circular orifices | - Identify the orifice and adjust with the apparatus - Set constant head in the tank - Measure horizontal and vertical coordinates - Find actual discharge by using a container and stop watch - Use formulae to calculate coefficient of velocity and discharge |
| - Calculate hydraulic and energy gradient for pipe lines. | - Prepare pipeline design charts using standard formulae. - Identify the limitations of formulae. - Identify variations in roughness coefficients. - Calculate the pressure in pipeline systems using the hydraulic gradient line. - Calculate the pipe discharge from reservoirs. |
| - Calculate flow in open channels. | - Identify methods used for measuring flows in open channels. - Identify instruments to be used - Use formulae for calculating flows in open channels. - Find the velocity by current meter and velocity rod - Find discharge. |
| - Calculate flows through Vee and Trapezoidal Notch. | - Identify the methods used for measuring flows in notches. - Calculate area of notch. - Measure head of water over the notch. - Use the formulae for calculating flow in notches. |
| - Calculate flows through weirs | - Identify the methods used for measuring flows in notches. - Calculate area of weirs - Measure head of water over the weirs - Use the formulae for calculating flow in weirs |

Knowledge & Understanding

- Define hydro kinematics

- State discharge and equation of continuity of a liquid flow.

- Distinguish path lines and stream lines.

- Distinguish the type of flow in pipes i.e. steady and unsteady flow, uniform and non-uniform flow, turbulent flow.

- State the term hydrodynamics.

- State the energies of liquid in motion.

- State the total head of flowing liquid and total energy.

- Explain Bernoulli's theorem with its formula, limitations and practical application i.e., venture meter & pipit tube.

- Understand the Flow Through Pipes.

- State and explain difference between flow through pipes and open channel flow

- Distinguish types of flow in pipes i.e. steady and unsteady flow, uniform and non-uniform flow, turbulent flow.

- Explain the major and minor losses of head of water flowing through pipes.

- State Chezy's and Darcy's formulae for friction loss in pipe flow.

- Apply Chezy’s& Darcy’s formulae for calculation of losses in pipes.

- Explain with sketches the hydraulic gradient and total energy line under different conditions.

- Define orifice

- State types of orifices

- State the terms; jet of water, vena contracta, co-efficient of discharge and velocity of approach.

- Derive formulae for discharge through orifices

- Differentiate between orifice and mouth piece.

- Define notch

- State types of notches

- State the discharge formulae for notches.

- Define weir

- State types of weirs

- Differentiate sharp crested and broad crested weirs.

- State the discharge formulae for weirs.

- State the flow through open channels.

- State Chezy's, Manning & s Bazin's formulae for discharge through open channel.

- State most economical section of channel and condition for maximum discharge through channel.

- State discharge through rectangular & trapezoidal channel section and their formulae.

Critical Evidence(s) Required

The candidate needs to produce following critical evidences in order to competent in this competency standard.

- Observation and calculations of venturimeter.

- Readings ,Observation and calculations of piezometer.

- Calculations of of coeffient of velocity and discharge.

- Calculation sheet of discharge for vee and trapezoidal notch.

- Calculation sheet of discharge over weir.

Tools and Equipment

- Venturi meter

- Friction in pipes apparatus.

- Orifices.

- Vee and trapezoidal notches.

- Weirs

### Produce sketches of canals and head works

Overview: This competency standard covers the skills and knowledge required to draw a skeleton map of Pakistan showing rivers, main and link canal, Head works and barrages, Draw the plan of a multipurpose irrigation project, Draw a plan showing general layout of river training and protection works, Draw cross section of dams, Draw a plan showing the general layout of head works of a perennial canal, Draw cross-sections of a weir floors, Draw the plan and section of a silt ejector

| Competency Units | Performance Criteria |
| --- | --- |
| - Draw a skeleton map of Pakistan showing rivers, main and link canal, Head works and barrages | - Arrange drawing instruments - Select drawing sheet - Set sheet on drawing table as per standards. - Draw map of Pakistan. - Show rivers on map. - Draw barrages, main canals, head works and link canals |
| - Draw the plan of a multipurpose irrigation project | - Arrange drawing instruments - Select drawing sheet - Set sheet on drawing table as per standards. - Draw plan of project. - Show all details on plans . |
| - Draw a plan showing river training and Protection works. | - Arrange drawing instruments - Select drawing sheet - Set sheet on drawing table as per standards. - Draw plan of training and Protection works. - Show all details on plans |
| - Draw cross section of dams | - Arrange drawing instruments - Select drawing sheet - Set sheet on drawing table as per standards. - Draw x-section of dam. - Label all necessary details on plan. |
| - Draw a plan showing the general layout of head works of a perennial canal | - Arrange drawing instruments - Select drawing sheet - Set sheet on drawing table as per standards. - Select suitable scale. - Draw layout of head works. - Label all necessary details on plan. |
| - Draw cross-sections of a weir floors | - Arrange drawing instruments - Select drawing sheet - Set sheet on drawing table as per standards. - Select suitable scale. - Draw weir’s section. - Label all necessary details. |
| - Draw the plan and section of a silt ejector | - Arrange drawing instruments - Select drawing sheet - Set sheet on drawing table as per standards. - Select suitable scale. - Draw plan and section. - Label all necessary details. |

Knowledge & Understanding

  - Define irrigation

  - State history of irrigation.

  - State necessity and scope of irrigation.

  - State merits and demerits of irrigation

  - Explain types of irrigation i.e. flow irrigation and lift irrigation

  - Explain various sources of irrigation water.

  - Describe with map the irrigation network in Pakistan.

  - State the characteristics of Pakistan’s rivers.

  - State the important barrages of Pakistan.

  - State Indus Basin Project

  - Explain need and details of replacement works in Indus Basin Project

  - Know IRSA and PIDA

  - State the necessity of storage irrigation.

  - Define the various terms used in storage irrigation.

  - Explain the methods of assessment of maximum run off from a   catchment area

  - Define reservoirs

  - State the purpose of reservoir and its classification.

  - Describe the location of site selection for reservoir

  - State classification of dams i.e. based on function and use, structural design, materials of construction, shape of X-section

  - State factors to be considered during choice of dam for hydro project

  - explain the construction details of earthen dams

  - State the causes of failure of earthen dams and their remedies

  - Explain methods to control seepage in earthen dams

  - Explain necessity of raising of dams.

  - Explain methods of raising dam.

  - Understand Features and Function of Weir/Barrages.

  - Define weir and barrages.

  - Distinguish between barrages and weirs and explain their purposes.

  - Describe with sketches the components/parts of a barrage.

  - State the factors governing the site selection of a barrage.

  - State the types of weirs.

  - Explain surface flow at weirs.

  - Describe the necessity and importance of regulation and silt controlling works.

  - Explain head regulator and its types, i.e. flume, meter flume.

  - Describe with sketches the silt ejector, silt vanes, silt excluder and skimming platform.

  - Describe the necessity and importance of regulation and silt controlling works.

  - Describe with sketches the silt ejector, silt vanes, silt excluder and skimming platform.

  - List the objects of river training.

  - Explain with sketches different types of protective and river training works.

Critical Evidence(s) Required

The candidate needs to produce following critical evidences in order to competent in this competency standard.

- Drawing sketches showing rivers barages.

- Drawing sketch of multipurpose irrigation project.

- Drawing  river training works.

- Drawing dam section.

- Drawing  head works.

- Drawing weir floor.

- Drawing silt ejectors

Tools and Equipment

| S No. | Description (Instruments) | S No. | Description (Consumable) |
| --- | --- | --- | --- |
| 1 | Drawing board | 1 | Drawing sheet |
| 2 | T square | 2 | Eraser |
| 3 | Pair of Set squares | 3 | HB, H, 2H, 3H Pencils |
| 4 | Drawing Box (Compasses, divider, protractor, rule) | 4 | Scotch tape |
| 5 | Sharpener/ Sand paper |  |  |

### Design Canals

Overview: This competency standard covers the skills and knowledge required to Find design discharge of Karif and Rabi crops for given area, Draw the alignment of a canal, minor distributary and watercourses on contour map, Design a canal by Kennedy Critical velocity theory, Design a canal by Lacey's Regime velocity and  Draw the typical X-sections of channels

| Competency Units | Performance Criteria |
| --- | --- |
| - Find design discharge of Karif and Rabi crops for given area | P1. Identify area of crops (Kharif or Rabi) P2. Identify delta of each crop P3. Calculate duty P3. Estimate total water requirement |
| - Draw the alignment of a canal, minor distributary and watercourses on contour map | P1. Arrange drawing instruments P2. Draw a contour map with two meter interval P3. Draw alignment of canal, distributary and water course on some scale |
| - Design a canal by Kennedy Critical velocity theory | P1. Calculate area of cross-section and wetted perimeter P2. Assume depth and calculate critical velocity P3. Calculate C and R P4.Find velocity by using formulae P5.Calculate CVR P6. Find design parameters. |
| - Design a canal by Lacey's Regime velocity | P1. Identify formulae for design P2. Calculate f, V, A, PwAssume depth and calculate critical velocity P3. Calculate C and R P4.Find velocity by using formulae P5.Calculate CVR P6. Find design parameters. |
| - Draw the typical X-sections of channels | - Arrange drawing instruments - Select drawing sheet - Set sheet on drawing table as per standards. - Select suitable scale. - Draw sections of channel - Label all necessary details. |

Knowledge Area:

- Describe the term water requirement of crops.

- Enlist factors affecting water requirement

- Define the terms crop period, base period, Kharif-Rabi ratio, core watering, cash crop, crop rotation, and delta.

- Explain duty of water, factors affecting and its significance.

- State relation between duty and delta.

- Explain basic methods of water distribution to field i.e. Surface irrigation method, Furrow method, Contour method, Flooding method.

- Explain Sprinkler irrigation method

- Explain Drip or Trickle irrigation method.

- State the types of canal.

- Explain with sketches, components of a canal section

- State classification of canals

- Explain the factors governing alignment of canal.

- Explain lining and its types.

- Enlist factors to be considered for selection of type of lining

- State merits and demerits of lined and unlined channels.

- Describe Kennedy's critical velocity and Lacy's regime velocity for design of canals

- State Water logging

- State Causes and prevention measures.

- Explain Salinity.

- State Causes & prevention measures.

- Explain Methods of reclamation of soil.

- Describe up keep and maintenance of canals.

- Explain breaches in canal, water courses, preventive measure and methods of closing.

- Describe with sketch the silting tanks their classes, objects and working.

- Explain repair to bunds and formation of new bunds.

Tools and Equipment

| S No. | Description (Instruments) | S No. | Description (Consumable) |
| --- | --- | --- | --- |
| 1 | Drawing board | 1 | Drawing sheet |
| 2 | T square | 2 | Eraser |
| 3 | Pair of Set squares | 3 | HB, H, 2H, 3H Pencils |
| 4 | Drawing Box (Compasses, divider, protractor, rule) | 4 | Scotch tape |
| 5 | Sharpener/ Sand paper |  |  |

### Produce sketches of Hydraulic structures

Overview: This competency standard covers the skills and knowledge required to draw sketches of various canal falls. Draw the plane and L-section of a masonry flume. Prepare drawings of an Aqueduct crossing, Prepare drawings of a pipe outlet. Prepare drawings of an A.P.M Outlet

| Competency Units | Performance Criteria |
| --- | --- |
| - Draw sketches of various canal falls | - Identify falls(Ogee, rapids, stepped, trapezoidal, sarda and glaces) - Arrange drawing instruments - Select drawing sheet - Set sheet on drawing table as per standards - Draw sketches of falls |
| - Draw the plane and L-section of a masonry flume | - Identify flume structures - Arrange drawing instruments - Select drawing sheet - Set sheet on drawing table as per standards - Select scale as per requirement - Make drawing of masonry flume |
| - Prepare drawings of an Aqueduct crossing | - Identify cross drainage works(aqueduct, super passage, level crossing, tail escape) - Arrange drawing instruments - Select drawing sheet - Set sheet on drawing table as per standards - Select scale as per requirement - Make drawing of aqueduct |
| - Prepare drawings of a pipe outlet | - Identify outlets - Arrange drawing instruments - Select drawing sheet - Set sheet on drawing table as per standards - Select scale as per requirement - Make drawing of pipe outlet |
| - Prepare drawings of an A.P.M Outlet | - Identify outlets - Arrange drawing instruments - Select drawing sheet - Set sheet on drawing table as per standards - Select scale as per requirement - Make drawing of A.P.M. outlet |

Knowledge & Understanding

- Define canal falls.

- State the basic requirement of canal fall.

- Describe the types of canal falls.

- Explain the factors governing the site selection of canal falls.

- Explain head regulator and its types, i.e. flume, meter flume.

- Describe with sketches the different types of cross drainage works.

- Describe with sketches, super passage, syphon supper passage and level crossing.

- Describe drainage outlet and tail escape.

- Define outlet.

- State essential requirements of an outlet.

- Explain the characteristics of outlets.

- Describe with sketches the types of outlets (modular, semi modular and non-modular).

- Design of outlet, modular, semi-modular and non-modular

Critical Evidence(s) Required

The candidate needs to produce following critical evidences in order to competent in this competency standard.

- Drawing of canal falls.

- Drawing of masonary flume.

- Drawing of an aqueduct.

- Drawing of pipe out let.

- Drawing of APM out let

Tools and Equipment

| S No. | Description (Instruments) | S No. | Description (Consumable) |
| --- | --- | --- | --- |
| 1 | Drawing board | 1 | Drawing sheet |
| 2 | T square | 2 | Eraser |
| 3 | Pair of Set squares | 3 | HB, H, 2H, 3H Pencils |
| 4 | Drawing Box (Compasses, divider, protractor, rule) | 4 | Scotch tape |
| 5 | Sharpener/ Sand paper |  |  |