Curriculum for National Diploma Level 4 in Wind Power Plant Technician

National Vocational and Technical Training Commission (NAVTTC)

Government of Pakistan

FOREWORDS

National Vocational and Technical Training Commission (NAVTTC) extends its gratitude and appreciation to representatives of business, industry, academia, government agencies, provincial TEVTAs, sector skill councils and trade associations who spared time and extended their expertise for the development of National Vocational Qualification for Level-4 “Wind Power Plant Technician”. This work would not have been possible without the technical support of the experts.

It may not be out of place to mention here that all the experts of Industry, Academia and TVET experts of TEVTAs, and PVTC work diligently for making this qualification worthy and error free for which all credit goes to them. However, NAVTTC accepts the responsibility of all the errors and omissions still prevailing in the Qualification document.

It is also noteworthy that development of Skill Standards is a dynamic and ongoing process, and the developed competency standards needs periodic review and updating owing to the constant technological advancements, development in scientific knowledge, and growing experience of implementation at the grass root level as well as the demand of industry. The NAVTTC, Government of Pakistan will ensure to keep the qualifications abreast with the changing demands of both national and international job markets.

Executive Director (NAVTTC)

TABLE OF CONTENTS

1.	Introduction	1

1.1 Date of Development	1

1,.2. Date of Review and Validation	1

1.3. Entry Requirement	1

1.4. Minimum qualification for teachers	1

1,5 Codes of qualification (ISCED)	1

1.6. Medium of instruction	1

1.7. Duration of Course	1

2.	Scheme of Studies	2

3.	Daily Contact Hours	3

4.	Modules:	4

4.1 0031PSD01 Perform Basic Communication	4

4.2 0612CS01 Perform Basic Computer Operations	6

4.3 0713E&E4501 Apply Wind Power Plant Safety Procedures	9

4.4 0713E&E4502 Interpret Technical Drawings	14

4.5 0713E&E4503 Apply Environmental Protection Procedures	18

4.6 0713E&E4504 Control Operations of Wind Power Plant	21

4.7 0713E&E4505 Analyse Electrical Parameters through Testing	25

4.8 0713E&E4506 Analyse Mechanical Systems through Inspection	30

4.9 0713E&E4507 Conduct Preventive Maintenance of Mechanical Systems	36

4.10 0713E&E4508 Conduct Preventive Maintenance of Electrical Systems	41

4.11 0713E&E4509 Conduct Preventive Maintenance of Hydraulic Systems	49

4.12 0713E&E4510 Implement Corrective Maintenance of Wind Power Plant	52

4.13 0713E&E4511 On-Job Training	57

5.	List of Consolidated Consumables, Tools, Machinery & Equipment	58

6.	Members of Qualification Development Committee	60

# Introduction

The Wind Power Plant Technician Level 4 course curriculum has designed to develop highly skilled technicians proficient in advanced wind turbine technologies, operation, maintenance, and troubleshooting of wind power plants. This curriculum provides comprehensive theoretical knowledge combined with practical skills to ensure effective installation, commissioning, preventive maintenance, fault diagnosis, and safety management in large wind generation system. It aims to equip technicians with the competencies necessary to work independently and efficiently in modern wind power plants, ensuring optimal performance, reliability, and adherence to industry standards and safety regulations. The course covers critical areas such as electrical and mechanical systems of wind turbines, SCADA systems, control and monitoring techniques, safety protocols, and environmental considerations, preparing technicians for professional careers in the renewable energy sector.

.

| ## 1.1 Date of Development | 29th Sep – 3rd Oct, 2025 |
| --- | --- |
| ## 1,.2. Date of Review and Validation | 2028 |
| ## 1.3. Entry Requirement | Must have Secondary School Certificate (Science) or equivalent. OR Industrial Electrician Level 3 |
| ## 1.4. Minimum qualification for teachers | Bachelor’s degree in electrical engineering with at least 2 years of wind power plant industrial experience. |
| ## 1,5 Codes of qualification (ISCED) | Code: 0713E&E45 Description: National Diploma Level 4 in Energy Sector (Wind Power Plant Technician) |
| ## 1.6. Medium of instruction | Urdu, English or local language |
| ## 1.7. Duration of Course | Total. 857 hours. Theory. 83 hours Practical. 774 hours On Job Training. 240 hours |

# Scheme of Studies

| Competency Standards | NVQF Level | Category | Estimated Contact Hours |  |  | Cr. Hr. |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Th. | Pr. | Total |  |
| 0031PSD01 Perform Basic Communication | 2 | Generic | 4 | 12 | 16 | 1 |
| 0612CS01 Perform Basic Computer Operations | 2 | Technical | 6 | 18 | 24 | 1.5 |
| 0713E&E4501 Apply Wind Power Plant Safety Procedure | 3 | Functional | 6 | 48 | 54 | 3 |
| 0713E&E4502 Interpret Technical Drawings | 3 | Technical | 9 | 42 | 51 | 3 |
| 0713E&E4503 Apply Environmental Protection Procedures | 3 | Generic | 5 | 30 | 35 | 2 |
| 0713E&E4504 Control Operations of Wind Power Plant | 4 | Technical | 8 | 54 | 62 | 3.5 |
| 0713E&E4505 Analyse Electrical Parameters through Testing | 4 | Technical | 5 | 30 | 35 | 2 |
| 0713E&E4506 Analyse Mechanical Systems through Inspection | 4 | Technical | 9 | 42 | 51 | 3 |
| 0713E&E4507 Conduct Preventive Maintenance of Mechanical Systems | 4 | Technical | 7 | 66 | 73 | 4 |
| 0713E&E4508 Conduct Preventive Maintenance of Electrical Systems | 4 | Technical | 9 | 72 | 81 | 4.5 |
| 0713E&E4509 Conduct Preventive Maintenance of Hydraulic Systems | 4 | Technical | 7 | 66 | 73 | 4 |
| 0713E&E4510 Implement Corrective Maintenance of Wind Power Plant | 4 | Functional | 8 | 54 | 62 | 3.5 |
| 0713E&E4511 On Job Training | 4 | Technical | - | 240 | 240 | 6 |
| Total |  |  | 83 | 774 | 857 | 41 |

# Daily Contact Hours

| Daily Contact Hours by Institute | Duration |
| --- | --- |
| 2 | 17 months |
| 4 | 9 months |
| 5 | 7 months |
| 6 | 6 months |
| 8 | 5 months |
| Note: For Institute offering 6 days a week. The weekend institute may use formula: Credit hours / Daily hours = Months Duration |  |

# Modules:

## 4.1 0031PSD01 Perform Basic Communication

Objective: This module covers the skills and knowledge required to assist in the development of communication competency at the workplace by providing information regarding different forms of workplace communication and their appropriate use.

Duration: 16 Hours			Theory: 04 Hours			Practice: 12 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Follow workplace instructions | - Execute workplace instructions. - Ask questions to extract relevant information. - Carry out instructions based on received information. - Provide feedback based on written instructions received. - Compose workplace notes and memos. | - Mode of communication - Questioning Techniques - Rules on how to write memos, notes, messages - Understand feedback process Activity: Scenario The candidate is required to follow the instructions of the instructor. The instructor will ask to execute a simple task having three steps and student must do the task following the same three steps. | Theory-01Hrs Practice-03Hrs Total- 04Hrs | - Printouts of safety manual | - Classroom |
| Develop effective workplace relationships | - Perform duties to improve team cooperation. - Consult team members when challenges arise. - Respect differences in personal values and beliefs. - Report observed workplace harassment to relevant authority. | - Communication technology relevant to the workplace - Effective communication (body language) - Basic workplace documentation - Introduction to workplace harassment Activity: Roleplay Candidates will roleplay a scenario in pairs where a new employee introduces themselves to colleagues and ask for help in understanding their first task and colleagues will help them guide to perform the task. | Theory-01Hrs Practice-03Hrs Total- 04Hrs |  | - Classroom |
| Communicate and work with team members | - Identify individual roles and responsibilities within the team. - Recognize team members responsibilities with respect. - Identify the person for reporting inside and outside the team. - Participate in team meetings for discussions. - Communicate with team members through interaction tools and equipment. - Provide support to team members as needed during tasks. - Provide and respond to feedback | - Hierarchy of command - Communication tools and equipment Activity: Roleplay Candidates will roleplay a scenario in pairs where a team leader will give instructions for a task having three steps while other will listen, ask questions and execute the task following the three steps completely. | Theory-01Hrs Practice-03Hrs Total- 04Hrs | - Printouts of communication skills | - Classroom |
| Respond effectively to customer requests | - Listen to customer requests effectively. - Speak to customers using polite words. - Deliver information to required person in written or verbal form. | - Types of Customers - Speaking skills Activity: Roleplay Candidates will roleplay a scenario in pairs where one act as a customer asking for information about a product and other act as staff member who listens and respond to the queries to satisfy the customer | Theory-01Hrs Practice-03Hrs Total- 04Hrs | - Printouts of safety manual | - Classroom |

## 4.2 0612CS01 Perform Basic Computer Operations

Objective: This module covers the knowledge and skills required to understand basic computer hardware, software, applications and troubleshooting. You will be able to demonstrate your skills in operating a computer system and software such as MS Office as well as installation and troubleshooting of operating system and software.

Duration: 24 Hours			Theory: 06 Hours				Practice: 18 Hours

| Learning Unit |  | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- | --- |
| Perform basic configuration of computer system | - Connect computer components and peripherals as per requirement - Install Drivers and applications according to the software specification - Troubleshoot Applications to trace and fix faults if any | - Basic computer components - Peripherals & ports - Drivers - Software applications - Procedure of troubleshooting Activity: Candidate is required to connect a computer with monitor, keyboard, and mouse, install drivers and a basic application, simulate and fix a simple fault to show troubleshooting skills | Theory-01Hrs Practice-03Hrs Total- 04Hrs | - Labels for marking cables and ports - Computers with basic peripherals - USB drive - Whiteboard/Projector/Multimedia/LED | - Classroom - Lab |
| Perform software installation | - Download relevant software - Follow the Setup Wizard - Launch Software | - Software Acquisition - Software Installation - Application extensions - Desktop shortcuts Activity: Candidate is required to download and install a basic software using the setup wizard, then launch it to confirm successful installation | Theory-01Hrs Practice-03Hrs Total- 04Hrs | - Installation guide handout - Printed checklist for installation verification - Computers with internet access - USB drive - Whiteboard/Projector/Multimedia/LED | - Classroom - Lab |
| Demonstrate computer and internet use cases | - Operate common software applications - Access and use internet-based tools - Apply online safety and ethical practices | - Common software applications - Web navigation - Secure browsing - Online and Digital Privacy - Digital ethics Activity: Candidate is required to use a browser to search and download a safe file, create and save a short document, then explain one online safety tip to the class | Theory-01Hrs Practice-03Hrs Total- 04Hrs | - Printed safety tips handout - Computers with internet access - Whiteboard/Projector/Multimedia/LED | - Classroom - Lab |
| Perform basic documentation and presentation skills using MS Office | - Create and format documents using MS Word - Create and manage spreadsheets using MS Excel - Design and deliver presentations using MS PowerPoint | - Introduction to MS Word - Introduction to MS Excel - Introduction to MS PowerPoint - Procedure to print documents Activity: Candidate is required to create a short document in Word, a simple spreadsheet in Excel, and a three-slide presentation in PowerPoint, then save and present the files | Theory-01Hrs Practice-03Hrs Total- 04Hrs | - Computers with MS Office installed - Whiteboard/Projector/Multimedia/LED | - Classroom - Lab |
| Manage electronic mail | - Set up and configure email account - Compose emails - Attach and Download files - Receive and respond to emails - Print email | - Introduction to Email - Email Service Providers - Email Account Configuration - Email Composition Activity: Candidate is required to set up an email account, send an email with an attachment to a classmate, download the received file, and print the email. | Theory-01Hrs Practice-03Hrs Total- 04Hrs | - Printer paper - Computers with internet access - Printer | - Classroom - Lab |
| Apply cyber security best practices | - Identify common cyber threats and risks - Use strong, unique passwords for different accounts - Enable Multi-Factor Authentication (MFA) - Install and update antivirus or anti-malware software - Turn on firewalls and disable unused ports or services - Back up important data using secure storage - Control data sharing and adjust privacy settings on devices and platforms | - Cyber threats - Secure password rules - Multi-Factor Authentication (MFA) - Antivirus software - Firewalls and ports - Data backup procedure - Data Privacy and Protection Activity: Candidate is required to demonstrate three cyber threats, create a strong password, enable MFA on an account, and check antivirus and firewall status on a computer | Theory-01Hrs Practice-03Hrs Total- 04Hrs | - Computers with internet access - Antivirus - Whiteboard/Projector/Multimedia/LED | - Classroom - Lab |

## 4.3 0713E&E4501 Apply Wind Power Plant Safety Procedures

Objective: This module covers knowledge and skills required to apply safety procedures at wind power plant according to the industry’s approved guidelines. The underpinning knowledge regarding workplace safety practices will be sufficient to provide the basis for the job at workplace.

Duration: 54 Hours			Theory: 06 Hours				Practice: 48 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Prepare for safe work practices | - Identify emergency procedures - Use personal protective equipment - Follow safety instructions & signs during work. - Identify workplace hazards - Report hazards, incidents, and injuries according to workplace procedures. - Obtain work permit in accordance with standard procedure. | - Hazard, it’s types & management - Type of PPEs & usage - Type of Work Permits - Work Permit conditions - Types of Safety Signs Activity: Candidate will roleplay a scenario to wear required PPEs and to perform hazard identification walk-around in a simulated environment. Also perform job safety analysis, fill a sample work permit and fill a sample incident reporting form for a given job | Theory-1Hrs Practice-6Hrs Total- 7Hrs | - Incident reporting templates - Work permit templates - Job Safety Analysis Template | - Classroom - Workshop |
| Perform safe handling of tools and equipment | - Inspect tools and equipment for defects - Follow safety guidelines while using tools and equipment. - Clean and store tools and equipment after use - Report damaged tools and equipment to supervisor | - Types of tools and usage - Tools Management - Damaged tools reporting techniques Activity: Candidate will role play a scenario to inspect given tool kit, to identify defects, to demonstrate safe usage and storage of the tool. Fill sample damage report | Theory-1Hrs Practice-6Hrs Total- 7Hrs | - Toolkit | - Classroom - Workshop |
| Perform basic first aid for minor injuries | - Ensure availability of first aid box - Check first aid box for requisite emergency medicines - Check expiry date of medicines - Perform first aid for minor skin cut - Perform CPR | - Types of Emergencies - Medicines/Bandages application - Introduction to First Aid Kit - Minor cuts & bruise management - Basics of CPR Activity: Candidate will role play a scenario to practice first aid on minor cut in a simulated condition and perform CPR on mannequin. Fill inspection checklist of first aid kit | Theory-1Hrs Practice-6Hrs Total- 7Hrs | - First aid kit - CPR mannequin. | - Classroom - Workshop |
| Operate fire extinguisher | - Identify fire extinguisher according to type of fire - Check expiry of fire extinguisher - Operate fire extinguisher using PASS - Replace expired or used fire extinguisher | - Types of fire extinguishers - PASS method - Procedure of fire extinguisher health check up Activity: Candidate will role play a scenario to extinguish a controlled fire simulation, fill inspection checklist for fire extinguishers | Theory-0.5Hrs Practice-6Hrs Total- 6.5Hrs | - Fire Extinguisher | - Classroom - Workshop |
| Respond to emergencies | - Identify potential hazards in the designated area - Select control measure in accordance with workplace procedure - Follow emergency plan - Implement evacuation procedures as per SOPs - Operate emergency equipment and supplies | - Emergency planning management - Evacuation procedures - Precautionary measures in case of emergency Activity: Candidate will role play a scenario to participate in an evacuation drill and communicate via radios. | Theory-0.5Hrs Practice-06Hrs Total- 6.5Hrs | - Emergency plan maps - Emergency and Communication Devices | - Classroom - Workshops |
| Perform log out tag out procedure | - Identify energy sources for isolation - Switch off machines - Switch off equipment - Apply lockout devices - Attach safety tags - Verify isolation of equipment - Handover for job execution - Perform closure of equipment - Remove lockout and tagout devices | - Introduction of Energy Sources - Understand LOTO Mechanism - Handover Procedure for LOTO Activity: Candidate will role play a scenario to perform LOTO on a given live demonstration panel and fill a document for LOTO | Theory-0.5Hrs Practice-6Hrs Total- 6.5Hrs | - LOTO kits | - Classroom - Practical |
| Perform wind turbine generator climbing procedure | - Wear personnel protective equipment - Inspect climb gear system as per OEM instruction - Engage runner to safety rope/rail - Ascend ladder using three-point contact. - Inspect climbing ladder system as per OEM instruction - Descend ladder while attached with fall protection system. | - Introduction to Climb gear System - Ladder inspection techniques - Climbing & Rescue techniques Activity: Candidate will role play a scenario to demonstrate safe climbing on training ladder and perform rescue in different given scenarios: - Self Rescue - Assisted Casualty Rescue | Theory-0.5Hrs Practice-06Hrs Total- 6.5Hrs | - Ladder climbing gear - fall arrest systems - Climbing Simulator | - Classroom - Workshop |
| Perform wind turbine elevator operations | - Wear personal protective equipment - Inspect elevator instruction - Attach lanyard with lift safety anchor point - Operate elevator to ascend - Operate elevator to descend automatically - Operate elevator to descend manually | - Elevator inspection techniques - Manual v/s auto operations of elevator - Troubleshooting techniques for elevator system - Function of fall arrester system - Procedure of manual descend without grid power. Activity: Candidate will role play a scenario to ascend and descend on a simulated elevator simulator in a positioning and transition scenario | Theory-0.5Hrs Practice-03Hrs Total- 3.5Hrs | - Elevator simulator - harness. | - Classroom - Workshop |
| Perform wind turbine generator rescuing procedure | - Identify emergency situation - Report emergency situation to concern authority. - Prepare rescue equipment - Follow given rescue plan - Secure casualty with rescue system - Transfer casualty to medical care | - Introduction to Rescue plan - Casuality securing techniques - Safe lowering of causality techniques. - Active and Passive method WTG rescue. Activity: Candidate will role play a scenario to perform in a simulation of casuality rescue drill from turbine trainer. This will be a two person activity where one will act as casuality and other will rescue that person. | Theory-0.5Hrs Practice-03Hrs Total- 3.5Hrs | - Rescue device | - Classroom - Workshop |

## 4.4 0713E&E4502 Interpret Technical Drawings

Objective: This module covers the skills and knowledge required to understand and interprets technical drawing related to wind Turbines, including Symbols, annotations, and Specifications.

Duration: 51 Hours			Theory: 9 Hours				Practice: 42 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Identify drawing symbols of wind power plant | - Select relevant technical drawings of wind turbine systems - Identify standard drawing symbols. - Classify symbols into categories - Verify accuracy of interpretation through symbol legends - Document identified symbols with proper labeling | - Types of technical drawing - Introduction to drawing tools/Instruments. - Standard drawing conventions and symbol standards - Legends, keys, and references of drawing Activity: Candidate is provided with mixed technical drawings mechanical/electrical. They must highlight symbols, classify them, verify with legends and to prepare a labeled reference sheet. | Theory-02Hrs Practice-06Hrs Total- 08Hrs | - Drawing sheet - Led pencil - Eraser - Symbol reference booklets/handouts | - Classroom - Lab |
| Interpret layout diagram of wind turbine components | - Identify main components of wind turbine generator. - Identify arrangement of components in layout diagrams. - Verify layout diagrams against actual site placement. - Verify dimensions of Lay out - Verify scaling of Lay out - Identify missing details in layout. | - Main components of a wind turbine - Layout Diagram of nacelle, tower and rotor. Activity: Candidate is provided with a layout drawing of Wind Turbine nacelle. They must annotate the placement of components and check scaling/dimensions of the components. | Theory-01Hrs Practice-06Hrs Total- 07Hrs | - Drawing Table - Set square | - Classroom - Lab |
| Interpret mechanical drawings | - Interpret sectional views. - Identify power transmission components of wind power plant. - Identify drawing specifications. - Match drawing details with physical parts during inspection. - Submit final report | - Sectional views of wind Turbine components. - Introduction to power transmission components in wind power Plant. - Specification and tolerances in Sectional drawing of mechanical system. Activity: Candidate is given with a sectional views of turbines drawings, they should mark components of power transmission and report the findings. | Theory-01 Hrs. Practice-06Hrs Total- 07 Hrs. | - Mechanical drawings of wind turbine systems - Manufacturer’s technical manuals and specification sheets - CAD Software | - Classroom - Lab |
| Interpret electrical drawings | - Interpret standard electrical symbols. - Interpret single line diagrams - Interpret wiring schematics. - Follow electrical power flow from generator to grid using technical drawings - Verify Electrical parameters ratings - Verify specifications of electrical equipment. - Report issues in drawings to supervisor | - Understanding of Standard Electrical Symbols - Understand Single Line Diagram of Electrical Power Flow from Generator to Grid Activity: Candidates are provided with a single line diagram of Wind turbine. They must identify power flow, protective devices and verify equipment rating against OME Manual and report the findings. | Theory-02 Hrs. Practice-06Hrs Total- 08Hrs | - Set-Square - Manufacturer’s technical manuals and specification sheets - CAD Software | - Classroom - Lab |
| Interpret civil drawings | - Interpret foundation drawings of towers. - Interpret structural reinforcement details. - Identify site layout - Identify access routes. - Verify scale of drawing - Verify dimension of drawing - Check compliance with civil engineering standards. | - Overview of Civil engineering drawings - Types of civil construction plans - Foundation Drawing & Symbols. - Details and bar bending schedules. - Introduction to Drawing Scale and dimensions. - Civil engineering Codes & Standards. Activity: Candidates are given a foundation drawing of turbines tower. They are required to prepare a report containing reinforcement details of the foundation. Also check compliance with civil standards and calculates scale/levels. | Theory-02Hrs Practice-03Hrs Total- 05Hrs | - Calculator - CAD software | - Classroom - Lab |
| Interpret hydraulic drawings | - Recognize symbols in hydraulic drawing - Interpret fluid lines in given hydraulic diagram. - Identify components in hydraulic pitch System - Identify components in braking system - Identify pressure and flow specifications indicated in hydraulic circuit diagrams - Identify fluid circuits in hydraulic system drawings. - Report unclear details in drawings to supervisor | - Interpretation of hydraulic symbols and fluid line Conventions. - Components of Hydraulic pitch & Brake System - Overview of pressure and flow specification in hydraulic circuit diagrams. - Fluid circuit in hydraulic system drawing. Activity: Candidates are provided with a hydraulic circuit diagram of the Pitch/Braking System. They are required to prepare a report containing components pressure lines. | Theory-02Hrs Practice-03Hrs Total- 05Hrs | - CAD Software - Manufacturer’s technical manuals and specification sheets. | - Classroom - Lab |

## 4.5 0713E&E4503 Apply Environmental Protection Procedures

Objective: This module covers the skills and knowledge required to apply environmental protection procedures during the activities at workplace. This will equip them to handle and transport waste material and store it per green practices.

Duration: 24 Hours			Theory: 06 Hours				Practice: 18 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Identify hazards at workplace | - Check oil leak at in work area - Detect damaged electrical wiring in work area - Identify leakage of chemical substances in work area - Inspect hazard warning labels for damage in workplace - Report identified hazards to concerned authority | - Understanding of Oil leakage Conditions - Understanding of Standard Electrical Wiring Tests - Understanding of chemical Leakages conditions - Reporting of hazards Procedure Activity: Make a group of five trainees and assign the following task to perform: Identify oil leakage, damaged wiring, chemical leakage, safety instructions, and reportable hazards in the workplace . | Theory-01Hrs Practice-03Hrs Total- 04Hrs | - Stickers for Safety Signs - PPE’s - Emergency Alarm | - Classroom - Lab |
| Handle hazardous material safely | - Identify hazardous substances in workplace - Select required personal protective equipment - Label container according to hazard class - Store hazardous material in labelled containers - Transport hazardous material using safe handling procedure - Apply spill prevention procedure during handling. | - Understanding of Hazards and their types - Storage of hazardous material - procedure of Transportation of hazardous material - Spill prevention procedure Activity: Candidate will role play a scenario to Observe hazardous substances, check labels, inspect storage, monitor transport and examine spill prevention procedures. | Theory-02Hrs Practice-03Hrs Total- 05Hrs | - Tags | - Classroom - Lab |
| Dispose of waste material as per green practices | - Identify waste material in workplace - Segregate waste material according to type. - Place waste material in designated collection bins - Transfer segregated waste to disposal facilities - Maintain disposal record | - Understanding of Waste Segregation - Placement of Waste at designated Allocation - Understanding of Green Practices - Maintenance of waste disposal record Activity: Make a team of trainees and assign them the following tasks: to perform waste segragation, to place at designated allocation, to dispose the waste and to maintain record | Theory-02Hrs Practice-06Hrs Total- 08Hrs | - Waste bins - Record Maintenance Book | - Classroom - Lab |
| Apply resource conservation practice | - Switch off electrical equipment when not in use - Use water in controlled amount during maintenance of systems. - Re-use material where applicable - Re-use components where applicable. - Record daily consumption of material in log sheet - Report excess consumption of material to supervisor. | - Resource Conservation standards - Preparation of Logbook - Significance of logbook - Introduction to 6 R’s of Greening Activity: Candidate is required to apply conservation practices in terms of energy and water systematic practices, record-keeping, reuse, and reporting. | Theory-01Hrs Practice-06Hrs Total- 07Hrs |  | - Classroom - Lab |

## 4.6 0713E&E4504 Control Operations of Wind Power Plant

Objective: This module covers the skills and knowledge required to perform various operations of Wind Power Plant. The underpinning knowledge will be sufficient to provide the basis for the job at workplace.

Duration: 62 Hours			Theory: 08 Hours				Practice: 54 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Perform operation of wind turbine on SCADA | - Access Securely WTG SCADA System. - Operate turbine as per instructions - Monitor wind turbine parameters on dashboard - Identify System alarms as per instructions - Respond to system alarms as per procedures - Maintain WTG SCADA logs | - Function of WTG SCADA system - Overview of wind turbine operations - Overview of WTG SCADA system - Introduction to WTG SCADA Logs Activity: Candidate is required to log in to the SCADA system with proper credentials provided. | Theory-01Hrs Practice-09Hrs Total- 10Hrs | - SCADA simulator | - Classroom - Lab |
| Perform operation of electrical system on eBOP SCADA | - Access securely eBOP SCADA System - Perform switching operations on electrical equipment as per instructions. - Monitor electrical system parameters on dashboard - Identify system alarms as per instructions - Respond to system alarm as per procedures - Maintain eBOP SCADA logs | - Function of eBOP SCADA system - Overview of eBOP SCADA system - Electrical Safety Rules - Operational Procedures - Introduction to eBOP SCADA logs Activity: Candidate is required to Identify different alarm types of Wind turbines and prepare a report showing different actions against the alarms. | Theory-01Hrs Practice-09Hrs Total- 10Hrs | - SCADA simulator | - Classroom - Lab |
| Perform manual operations of wind turbine | - Identify equipment for command execution - Perform operation using relay HMI where available - Perform Operation through local field switch. - Maintain respective log | - Overview of manual operational procedures - Introduction to Grid Codes - Basics of HMI Relay - Overview of Wind Turbine Operations Activity: A turbine T2 trip suddenly and eBOP & WTG SCADA system is not working. Candidate is required to manually perform emergency operations on wind turbine mockup. | Theory-01Hrs Practice-09Hrs Total- 10Hrs | - Human Machine Interface (HMI) Panels - Simulated HMI Screens - Wind turbine Mock up | - Classroom - Lab |
| Communicate with system operator | - Communicate with system operator using approved communication device. - Follow instructions provided by the system operator - Report task completion, - Report to status back to the system - Inform system operator of any faults as per operating procedure. | - Overview of Communication Protocols. - Modes of Communication with system Operator Activity: Frequency deviation occurs on a trip. Candidate is required to communicate with the system operator for a quick action to solve frequency deviation. | Theory-01Hrs Practice-09Hrs Total- 10Hrs | - Communication device - PLC - DCS | - Classroom - Lab |
| Perform data reporting | - Record parameters data from SCADA system as per requirement - Prepare reports as per required format - Confirm accuracy of prepared report with SCADA data - Obtain authorization before executing operational actions - Communicate reports using the required medium as per procedures - Maintain reports in data archival system | - Overview of Data Validation - External data reporting - Internal data reporting - Overview of data archive system Activity: All the trainees are required to prepare the data sets of 3 turbines from the SCADA system in terms of Wind Speed, Power Output, Turbine Status and maintenance record. | Theory-01Hrs Practice-06Hrs Total- 07Hrs | - SCADA simulator | - Classroom - Lab |
| Prepare work permit for maintenance | - Identify scope of maintenance activity - Fill work permit with correct details - Obtain approvals from authorized personnel - Communicate work permit conditions to requesting concerned party - Close work permit after job completion - Maintain work permit log | - Overview of maintenance schedule - Introduction to Work Permit Activity: Candidate is required to prepare work permit for the maintenance of gear box oil change. | Theory-01Hrs Practice-06Hrs Total- 07Hrs |  | - Classroom - Lab |
| Monitor via HMI panels of relay | - Navigate HMI control panel of Relay - Identify alarms on HMI Control Panel - Check operational parameters on Control Panel - Prepare report of findings and submit it - Take corrective or preventive actions, if required | - Electrical Safety rules - Overview of Grid Codes Activity: Candidate is required to Identify active alarm from HMI Panel and prepare a report with Rectification plan. | Theory-01Hrs Practice-03Hrs Total- 04Hrs | - Human Machine Interface (HMI) Panels - Simulated HMI Screens | - Classroom - Lab |
| Maintain record of maintenance activity | - Identify Faults on equipment - Create notifications for maintenance as Per instructions - Close notification after maintenance completion as per instructions - Update maintenance record through respective checklist | - Log preparation technique - Overview of archiving procedures Activity: Prepare a pre and post record of routine inspection of given fault in equipment and submit a report with recorded data. | Theory-01Hrs Practice-03Hrs Total- 04Hrs |  | - Classroom - Lab |

# 4.7 0713E&E4505 Analyse Electrical Parameters through Testing

# Objective: This module covers the knowledge and skills required to understand the procedures to safely carry out electrical testing, diagnosis, and maintenance tasks on wind turbine electrical systems. This includes understanding basic electrical concepts, identifying electrical components and their functions, recognizing electrical safety hazards, and performing practical electrical testing routines such as using multimeters, insulation testers, and interpreting electrical schematics relevant to wind turbines

# Duration: 73 hrs                                           Theory: 7 hrs                                               Practical: 66 hrs

| Learning Unit |  | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- | --- |
| Measure basic electrical parameters | - Select testing tools as per testing requirements. - Select PPE’s as per testing requirement. - Measure voltage values of electrical components - Measure current values of electrical components - Measure waveform of electrical components - Measure resistance values of electrical components - Measure capacitance of electrical components - Measure inductance of electrical components | - Fundamentals of Electrical - Basic Electrical Quantities - Basic Testing Tools - Selection of PPE as per testing requirement - Measurement of Basic Electrical Quantities Activity: Candidate is required to perform routine electrical testing and safety checks on wind turbine simulator and prepare a report. | Theory-01Hrs Practice-09Hrs Total- 10Hrs | - Fuses - Electrical Contact Cleaner - Batteries - Gloves - Digital Multimeter - Clamp meter - Whiteboard/Projector/Multimedia/LED - Oscilloscope - Clamp on meter - Insulation resistance Tester | - Classroom - Lab |
| Verify insulation resistance | - Select Insulation Tester as per system voltage rating. - Inspect Instrument Calibration before use. - Inspect Tester leads before use. - Check the System is de-energized before testing. - Apply Test Voltage according to equipment rating. - Record Insulation resistance readings for all phases and earth connections. - Compare Obtained Readings with manufacturer’s Specifications. - Document Test Results clearly in prescribed log report format. - Report Abnormal Values/ Faults to supervisor | - Understanding of System Voltage Rating - Selection of Insulation Resistance Tester - Procedure of Insulation Resistance Testing - Documentation of test results Activity: Candidate is required to perform insulation resistance testing on wind turbine system. He is tasked with performing an insulation resistance test on the electrical system. | Theory-01Hrs Practice-09Hrs Total- 10Hrs | - Batteries - Fuses - Cleaning spray - Gloves - Digital Multimeter - Clamp on meter - Insulation resistance tester | - Classroom - Lab |
| Inspect contact resistance | - Select contact resistance tester as per voltage rating - Check Tester Calibration. - Check Clamps/ leads. - Apply Test current as per manufacturer’s Specifications. - Measure resistance values accurately. - Record Resistance Values accordingly. - Compare readings with manufacturer’s specifications. - Document Results on prescribed format. - Report abnormal values or defective contacts to supervisor | - Understand Voltage rating of wind power plant - Significance of Calibration of Insulation Resistance Tester - Application of test results - Documentation of test result Activity: Candidate is required to perform scheduled preventive maintenance check on a wind turbine's electrical contacts to ensure good conductivity and prevent failures. | Theory-01Hrs Practice-09Hrs Total- 10Hrs | - Insulation Tapes - Contact resistance tester - Toolkits - Test Leads | - Classroom - Lab |
| Perform phase sequence test | - Select Phase Sequence Tester according to the system voltage level. - Connect Phase Sequence Tester Leads to three supply terminals. - Record phase sequence result. - Interpret results to verify correct motor/generator rotation direction as per operational requirement. - Document Phase Sequence Test Results on log sheet. - Report abnormal conditions to in charge. | - Selection of Phase Sequence Tester - Connection of Phase sequence tester - Record Phase Sequence Test Results Activity: Candidate is required to conduct a phase sequence test on the main electrical supply. | Theory-01Hrs Practice-09Hrs Total- 10Hrs | - Phase Sequence Tester - Test Leads - Log Sheet | - Classroom - Lab |
| Perform grounding resistance test | - Check Tester Calibration - Install grounding resistance electrodes on ground - Document values of resistance in log sheet - Compare readings with reference values - Report abnormal conditions to in charge. | - Check Tester Calibration - Install Grounding resistance electrodes on ground - Comparison of reading values with reference values Activity: Candidate is required conduct a grounding resistance test on the wind turbine’s earthing system. | Theory-01Hrs Practice-09Hrs Total- 10Hrs | - Grounding resistance tester - Grounding electrodes - Test Leads | - Classroom - Lab |
| Inspect protection system | - Identify protective devices. - Check correct rating. - Verify ON/OFF operation of protective devices. - Record Test results. - Document results on prescribed format. - Report abnormal conditions to in charge. - Control data sharing and adjust privacy settings on devices and platforms | - Identification of Protective devices - Test On/Off Operation of Protection devices Activity: Candidate is required to inspect and test the protective devices (such as circuit breakers, fuses, surge arresters, and relays) within a wind turbine’s electrical control panel | Theory-01Hrs Practice-09Hrs Total- 10Hrs | - Protective device tester - Test Leads | - Classroom - Lab |
| Conduct functional tests on switchgear | - Select testing instruments - Perform visual inspection of switchgear components. - Carry out ON/OFF tests. - Record test results. | - Selection of testing instruments - Visual inspection of switchgear components. - Carry out ON/OFF tests. - Record test results. Activity: Candidate is required to inspect and perform basic operational tests on the main switchgear panel. | Theory=0.5 Hrs Practical= 06 Hrs Theory= 6.5 Hrs | - Insulation tester - Magnifying Glass | - Class room - Lab |
| Perform continuity test | - Select testing instruments. - Check system is isolated before use. - Connect Test leads between protective conductor and main - earthing terminal as per procedure - Measure resistance value. - Check resistance value is in acceptable range. - Record resistance accurately. - Document Test Results. - Report abnormal conditions to supervisor | - Selection of testing instruments - Check system is isolated before use - Connection of Test Leads Between Protective Conductor and Main Earthing Terminal Activity: Candidate is required to measure and verify the grounding resistance of a wind turbine system. | Theory=0.5 Hrs Practical= 06 Hrs Theory= 6.5 Hrs | - Insulation Tester - Micro-ohm meter - Timing Tester | - Class room - Lab |

### 4.8 0713E&E4506 Analyse Mechanical Systems through Inspection

Objective: This module covers the skills and knowledge required to the trainee will be able to describe the skills and knowledge required to perform inspection of mechanical systems. The underpinning knowledge will be sufficient to provide the basis for the job at workplace.

Duration: 51 Hours			Theory: 09 Hours				Practice: 42 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Inspect physical condition of equipment | - Identify cracks, corrosion and wear. - Inspect seals/gaskets for leakage - Prepare inspection report with photographs - Report condition to supervisor | - Knowledge of degradation of mechanical systems - Visual inspection techniques of equipment - Physical inspection techniques of equipment Activity: Candidate is required to perform a complete physical inspection of a wind turbine’s Yaws system training mock-up, compare readings with OEM limits and report the findings. | Theory-01Hrs Practice-03Hrs Total- 04Hrs | - Stickers for marking - Yaw’s system training mockup | - Classroom - Workshop |
| Check dimension of components | - Identify required tool for dimensional check - Record dimension of brake pad thickness - Record dimension of slip-ring carbon brushes - Compare recorded dimensions with OEM standard dimensions. - Report conditions to supervisor | - Overview of measuring instruments - Knowledge of measuring instrument calibration techniques Activity: Candidate is required to perform dimensional checks on brake pads and slip-ring of wind turbine training mock-up, compare readings with OEM limits and report the findings. | Theory-01Hrs Practice-03Hrs Total- 04Hrs | - Tags - Measuring tape - Wind turbine training model | - Classroom - Workshop |
| Check temperature of components | - Check calibration of IR thermometer - Use IR thermometer on transformer - Record readings of temperature - Compare against OEM limits - Report conditions to supervisor | - Working principles of IR thermometer - IR thermometer calibration techniques - Effect of temperature on components. Activity: Candidate is required to perform a complete temperature inspection of a transformer mockup using an IR thermometer, verify calibration, compare readings with OEM limits and report the findings. | Theory-01Hrs Practice-03Hrs Total- 04Hrs | - Tags - Transformer training model | - Classroom - Workshop |
| Inspect noise level | - Check calibration of sound meter - Use sound meter as per instruction - Record dB levels at required key points - Compare against OEM limits - Identify abnormal sounds or vibrations in wind turbine - Report condition to supervisor | - Overview of sound meter - Types of sound meter - Difference between Sound and Noise Activity: Candidate is required to perform a complete noise level inspection of a given wind turbine training model, identify abnormal sounds, compare measurements with OEM limits, and report the findings. | Theory-1Hrs Practice-03Hrs `Total- 4Hrs | - Sound meter - Wind turbine training model | - Classroom - Workshop |
| Check oil level of components | - Check oil levels of gearbox through oil level indicator - Check oil levels of transformer through oil level gauge - Record oil levels as per instructions - Compare against OEM limits - Report condition to supervisor | - Role of oil in cooling, lubrication, and insulation. - Knowledge of oil level indicators and gauges Activity: Candidate will check and record oil levels of a gearbox and transformer model and compare measurements with OEM and report the findings. | Theory-1Hrs Practice-03Hrs Total- 4Hrs | - Oil level indicator - Gearbox training model - Transformer training model | - Classroom - Workshop |
| Perform oil sampling | - Identify required sample bottle - Collect oil sample from sampling point of gearbox as per instructions - Collect oil sample from sampling point of transformer as per instructions - Label sample bottle. - Seal sample bottle - Fill Performa for sample bottle - Submit sample to supervisor | - Types of oil sample bottles - Oil sample collection techniques - Labeling and sealing techniques Activity: Candidate is required to collect oil sample from a given gearbox and transformer training model, label and seal it and submit oil samples as per standard procedure. | Theory-01Hrs Practice-03Hrs Total- 4Hrs | - Oil Sample bottles - Labels - Gearbox training model - Transformer training model | - Classroom - Workshop |
| Perform grease sampling | - Identify required sample bottle - Collect grease sample from main bearing as per instructions - Collect grease sample from generator bearing as per instructions - Label sample bottle. - Fill Performa for sample bottle - Submit sample to supervisor | - Types of grease sample bottles - Grease sampling techniques Activity: Candidate is required to perform grease sampling from the given main bearing and generator bearing training model, label the sample properly and submit grease sample as per standard procedure. | Theory-1Hrs Practice-03Hrs Total- 04Hrs | - Greasing bottles - Labels - Spatula - Generator training model - Main bearing training model | - Class room - Workshop |
| Inspect pressure of hydraulic systems | - Identify required gauge as per system rating - Check calibration of gauge - Check hydraulic pressure from required points as per instructions - Record pressures of hydraulic system - Compare with set values as per OEM instructions - Report condition to supervisor | - Types of Hydraulic pressure gauges - Importance of gauge calibration - Pressure measurement procedure Activity: Candidate is required to inspect the pressure of a training model of hydraulic system using a calibrated pressure gauge and report the findings. | Theory-1Hrs Practice-03Hrs Total- 4Hrs | - Hydraulic pressure gauges - Pressure hoses - Hydraulic system training model | - Classroom - Workshop |
| Check alignment of components | - Check calibration of laser alignment tool - Mount laser alignment tool components as per instructions - Record alignment values. - Compare with set values as per OEM instructions - Adjust horizontal position of generator as required - Adjust vertical position of generator as required - Record alignment values and repeat procedure if required - Report conditions to supervisor | - Basics of shaft alignment - Working principles of laser alignment tools - Alignment techniques Activity: Candidate is required to perform alignment of the generator and gearbox shafts model using a laser alignment tool and report the findings. | Theory-0.5Hrs Practice-09Hrs Total- 9.5Hrs | - Wedges - Jack bolts/ Alignment screws | - Classroom - Workshop |
| Perform load testing | - Identify suitable weights as per system ratings - Load overhead crane progressively as per instructions - Operate overhead crane as per instructions - Hold loaded crane for defined duration as per instructions - Report conditions to supervisor | - Types of overhead crane - Load calculation procedure - Progressive loading Procedures Activity: Candidate is required to perform a safe load test on an overhead training mock-up crane used in wind turbine maintenance and report the findings. | Theory-0.5Hrs Practice-09Hrs Total- 9.5Hrs | - Tags - Load blocks - Lifting gear | - Classroom - Workshop |

## 4.9 0713E&E4507 Conduct Preventive Maintenance of Mechanical Systems

Objective: This module covers knowledge and skills required to describe the skills and knowledge required to perform preventive maintenance of Mechanical systems. The underpinning knowledge will be sufficient to provide the basis for the job at workplace.

Duration: 73 Hours			Theory: 07 Hours				Practice: 66 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Maintain gearbox | - Perform physical inspection of gearbox - Check seal of inspection window - Check surface tooth system - Check oil level and condition - Perform oil sampling - Change oil of gearbox, if required. - Perform physical Inspection of ventilation filter - Perform physical Inspection of elastomer bearing - Check screw tightness - Record activity on maintenance checklist - Submit results to supervisor | - Components of gearbox - Introduction to elastomer bearing - Types of ventilation filters Activity: Candidate is required to inspect elastomer bearing, check screw tightness, replace ventilation filter of a given mockup gearbox and prepare a report of findings. | Theory-0.5Hrs Practice-9Hrs Total- 9.5Hrs | - Oil sampling kit - log sheets. - Ventilation filter - Torque wrench | - Classroom - Workshop |
| Maintain braking system | - Perform physical inspection of brake disc - Inspect brake pads and calipers. - Check hydraulic pressure. - Measure brake pad thickness. - Replace worn brake pads when required. - Check for hydraulic oil leakage - Check screw connections - Record activity on maintenance checklist - Submit results to supervisor | - Brake Pad inspection techniques - Brake Disc inspection techniques - Brake Caliper inspection techniques - Components of hydraulic braking system Activity: Candidate is required to measure brake pad thickness and hydraulic pressure of a given mock-up hydraulic system and report the findings. | Theory-0.5Hrs Practice-3Hrs Total- 3.5Hrs | - Hydraulic gauge - Measuring gauge | - Classroom - Workshop |
| Maintain yaw system | - Check yaw gearbox oil level - Check yaw gearbox leakage - Change oil of yaw system, if required. - Check screw connections - Check hydraulic connections, hoses and pips - Check brake lining thickness - Check hydraulic oil pressure at yaw calipers - Perform lubrication of tooth system according to OEM guidelines - Perform lubrication of bearing - Perform physical inspection of yaw system - Record activity on maintenance checklist - Submit results to supervisor | - Components of yaw system - Procedure of lubrication in yaw system Activity: Candidate is required to demonstrate lubrication of training mockup bearing yaw teeth system, check hydraulic pressure & bleed and charge hydraulic system. | Theory-01Hrs Practice-9Hrs Total- 10Hrs | - Lubrication kit. - Grease gun | - Classroom - Workshop |
| Maintain cooling system | - Inspect physical condition of heat exchanger for damage. - Perform cleaning of heat exchanger as per OEM guidelines - Inspect gear oil hoses for leaks. - Replace gear oil filter. - Record operating temperature trends. - Record activity on maintenance checklist - Submit results to supervisor | - Heat exchanger - Heat exchanger cleaning techniques - Oil filter replacement techniques Activity: Candidate is required to clean training model of a heat exchanger and replace oil filter. Prepare a report of findings. | Theory-1Hrs Practice-9Hrs Total- 10Hrs | - Oil Filter | - Classroom - Workshop |
| Maintain lubrication system | - Inspect lubrication pumps. - Check grease levels. - Verify connection of grease block with hoses - Perform grease filling if required. - Perform pump operational testing. - Record activity on maintenance checklist - Submit results to supervisor | - Understanding of lubrication pump operations - Type of grease and their properties - Lubrication system control circuit - Introduction to grease block operations Activity: Candidate is required to perform pump operation testing and verify connections on lubrication system training model. Prepare a report of findings. | Theory-01Hrs Practice-09Hrs Total- 10Hrs | - Grease gun | - Classroom - Workshop |
| Maintain pitch system | - Inspect pitch motor/actuator. - Check limit switch functionality - Check pitch gearbox oil level - Perform physical inspection for leakage - Change oil of pitch system, if required - Check screw connections - Check pitch motor carbon brushes. - Check blade angle calibration. - Inspect slip rings and connections. - Perform Lubrication of pitch bearings. - Perform Lubrication of tooth system - Perform manual pitch movement test. - Record activity on maintenance checklist - Submit results to supervisor | - Types of Motors - Importance of control system of pitch motors. - Types of Encoders and tacho-generator of pitch motor - Types of limit switches of blades - Blade Calibration techniques Activity: Candidate is required to inspect motor and pitch drive of a given pitch system training model and report the findings. | Theory-01Hrs Practice-09Hrs Total- 10Hrs | - Torque wrench. | - Classroom - Workshop |
| Maintain coupling system | - Inspect shaft couplings. - Check screw connections - Check generator alignment. - Record activity on maintenance checklist - Submit results to supervisor | - Types of coupling - Coupling alignment procedure. Activity: Candidate is required to inspect shaft coupling and perform coupling alignment on training model of gearbox generator. | Theory-1Hrs Practice-9Hrs Total- 10Hrs | - Coupling - Laser Alignment tool | - Classroom - Workshop |
| Perform bolt tightening | - Select correct torque/tension tool. - Verify calibration of tools. - Apply correct torque as per OEM. - Record activity on maintenance checklist - Submit results to supervisor | - Types of Bolts - Fundamentals of torque application - Manual and hydraulic torquing Activity: Candidate is required to demonstrate bolt tightening on a given sample as per OEM torque specs. | Theory-01Hrs Practice-09Hrs Total- 10Hrs | - Manual torque wrench - Hydraulic torque wrencg | - Classroom - Workshop |

### 4.10 0713E&E4508 Conduct Preventive Maintenance of Electrical Systems

Objective: This module covers the skills and knowledge required to maintain electronic components, electrical Sensors, control circuits, power circuits, generators, transformers, AC motor, DC motor, switch gear and frequency convertor

Duration: 81 Hours			Theory: 09 Hours				Practice: 72 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Maintain electronic components | - Identify cleaning tools of electronic components. - Clean given electronic components as per requirement. - Check for signs of damage at connection points. - Check voltage of required component as per standard. - Check current of required component as per standard. - Check resistance of required component as per standard. - Check continuity of required component as per standard. - Check inductance of required component as per standard - Check capacitance of required component as per standard - Fill required checklist as per OEM guidelines - Submit results to supervisor | - Fundamentals of electronic components - Damage indicators of electronic components - Electrical measurement instruments - Standard testing procedures of electronic components - OEM guidelines and standards for electronic component testing Activity: The candidate is provided with an electronic component, clean it and visually inspect it for damage. Measure the electrical parameter, compare the results with OEM specifications, and record findings. | Theory-01 Hrs Practice-06Hrs Total- 7Hrs | - Cleaning swabs/cloths - Contact cleaner/solvent - Electronic components (resistors, capacitors, inductors, connectors, etc.) - Multimeter | - Classroom - Lab |
| Maintain electrical sensors | - Inspect physical condition of sensors and devices. - Clean sensor terminals/connectors as per SOPS. - Perform signal output verification on given sensor as per standard. - Check resistance of optical encoder, limit switches and pressure sensor as per standard. - Verify continuity of optical encoder, limit switches and pressure sensor as per standard. - Fill required checklist as per OEM guidelines - Submit results to supervisor | - Types of sensors and devices - SOPs for cleaning connectors/terminals - Sensor signal output verification methods - Resistance measurement of sensors - Continuity testing methods for sensors Activity: Candidate is given 3 sensors (optical encoder, limit switch, pressure sensor) etc. to inspect, clean, test (resistance, continuity, signal output), and record results in the OEM. | Theory-01 Hrs Practice-06Hrs Total- 7Hrs | - Cleaning cloths / lint-free wipes - Contact cleaner / isopropyl alcohol - Cotton swabs - Sensors - Power supply unit - Multimeter | - Classroom - Lab |
| Maintain control circuits | - Perform functionality test through wind turbine control panel as per OEM instructions - Identify abnormality on control panel - Fill required checklist as per OEM guidelines - Submit results to supervisor | - Principal of wind turbine control and monitoring systems - Overview of control panel indicators, alarms, and faults Activity: The candidate is required to correctly operates the wind turbine control panel simulation following OEM procedures, performs functional tests of turbine subsystems, identifies and records any abnormalities or alarms, completes the OEM checklist with measured and observed data, and submits a technical report to the supervisor. | Theory-01 Hrs Practice-06Hrs Total- 7Hrs | - Cleaning wipes - Wind turbine control panel simulator - Power supply unit - Multimeter | - Classroom - Lab |
| Maintain power circuits | - Check grid power cables connection tightness - Perform thermal vision inspection on busbars - Perform thermal vision inspection on breakers - Perform insulation resistance testing. - Tighten loose connections as per standard, if any. - Replace damaged cables as per OEM guidelines - Measure voltage, and current for reliability. - Fill required checklist as per OEM guidelines - Submit results to supervisor | - Grid power cable connections and standards - Thermal imaging principles for busbars and breakers - Insulation resistance testing methods and safety - Procedures for tightening and replacing electrical connections - Voltage and current measurement techniques Activity: The candidate is given a power circuit sample. He has to inspects grid power cables, performs thermal imaging on busbars and breakers, conducts insulation resistance testing, rectifies loose or damaged connections as per OEM guidelines and submits the report to the supervisor. | Theory-01 Hrs Practice-06Hrs Total- 7Hrs | - Insulation tape - Grid power cables - Busbars - breakers - Thermal imaging camera - Insulation resistance tester - Multimeter - Power circuit mock up | - Classroom - Lab |
| Maintain generator | - Check lubrication of generator bearings - Perform visual inspection of grounding straps - Perform tightness of control cable terminals inside terminal box - Perform tightness of power cable connections - Check slip ring tracks for wear - Replace phase/earthing slip ring carbon brushes as per OEM guidelines - Clean slip ring compartment for carbon dust and replace carbon dust filters as required - Check limit switches/sensors for carbon brush holders - Check alignment of generator as per OEM guidelines - Fill required checklist as per OEM guidelines - Submit results to supervisor | - Generator bearing lubrication methods and standards - Grounding systems, cable terminations, and connection tightness - Slip ring construction, wear inspection, and brush replacement procedures - Cleaning and maintenance of slip ring compartments and carbon dust filters - Limit switches, sensors, and alignment checks for generators Activity: The candidate is given a generator model. Inspects and lubricates generator bearings, checks grounding straps and cable connections, examines slip rings for wear, replaces carbon brushes, cleans the slip ring compartment and filters and submits the report to the supervisor. | Theory-01 Hrs Practice-09Hrs Total- 10Hrs | - Lubricants/grease - Carbon brushes - Carbon dust filters - Generator bearings, grounding straps, and slip rings - Grease gun - Torque wrench, - Laser alignment tool - Multimeter - Generator model | - Classroom - Lab |
| Maintain transformer | - Check oil level of transformer - Perform Insulation resistance test - Perform earth resistance test for grounding network - Check bushings, terminals, and grounding as per OEM standard - Remove rust from transformer body and connections, if required. - Apply paint on transformer body, if required. - Fill required checklist as per OEM guidelines - Submit results to supervisor | Components of transformer Principle of Insulation resistance test Grounding systems design and earth resistance testing procedures Corrosion control techniques Activity: The candidate checks transformer oil level, performs insulation and earth resistance tests, inspects bushings and terminals, removes rust and applies paint if required, completes the OEM checklist, and submits the report to the supervisor. | Theory-01 Hrs Practice-09Hrs Total- 10Hrs | - Transformer oil - cloths / rags - Rust remover - Paint - Brushes - Insulation Resistance Tester - Earth Resistance Tester - Oil level gauge - Hand tools | - Classroom - Lab |
| Maintain AC motor | - Perform visual inspection for external damage as per standards - Clean AC motor components according to standard procdure - Monitor sound of bearing - Perform insulation resistance test as per standard - Perform tightness of connections inside distribution box - Perform visual inspection of coupling - Perform functional test on motor as per standard - Report sound level through functional test as per standards - Fill required checklist as per OEM guidelines - Submit results to supervisor | - Inspection and Cleaning of Motor Components - Alignment of bearing. - Vibrational analysis. - Electrical testing - Mechanical testing - Performance Evaluation, and Reporting Activity: The candidate is required to perform visual inspection, cleaning, and connection tightness checks on a given AC motor training unit, conducts insulation resistance and functional tests and records results as per OEM checklist for onward submission to the supervisor. | Theory-01 Hrs Practice-06Hrs Total- 7Hrs | - Degreasing/cleaning solution - Insulation tape - Lubricants/grease - AC motor training unit - Insulation resistance tester - Torque wrench | - Classroom Lab |
| Maintain DC motor | - Perform visual inspection for external damage as per standard - Monitor sound of bearing - Perform insulation resistance test as per standard - Clean carbon deposits from commutators and field windings - Perform functional test on motor as per standard - Report sound level through functional test as per standards - Check worn brushes as per standard - Replace brushes, if required. - Fill required checklist as per OEM guidelines - Submit results to supervisor | - Construction of DC Motors - Thermal analysis - Abnormal noise in DC Motor - Alignment of bearing - Procedure of Winding test - Brushes, Commutators, and Field Windings Maintenance - Functional Testing and Performance Evaluation of DC Motors Activity: The candidate is required to inspect external damage, insulation resistance, commutators and windings. If there is any damage it will be replaced as per checklist for onward submission to supervisor. | Theory-01 Hrs Practice-06Hrs Total- 7Hrs | - Carbon brushes - Degreasing - Tape - DC motor (training/operational unit) - Multimeter - Insulation resistance tester - Torque wrench | - Classroom Lab |
| Maintain switchgear | - Check switchgear, circuit breakers, and isolators at tower base - Check mechanical interlocks test as per standard - Check mechanical operation as per standard - Check protective relays. - Check tightness of connections - Check lubrication of moving parts - Fill required checklist as per OEM guidelines - Submit results to supervisor | - Principles of Switchgear - Components of Circuit Breakers and Isolators - Mechanical Interlocks - Protective Relays - Overview of switchgear connections Activity: The candidate is given a switchgear model. Inspect switchgear for damages, tests mechanical interlocks and protective relays and submits results to the supervisor. | Theory-0.5 Hrs Practice-09Hrs Total- 9.5Hrs | - Cleaning agent - Lubricants - Tape - Switchgear assembly training unit - Multimeter - Relay testing kit - Torque wrench | - Classroom Lab |
| Maintain frequency convertor | - Check power converter modules for abnormality - Perform cleaning of cooling fans. - Perform functional test on cooling fans - Perform cleaning of filters. - Check power wiring connections for damage - Check control wiring connections for damage - Fill required checklist as per OEM guidelines - Submit results to supervisor | - Principle of Frequency Converters - Power Converter Modules - Cooling Systems in Frequency Converters - Standards and Testing Activity: The candidate is given a training model of frequency convertor. Inspects power converter modules, cleans and tests cooling fans and filters, checks wiring connections for damage,and submits results to the supervisor. | Theory-0.5 Hrs Practice-09Hrs Total- 9.5Hrs | - Compressed air canisters or blower - Contact cleaner spray - cooling filters - Frequency converter training unit - Multimeter - Insulation resistance tester - Screwdrivers | - Classroom Lab |

### 4.11 0713E&E4509 Conduct Preventive Maintenance of Hydraulic Systems

Objective: This module covers the skills and knowledge required to perform preventive maintenance of hydraulic systems in accordance with industry standards. It emphasizes identifying maintenance needs, inspecting components, and carrying out servicing tasks to maintain reliability and efficiency. The underpinning knowledge of hydraulic system functions and maintenance practices provides the basis for effective performance at the workplace.

Duration: 73 Hours			Theory: 07 Hours				Practice: 66 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Maintain pumps | - Replace hydraulic filters of pumps - Perform hydraulic oil sampling, if required. - Verify system pressure. - Inspect body, seals, connections for damage. - Measure vibration, temperature and noise to detect abnormalities. - Confirm lubrication and cooling systems function properly. - Record inspection results and report it. | - Types of hydraulic pump filters - Process of hydraulic oil sampling - Overview of Hydraulic system pressure - Cooling and lubrication system - Introduction to Hazard Report Activity: Candidate is required to measure vibration, temperature and noise of a given hydraulic pump training model. and verify functionality of lubrication system in it and record results in an inspection report.. | Theory-01Hrs Practice-12Hrs Total- 13Hrs | - Hydraulic filters - Hydraulic oil (top-up/refill) - Temperature gun - Noise meter | - Classroom - Lab |
| Maintain valves | - Inspect components for wear, corrosion, damage. - Verify sealing integrity to prevent leakage. - Monitor pressure and flow control within limits. - Confirm correct actuation under all conditions. - Verify protective devices remain functional and calibrated. - Record inspection results and report it. | - Overview of valve components - Protective device functionality and calibration Activity: Candidate is required to check seal and monitor pressure of given valves training model and confirm protective devices on the valves and record results in an inspection report. | Theory-0.5Hrs Practice-12Hrs Total- 12.5Hrs | - Tags - Lubricants and hydraulic oil - Seals and gaskets | - Classroom - Lab |
| Maintain actuators | - Inspect housings, seals, connections for damage. - Verify response times, positioning accuracy within limits. - Check vibration, temperature, power consumption for damage. - Confirm lubrication and fluid supply are adequate. - Record inspection results and report it | - Types of Actuator housing, seals, and connections - Overview of Response time and positioning accuracy - Condition of Actuators - Overview of lubrication and fluid supply Activity: Candidate is required to inspect housings, seals and connector of a given actuator training model, monitor operating parameters and check lubrication supply and record results in an inspection report. | Theory-0.5Hrs Practice-12Hrs Total- 12.5Hrs | - Seals and gaskets | - Classroom - Lab |
| Maintain accumulators | - Adjust pre-charge pressure within limits. - Verify fluid quality and cleanliness. - Inspect body, seals and connections for leaks or damage. - Monitor pressure stability and response. - Verify protective devices are functional and calibrated. - Record inspection results and report it | - Procedure of pre-charge pressure adjustment - Accumulator body, seals, and connections - Pressure stability and response Activity: Candidate is required to adjust pre-charge pressure and check fluid quality of a given accumulator training model. Monitor pressure stability and verify protective devices and record results in an inspection report. | Theory-01Hrs Practice-12Hrs Total- 13Hrs | - Nitrogen gas | - Classroom - Lab |
| Maintain hydraulic sensors | - Inspect housings, seals, connectors for damage or leaks. - Maintain clean, secure connections to prevent faults. - Monitor output trends for drift, noise, fluctuations. - Confirm accurate data transmission to control systems. - Record inspection results and report it. | - Types of sensor housing, seals, and connector - Overview of connection cleaning and security - Output trend and abnormalities - Introduction to data transmission Activity: Candidate is required to inspect housings, seals and connectors of a given hydraulic sensor training model. Monitor output signals and verify data transmission and record results in an inspection report. | Theory-01Hrs Practice-12Hrs Total- 13Hrs | - Seals and gaskets | - Classroom - Lab |
| Check pipe connections | - Inspect joints and fittings for leaks or cracks. - Verify connection torque meets requirements. - Check seals and gaskets for wear or misalignment. - Inspect pipes, fittings for corrosion or damage. - Monitor supports and clamps for secure positioning. - Record inspection results and report it | - Types of Joints and fittings - Overview of Connection torque - Types of seal and gasket - Condition of pipes and fittings Activity: Candidate is required to inspect joint, seals and clamps of given pipe connections. Verify torque and identifying any corrosion or damage, and record results in an inspection report. | Theory-03Hrs Practice-06Hrs Total- 9Hrs | - Tags - Borescope | - Classroom - Lab |

### 4.12 0713E&E4510 Implement Corrective Maintenance of Wind Power Plant

Objective: This module covers knowledge and skills required to perform corrective maintenance of Wind power plant systems. The underpinning knowledge will be sufficient to provide the basis for the job at workplace.

Duration: 62 Hours			Theory: 08 Hours				Practice: 54 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Perform replacement of brake pad | - Remove old brake pads as per specifications - Inspect caliper for wear and tear. - Install new brake pads as per specifications - Perform brake function testing - Submit faulty component to supervisor | - Introduction to brake pad materials - Overview of rigging arrangement for yaw calipers - Functional test of brake pad Activity: Candidate is required to replace a brake pad on training model of yaw system. Submit the report of findings. | Theory-1Hrs Practice-06Hrs Total- 7Hrs | - Brake pad mock up - Yaw system model | - Classroom - Workshop |
| Perform replacement of brake calipers | - Isolate hydraulic system. - Remove hydraulic pipes as per specifications - Dismount defective caliper - Install new caliper as per specifications - Reconnect hydraulic pipes - Perform Test operations - Inspect for leaks. - Submit faulty component to supervisor | - Introduction to brake calipers - Components of brake calipers - Pressure in brake calipers Activity: Candidate is required to disassemble and assemble given yaw brake caliper training model and prepare report of findings. | Theory-1Hrs Practice-06Hrs Total- 7Hrs | - Yaw brake caliper training model - Seals | - Classroom - Workshop |
| Perform replacement of motor | - Diagnose faulty motor. - Disconnect electrical supply. - Dismantle faulty motor - Install new pitch motor as per specifications - Reconnect wiring as per diagram. - Calibrate blade angle after motor replacement - Perform functional test - Submit faulty component to supervisor | - Types of motors - Motor wiring - Motor diagnosing test - Overview of coupling arrangements with gearbox/drive - Rigging technique Activity: Candidate is required to diagnose fault in a given motor mockup and perform replacement of motor with correct wiring attachment. | Theory-01Hrs Practice-06Hrs Total- 07Hrs | - Motor mockup - torque tools. | - Classroom - Workshop |
| Perform replacement of low voltage circuit breaker | - Identify faulty breaker - Isolate affected circuit - Remove defective breaker as per specifications - Install correct rating breaker as per specifications - Perform breaker test operation - Submit faulty component to supervisor | - Types of low voltage circuit breakers - Procedure of breaker installation - Functional test of breaker. Activity: Candidate is required to identify faulty breaker from a given circuit and perform replacement of breaker and test functionality. | Theory-01Hrs Practice-06Hrs Total- 07Hrs | - Low voltage circuit breakers | - Classroom - Workshop |
| Perform replacement of low voltage cable | - Identify faulty cable - Isolate circuit - Remove damaged cable as per specifications - Install new cable as per specifications - Terminate and label ends - Perform continuity test - Submit faulty component to supervisor | - Types of low voltage cables - Overview of single line diagram - Diagnostic test for cables Activity: Candidate is required to identify faulty cables through given single line diagram and perform diagnostic test on the cable. Replace faulty cables and submit a report with findings. | Theory-01Hrs Practice-06Hrs Total- 07Hrs | - Electrical cables - Crimping/termination tools | - Classroom - Workshop |
| Perform replacement of control cables | - Identify faulty cable. - isolate circuit. - Remove damaged cable as per specifications - Install new control cable as per specifications - Terminate and label ends. - Perform continuity check. - Verify control signal function. - Submit faulty component to supervisor | - Types of control cables - Loop testing of control cables - Control cable replacement procedure Activity: Candidate is required to identify faulty cable in a given circuit and perform replacement of the cable. Verify signal communication and submit a report with findings | Theory-01Hrs Practice-06Hrs Total- 07Hrs | - Termination tools - Control cables. - Continuity tester | - Classroom - Workshop |
| Perform rectification of oil leakage | - Identify source of leak. - Tighten pipes / fittings - Replace seals or gaskets if required - Clean oil spill area, if any. - Identify correct oil to be used - Refill system to correct level. - Run system and monitor for leaks. - Dispose waste oil safely. - Submit faulty component to supervisor | - Leakage identification procedure - Understand leakage sources - Types of seals and replacement techniques Activity: Candidate is required to identify source of leakage from the given gearbox training model and replace required gasket and also refill oil. | Theory-01Hrs Practice-06Hrs Total- 07Hrs | - Gear Oil | - Classroom - Workshop |
| Perform rectification of control circuits | - Identify abnormality on control panel - Check output of control relays for abnormality - Check output of timers for abnormality - Check output of transformer for abnormality - Check output of switches for abnormality - Check output of circuit breaker for abnormality - Check output of PLC module for abnormality - Perform loop testing of cables for abnormality - Check wiring, terminals and corrections for damage - Replace required component - Submit faulty component to supervisor | - Types of control circuits within wind turbines - Diagnostic test for relay - Diagnostic test for PLC faults. - Diagnostic test for contactors Activity: Candidate is required to tace fault in a give control circuit mockup and replace required component. Submit a report with findings. | Theory-0.5Hrs Practice-06Hrs Total- 6.5Hrs | - Control panel mock-up | - Classroom - Workshop |
| Perform replacement of sensors | - Identify abnormality on control panel - Remove connections from faulty sensor - Perform tagging of removed connection - Remove faulty sensor - Install new sensor - Perform functional test on sensor - Submit faulty component to supervisor | - Types of sensors within wind turbine - Diagnostic test of sensor - Functional test of sensor Activity: Candidate is required identify faulty sensor in the given control panel mock up and replace faulty sensor and test operation. Submit report with findings. | Theory-0.5Hrs Practice-06Hrs Total- 6.5Hrs | - Control panel mockup - Sensors | - Classroom - Workshop |

### 4.13 0713E&E4511 On-Job Training

Objective

The on-the-job training component of this qualification provides learners with the opportunity to apply their acquired skills and knowledge in a real-world environment. During this phase, students are expected to take on entry-level or support roles, such as that of a Wind Power Plant Technician. These roles may span across sections including operations, maintenance of wind power plant enabling learners to contribute to power generation while meeting the requirements of the qualification.

In case of unavailability of relevant industry for OJT, a project may be carried out for the fulfilment of OJT requirement.

- List of Consolidated Consumables, Tools, Machinery & Equipment

| 5A. List of Consolidated Consumables |  |  |
| --- | --- | --- |
| Serial No. | Item | Qty. Required |
| 1 | PPEs | 25 Sets |
| 2 | Oil Absorbing Pads | 25 Nos |
| 3 | Labels (LOTO Tags, Hazard Labels) | 25 Sets |
| 4 | Printing Paper, Drawing Sheets | 25 Sets |
| 5 | Cartridge/ Ink for Printer | 02 No.s |
| 6 | Small Replacement Parts (fuses, connectors, cable Lugs, Seals, gaskit etc) | 25 No.s |
| 7 | Cleaning and Lubricants (Oil, Grease, cleaning agents) | 02 Sets |

| 5B. Consolidated List of Tools, Machinery & Equipment |  |  |
| --- | --- | --- |
| Serial No. | Item | Qty. Required |
|  | Personal Computer with Basic Accessories | 25 |
|  | Internet Connection | 10 MB |
|  | Projector / Multimedia System / Whiteboard | 1 |
|  | MS Office Suite | 1 |
|  | SCADA Interface / Simulator | 1 |
|  | Printers / Plotters | 1 |
|  | Technical Drawings of Wind Turbine Systems (Mechanical, Electrical, Civil, Hydraulic) | 1 of each type |
|  | Manufacturer’s Technical Manuals & Specification Sheets | 2 |
|  | Engineering Handbooks & Drafting Standards | 1 set |
|  | Drawing Tools | 25 |
|  | Calculators | 10 |
|  | Measurement Conversion Charts / Tables | 5 |
|  | Symbol Reference Booklets / Handouts | 25 |
|  | Light Tables / Magnifying Tools | 5 |
|  | PPEs | 5 sets |
|  | Fire Extinguishers | 1 |
|  | First Aid Kits | 1 |
|  | High-Rise Ladder Climbing Gear | 5 |
|  | Fall Protection Kits (Full Body Harness, Lanyard, Anchor Point) | 5 |
|  | Emergency Rescue Kits (Rope, Pulley, Helmet with Chinstrap) | 5 |
|  | Communication Devices (Walkie-Talkie / Headsets) | 5 |
|  | Lockout–Tagout (LOTO) Kits | 5 |
|  | Hazard Signs | 1 set |
|  | Spill Control Kit (including Oil Absorbing Pads) | 1 set |
|  | Waste Container Bins (segregated categories) | 1 set |
|  | Gas Leakage Detector | 1 |
|  | Digital Multimeter | 5 |
|  | Clamp Meter (AC/DC) | 5 |
|  | Insulation Resistance Tester (Megger) | 5 |
|  | Earth / Ground Resistance Tester | 5 |
|  | Phase Sequence / Rotation Tester | 5 |
|  | Oscilloscope | 2 |
|  | Power Analyzer | 2 |
|  | Thermal Imaging Camera / IR Tester | 5 |
|  | Contact Resistance Tester | 5 |
|  | Vibration Meter / Analyzer | 5 |
|  | Sound Level Meter | 1 |
|  | Mechanical Tool Kits (complete sets) | 1 |
|  | Electrical Tool Kits (complete sets) | 1 |
|  | Screwdriver Sets (Insulated) | 5 |
|  | Combination Pliers / Insulation Pliers | 5 |
|  | Adjustable Wrenches | 5 |
|  | Spanner Sets | 5 |
|  | Cable Strippers | 5 |
|  | Crimping & Termination Tools with Lugs | 10 |
|  | Torque Wrenches (Mechanical & Electrical Use) | 10 |
|  | Soldering Irons | 3 |
|  | Laser Alignment Tool | 1 |
|  | Vernier Caliper | 1 |
|  | Screw Gauge | 1 |
|  | Measuring Tape | 1 |
|  | Pressure Gauges (Hydraulic) | 5 |
|  | Flow Meters | 5 |
|  | Hydraulic Fluid Tester / Sampling Kits | 5 |
|  | Nitrogen Charging Kits for Accumulators | 2 |
|  | Calibration Kits (for Hydraulic Sensors) | 2 |
|  | Seal & Gasket Inspection Tool Sets | 10 |
|  | Pipe Wrenches & Fitting Tool Sets | 10 |
|  | Lubrication Equipment (Grease Guns, Oilers, etc.) | 5 sets |
|  | Maintenance Logbooks / Digital Recorders | 25 |
|  | General Sampling Kits | 1 |
|  | Lifting Equipment (Slings) | 1 set |

# Members of Qualification Development Committee

The Qualifications Development Committee consisted of the following members:

| Sr. No. | Name | Designation | Organization |
| --- | --- | --- | --- |
| 1. | Abdul Moeez | DACUM Facilitator, | RMC Lahore |
| 2. | Hasan Hameed Malik | Executive. Tech | FFC ENERGY |
| 3. | Engr. Dr. Waqas Abdul Salaam | Assistant Director, | Govt. Centre of Excellence (GSTC) Mughal Pura Lahore |
| 4. | Engr. Muhammad Naveed | Lecturer Electrical | GPI Takht Bhai KP_TEVTA |
| 5. | Muhammad Shoaib | Jr. Instructor | GCT Kohat KP-TEVTA |
| 6. | Engr.Babar Noor | Assistant Professor | KP TEVTA |
| 7. | M. Usman Mujahid | Instructor | Vocational Training Institue Toba |
| 8. | Haris Bin Khalid | Sr. Executive | FFC Energy |
| 9. | Abdul Haseeb Imtiaz | Service Engineer | Jaffar Brothers Pvt. Limited |
| 10. | Muhammad Rashid Mansoor | Electrical Engineer | ITU Lahore |
| 11. | Muhammad Asim | Sr. Scientific Officer | PCSIR Islamabad |
| 12. | Iraj Rashid | Coordinator | NAVTTC |