National Vocational Certificate Electrical Technology (Domestic/General Electrician) Level-2

Curriculum

National Vocational and Technical Training Commission (NAVTTC)

Government of Pakistan

FOREWORD

National Vocational and Technical Training Commission (NAVTTC) extends its gratitude and appreciation to representatives of business, industry, academia, government agencies, provincial TEVTAs, sector skill councils and trade associations who spared time and extended their expertise for the development of National Vocational Qualification for Electrical Technology (Domestic/General Electrician) Level-2. This work was made possible with the technical support of the experts.

This curriculum has been designed in line with the vision of Pakistan’s National Skills Strategy (NSS), National TVET Policy, and the National Vocational Qualification Framework (NVQF). It addresses the demand of employers in the electrical sector while promoting green practices to meet international labor market requirements.

The curriculum provides structured learning outcomes, theory topics, and practical activities to equip trainees with knowledge, skills, and attitudes necessary for sustainable and environmentally responsible practices in electrical works.

It not only develops technical competencies but also integrates green skills, enabling trainees to minimize waste, conserve energy, and adopt renewable resources in their professional practice. The curriculum ensures alignment with NVQF pathways, supporting vertical career progression and equivalencies at par with international standards.

Ultimately, the purpose of this curriculum is to transform trainees into skilled, responsible, and employable graduates who can contribute to Pakistan’s social and economic development while meeting the expectations of both the domestic and international markets.

Executive Director (NAVTTC)

Table of Contents

1.	Introduction	4

1.1.	Date of Development	5

1.2.	Date of Review and Validation	5

1.3.	Entry Requirement	5

1.4.	Minimum qualification for teachers	5

1.5.	Medium of instruction	5

1.6.	Duration of Course	5

Overall objectives of training program	5

2.	Scheme of Studies	6

3.	Overview of the Curriculum for (Domestic/General Electrician) Level-2	6

4.	Details of Modules	8

0713E&E1 Follow Occupational Health and Safety Practices	8

0713E&E2	Demonstrate Basic Communication Skills	17

0713E&E3 Prepare Estimates for Electrical Work	20

0713E&E4 Follow basic green practices for Domestic/General Electrician	23

0713E&E5 Install single-phase Electrical wiring.	30

0713E&E6 Perform Testing of Electrical Wiring	42

0713E&E7 Install Security & Electrical Communication Systems	63

1.	List of Tools and Equipment (For a Class Of 25 Students)	68

2.	Members of Qualification Development Committee	74

# Introduction

G

reen skills incorporation in TVET aims to build capacity of skilled workforce, which is aware of environmental hazards and accordingly adopts more sustainable and environment friendly practices at the workplace. The workforce that possesses competencies and relevant knowledge & understanding oriented to green occupations is more employable and become an asset for businesses, enterprises and communities in developing green economies that results in improved human well-being and reducing environmental risks.

The United Nation’s Sustainable Development Goals (SDGs), UNESCO ESD initiatives UNEVOC, ILO, CPSC and ADB guidelines, studies and training manuals provide comprehensive green skill strategies to develop competencies / skills that can be imparted under vocational education and training. They are focused to prepare the workforce to adopt sustainable practices and address environmental degradation by appropriately managing human and material resources.

The vocational professions are increasingly getting attention in Pakistan, not only among the youth seeking to enter in the job market but also among adults who wish to polish their skills to develop a career out of it. The scope and demand of Domestic or General Electrician is very high in Pakistan due to fast growing population and construction projects in Pakistan. There are more job opportunities for electricians in Pakistan than any other vocational field. Pakistan is still facing energy crises, therefore needs more power houses, dams, renewable energy sources, solar installations etc. which will result in more demand of electrical technicians. Pakistan can boost economic growth and job creation by overcoming inefficiencies in its power sector. Power sector reforms that address these distortions can make better use of existing facilities. These need to focus on eliminating waste, promoting the shift towards cleaner energy and attracting private investments.

The Government of Pakistan through National Vocational & Technical Training Commission (NAVTTC) in collaboration with German Development Company & BMZ has revised the national vocational qualifications for NVQF level 1 to Level 3 in Electrical Technology with greening concepts, which not only allows trainees to equip with growing Industrial trends but will be beneficial in Rapidly capturing the job market across the globe.

This document identifies competencies related to electrician trade identified by the relevant industry during workshops held at Lahore Chamber of Commerce & Industry, Lahore. These skills either can be infused as a separate competency standard / competency unit in relevant qualifications or can be integrated as a separate module in the qualifications already developed or being developed under growth economic sectors. Critical evidence statements have also been added to assist assessors in preparation and conduct of assessment. The purpose of this document is to bring change in abilities, values and attitudes needed by human to support the sustainable and effective utilization of resources in the workplace. It focuses on the skills that will help preserve and conserve the environment. If qualifications implemented by training providers, will directly benefit the poor by increasing access, improving reliability, and reducing cost and pollution.

This qualification can create a considerable impact in electrical field especially in the following areas:

- Energy saving infrastructures

- Renewable Energy

- Building Automation

- Energy Network Management

- e-Vehicles

- LED Illumination

- Solar Energy

Structural changes will realign sectors that are likely to decline as a result of the greening of the economy and workers will need to be retrained accordingly. The successful transition to a low-carbon economy will only be possible if workers can flexibly adapt and practice to go green as per their industry standards.

| ## Date of Development | 25th – 30th August, 2025 |
| --- | --- |
| ## Date of Review and Validation | The Qualification has been validated by the Qualifications Validation Committee (QVC) members on 30 August, 2025 and will remain valid for ten years i.e. 29 August, 2035. and shall be reviewed after three years i.e. 29 August, 2028. |
| ## Entry Requirement | The entry level for this Qualification is Middle Grade 8 certificate /Preferably Matric. |
| ## Minimum qualification for teachers | - B.Sc. Engineering and 2 years of relevant work experience; or - B-Tech and 3 years of relevant work experience; or - Diploma Associate Engineer (DAE) and 5 years relevant work experience; or - Certificate as Electrical G-II with 8 years relevant work experience |
| ## Medium of instruction | Urdu/English |
| ## Duration of Course | Total. 600 hours. Theory. 120 hours Practical. 480 hours |

# Overall objectives of training program

0713E&E0201	Follow Occupational Health and Safety Practices

0713E&E0202	Demonstrate Basic Communication Skills

0713E&E0203	Prepare Estimates for Electrical Work

0713E&E0204	Follow basic green practices for Domestic/General Electrician

0713E&E0205	Install single-phase Electrical wiring.

0713E&E0206	Perform Testing of Electrical Wiring

0713E&E0207	Install Security & Electrical Communication Systems

# Scheme of Studies

| Module Code | Name of Competency | NVQF Level | Category | Contact Hour |  |  | Credit |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Th. | Pr. | Total |  |
| 0713E&E0201 | Follow Occupational Health and Safety practices | 2 | Functional | 8 | 32 | 40 | 4 |
| 0713E&E0202 | Demonstrate basic communication skills | 2 | Generic | 12 | 38 | 50 | 5 |
| 0713E&E0203 | Prepare estimates for electrical work | 2 | Functional | 16 | 64 | 80 | 8 |
| 0713E&E0204 | Follow basic green practices for Domestic/General Electrician | 2 | Generic | 8 | 32 | 40 | 4 |
| 0713E&E0205 | Install Single Phase Electrical Wiring | 2 | Technical | 60 | 250 | 310 | 31 |
| 0713E&E0206 | Perform Testing of Electrical Wiring | 2 | Technical | 8 | 32 | 40 | 4 |
| 0713E&E0207 | Install Security and Electrical Communication systems | 2 | Technical | 8 | 32 | 40 | 4 |
| Total |  |  |  | 120 | 480 | 600 |  |

# Overview of the Curriculum for (Domestic/General Electrician) Level-2

| Module Title | Learning Units | Theory hours | Workplace hours | Timeframe of modules |
| --- | --- | --- | --- | --- |
| 0713E&E0201 Follow Occupational Health and Safety Practices | - Use of personal protective equipment (PPE) - Maintain First-aid Box - Operate Fire Extinguisher - Ensure Safeguard of Machines - Adopt company policies and procedures - Attain health & safety training - Prepare for emergencies - Respond to emergencies | 8 | 32 | 40 |
| 0713E&E0202 Demonstrate Basic Communication Skills | - Work in Team - Deal with Clients - Demonstrate Basic IT Skills | 12 | 38 | 50 |
| 0713E&E0203 Prepare Estimates for Electrical Work | - Develop Basic Drawing - Perform Estimation of material - Calculate Labor Cost | 16 | 64 | 80 |
| 0713E&E0204 Follow basic green practices for Domestic/General Electrician | - Help in organizing working environment - Perform disposal of electrical waste in designated area as per SOP - Reuse training material (consumables) - Comprehend knowledge of Renewable Energy Recourses - Practice Green Skills at Workplace | 8 | 32 | 40 |
| 0713E&E0205 Install single-phase Electrical wiring. | - Maintain Tools & Equipment for Single Phase Wiring - Make Cable/Wire Joints for Single Phase Wiring - Prepare and Install Distribution Boards for Single Phase - Lay cables - Practice single phase electrical circuit - Perform single phase electrical domestic wiring. | 60 | 250 | 310 |
| 0713E&E0206 Perform Testing of Electrical Wiring | - Perform Earth leakage Test. - Perform Open Circuit Test - Perform Short Circuit Test - Perform Continuity/Loop Test - Perform Visual Test - Perform Insulation Test - Perform Polarity Test - Perform Earth Resistance Test - Perform Murray - Perform BLAVIER & Earth Loop Test | 8 | 32 | 40 |
| 0713E&E0207 Install Security & Electrical Communication Systems | - Select the type of Safety / Security & Communication System - Install Safety / Security & Communication System - Test the Installed system | 8 | 32 | 40 |
| Total |  | 120 | 480 | 600 |

# Details of Modules

## 0713E&E0201-Follow Occupational Health and Safety Practices

Objective:

After this Module, the Trainee will be able to develop skill and competence required to maintain Occupational Health and Safety and take remedial measures to deal with the emergencies in a professional manner, thus minimizing the losses and providing a safe and healthy working environment. The learner will also be able to practice green skills and become more environment friendly.

Duration: 40 Hours	Theory: 8 Hours	Practice: 32 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required |  | Learning Place |
| --- | --- | --- | --- | --- | --- | --- |
| Use of personal protective equipment (PPE) | - Arrange the required personal protective equipment - Check functional condition of PPE’s - Wear personal protective equipment - Store PPE at appropriate place after use. | - Importance of Occupational Health & Safety at workplace - Workplace hazards & risk identification. - Safety signs & its types (Mandatory, Prohibition, Warning, Emergency) - Personal Protective Equipment (PPE): types, uses, storage, disposal Practical Activity - Identify and enlist risk associated with job to be done at workplace/lab - Select PPE's according to job - Check PEEs for any damage - Wear PPEs according to job - Store PPEs at Designated place after use | Theory: 1Hr Practical: 4Hrs Total: 5Hrs |  | - Safety Helmet - Safety Goggles - Face Shield - Insulated Gloves - Safety Shoes - Ear Protection (Ear Muffs / Ear Plugs) - Dust Mask - Safety Harness - High-visibility Jacket - Apron - Insulated Mats - Safety Sign Boards - PPE Storage Cabinet Consumable Items: - Safety Posters - Disposable Gloves - Disposable Masks - Hand Sanitizer Bottles (500 ml) - Disinfectant Spray - Floor Safety Marking Tape - Cleaning Cloth | - Classroom and workshop |
| Maintain First-aid Box | - Ensure availability of first aid box - Check requisite first aid box for emergency - Check expiry of medicines - Perform first aid treatment against electric shocks - Perform first aid treatment/bandages against minor injuries. - Develop a waste management plan for first aid supplies, including proper disposal hazardous materials. - Promote the use of recyclable materials in the procurement of first-aid box. | - Importance of first-aid box at workplace. - Emergency medicines (Name, Type, Use) and to check expiry dates. - Waste management plan & disposal of hazardous materials. - Basics of electric shock and minor injury treatment. ### Practical Activity - Identify first aid box - Check first aid box for requisite emergency items - Check expiry of medicines - Perform first aid treatment against electric shocks / minor injuries. | Theory: 1Hr Practical: 4Hrs Total: 5Hrs |  | - First Aid Box - Scissors (medical) - Tweezers - Torch Consumable Items: - Cotton Rolls - Antiseptic Solution (Dettol) - Pyodine Solution - Antiseptic Cream - Ointment - Burn cream - Pain Relief Spray / Gel - Sterile Gloves (disposable) - Adhesive Tape / Medical Tape - Elastic Bandages (crepe bandages) - Burn Dressing / Burn Gel Packs - Instant Cold Pack - Medicines (Pain killers, ORS, etc.) - Expiry Checklist Sheet & Pen | - Classroom and workshop |
| Operate Fire Extinguisher | - Asses the fire situation. - Select the fire extinguisher based on the type and size of the fire. - Verify the working condition of the fire extinguisher, ensuring it is properly pressurized and has a vilid inspection tag or seal. - Apply appropriate fire extinguishing technique such as using the PASS method (Pull, Aim, Squeeze, Sweep) for extinguishing the small fire - Check expiry of fire extinguisher - Operate fire extinguisher | - Types of fire (A, B, C, D, K). - Types of fire extinguishers (CO₂, Dry Powder, Foam, Water). - PASS method (Pull, Aim, Squeeze, Sweep). - Fire extinguisher inspection (Expiry, Pressure Guage, Tempering, Corrosion and Blockage) ### Practical Activity - Carry out visual inspection of the fire extinguisher. - Check that fire extinguisher has not been used or tempered with - Take a pressure gauge reading. - Remove the discharge HOSE to check for corrosion and blockage. - Clean the Fire Extinguisher - Verify wall Mountings are secure. - Operate the Fire Extinguisher | Theory: 1Hr Practical: 4Hrs Total: 5Hrs |  | - Fire Extinguishers (Water, CO₂, Dry Powder, Foam type – for training use) - Pressure Gauge (built-in on extinguisher) - Spanner (for checking hose connection & mountings) - Discharge Hose (attached with extinguisher) - Torch (for visual inspection of corrosion & leaks) - Personal Protective Equipment (Safety Gloves, Safety Goggles, Dust Mask) - Secure Wall Mountings / Brackets for extinguishers Consumable Items: - Inspection Tag - Checklist Sheets - Cleaning Cloth - Mild Detergent / Cleaning Solution - Wire Brush (for corrosion removal, if allowed in demo) | - Classroom and workshop |
| Ensure Safeguard of Machines | - Maintain radiator shield - Maintain alternator fan shield - Maintain heat resister material on silencer - Cover main circuit breaker - Lock canopy doors | - Importance of guards on electrical machines. - Safety shields (radiator, alternator fan, silencer). - Safety practices related to circuit breaker safety. Practical Activity - Practice routine maintenance checks and ensure safeguard of machines | Theory: 1Hr Practical: 4Hrs Total: 5Hrs |  | - Electrician Tool Kit - Torque Wrench (for tightening shields/covers) - Protective Gloves (Heat-resistant and Electrical) - Safety Goggles - Face Shield - Circuit Breaker Cover (Protective enclosure) - Torch Consumable Items: - Cleaning Cloths - Brushes - Lubricating Oil - Grease (for moving parts if required) | - Classroom and workshop |
| Adopt company policies and procedures | - Ensure company’s safety policy - Adopt company safety procedure - Advocate worker with company safety policy - Implement Safety sign board as per standard | - Key elements of a Company’s Safety Policy at Electrical workplace. Practical Activity - Develop a layout plan for safety of workplace - Prepare an emergency plan for workplace hazards. | Theory: 1Hr Practical: 4Hrs Total: 5Hrs |  | - Company Safety Policy Manual / Documents - Safety Procedures Handbook - Safety Sign Boards (Danger, Caution, High Voltage, Fire Exit, No Smoking, etc.) | - Classroom and workshop |
| Attain health & safety training | - Take required health and safety training - Implement work hazardous material information system (WHMIS) - Adopt first aid cardio respiratory, resuscitation and CPR | - Importance of continuous training in Health & Safety. - WHMIS (Workplace Hazardous Material Information System). - Importance and Procedure of CPR and resuscitation. Practical Activity - Practice CPR (Cardio Pulmonary Resuscitation) | Theory: 1Hr Practical: 4Hrs Total: 5Hrs |  | - CPR Manikin (Adult) - CPR Manikin (Child/Infant) - AED (Automated External Defibrillator) Training Unit (Demo) - Training Mat (for manikin practice on floor) - Stopwatch / Timer (for chest compression timing practice) - Multimedia / Video Module (for demonstration) Consumable Items: - Disposable CPR Pocket Mask / Face Shield - Disposable Gloves - Antiseptic Wipes | - Classroom and workshop |
| Prepare for emergencies | - Take emergency response training - Ensure practice of emergency exercises - Check the emergency alarms - Ensure regular practice of gathering the workers in assembly area during the emergency. | - Types of emergencies (fire, electric shock, equipment failure, natural disaster). - Importance of emergency response training. - Role of alarms and assembly points. Practical Activity - Conduct a mock emergency evacuation drill. - Test workshop emergency alarms. - Practice gathering in assembly area. | Theory: 1Hr Practical: 4Hrs Total: 5Hrs |  | - Emergency Alarm System (Sirens / Bells / Flash Alarms) - Fire Alarm Switch / Manual Call Point - Public Address (PA) System / Megaphone - Emergency Exit Signs (illuminated / glow type) - Assembly Area Signage / Marking Boards - Safety Cones or Barricade Tape (to guide evacuation route) - Stopwatch / Timer (to record evacuation time) - Whistle (for evacuation command) Consumable Items: - Emergency Drill Log Sheets / Checklists - Marking Chalk / Tape (for temporary route markings) | - Classroom and workshop |
| Respond to emergencies | - Follow emergency plan - Communicate instructions to co workers - Assess risk and determine course of action - Operate emergency equipment and supplies - Ensure that the ambulance is at stand by(for emergency) | - Steps to follow in an emergency plan. - Instructions to communicate with co-workers during emergencies. - Role of ambulance/first responders. Practical Activity - Perform emergency exercise. - Follow emergency plan - Operate emergency equipment and supplies | Theory: 1Hr Practical: 4Hrs Total: 5Hrs |  | - Emergency Alarm System (siren, hooter, strobe lights) - Fire Extinguishers - First Aid Box - Emergency Exit Signs - Emergency Lighting / Torch / - Megaphone - Whistle - Rescue Tools (fire blanket, safety hook, crowbar) - Assembly Area Sign Board Consumable Items: - Emergency Drill Log Sheets / Checklists | - Classroom and workshop |

## 0713E&E0202-Demonstrate Basic Communication Skills

Objective:

This Module identifies the competencies required to apply communication skills at workplace in accordance with the organization’s guidelines and procedures. You are expected to work in a team to achieve common organizational goals and avoid conflicts. This competency standard would also enable you to use basic computer skills to communicate effectively and prepare work related documents and reports. This module also focuses on establishing a green environment by adopting paperless communication medium and emphasis more on digital skills.

Duration: 50 Hours	 Theory: 12 Hours	Practice: 38 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Work in Team | - Treat team members with respect and maintain Positive relationships to achieve common organizational goals. - Note the instruction. - Comply with the Instructions - Identify interrelated work activities to avoid confusion - Adopt communication skills appropriate to work activities and company procedures - Identify problems and resolve them through discussion and mutual agreement. | - Team dynamics (roles of team members, stages of team development). - Respectful workplace behavior and positive team relationships. - Importance of following instructions and teamwork for achieving goals. - Principles of effective communication (7 C’s of Communication). - Organizational practices for effective communication. - Conflict resolution strategies. Practical Activity - Group discussion activity to practice respectful listening and speaking. - Role-play on following supervisor’s instructions. - Team project: plan and complete a small task (e.g., wiring layout discussion). - Activity on identifying interrelated tasks and sequencing them. - Role-play on resolving conflicts between team members. | Theory: 4Hrs. Practical: 10Hrs. Total: 14Hrs. | - Task Cards (with supervisor’s instructions or role-play scenarios) - Stopwatch (for timed group activities) - Camera (optional, for feedback & review of role-play) Consumable Items: - A4 / Chart Papers - Notebooks & Pens/Pencils - Sticky Notes - Printed Role-Play Scenarios / Instruction Sheets - Masking Tape / Markers (for task sequencing activity) | - Classroom and workshop |
| Deal with Clients | - Collect Demand from clients. using appropriate communication procedures - Negotiate with client regarding wages, time, and labor requirements. - Develop consensus with the Clint. | - Effective communication procedures with clients. - Client handling skills (listening, questioning, clarifying). - Negotiation skills (time, cost, labor requirements). - Methods for building consensus with clients. - Professional ethics and cultural considerations in client dealing. Practical Activity - Mock client meeting: collect demands and note instructions. - Practice negotiating wages, time, and labor through role-play. - Case study activity: students develop a consensus with client on a small job. - Demonstrate professional greetings, body language, and tone in client interaction. | Theory: 2Hrs. Practical: 3Hrs. Total: 5Hrs. | - Sample Job Request Forms / Work Orders - Stopwatch / Timer (for timed negotiation role-play) - Audio Recorder / Camera (optional, for feedback on role-play performance) Consumable Items: - A4 / Chart Papers - Notebooks & Pens/Pencils - Sticky Notes - Printed Client Scenarios / Case Study Sheets - Role-Play Instruction Sheets (for wage/time/labor negotiation practice) - Name Tags (for role identification in mock meetings) | - Classroom and workshop |
| Demonstrate Basic IT Skills | - Create files and folder in Microsoft Word - Demonstrate major commands of operating system/windows - Create document - Edit document - Create tables in Microsoft Word - Insert header and footer, footnotes, and page number etc. - Create table of contents - Print document - Use appropriate e-media internet for sending/receiving emails | - Basic architecture of computer system. - Input and output devices and their functions. - Introduction to Operating System / Windows environment. - Basics of MS Word: - Creating, saving, editing documents. - Formatting text and paragraphs. - Creating tables, headers/footers, page numbers, footnotes. - Creating table of contents. - Printing documents. - Basics of Email communication (sending/receiving, attachments). - Importance of paperless/digital communication for green practices. Practical Activity: - Hands-on practice of creating folders and files. - Use of basic Windows commands (copy, paste, rename, search, etc.). - Create, edit, and format a Word document. - Insert a table, header, footer, page numbers, and footnotes. - Create and update a table of contents. - Print a document. - Activity: Draft a simple job completion report in MS Word. - Practice sending/receiving emails with attachments. | Theory: 6Hrs. Practical: 25Hrs. Total: 31 Hrs | - Desktop Computers / Laptops (with Windows OS & MS Office installed) - Internet Connection (for email practice) - Printer) - Projector / Screen (for demonstrations) Consumable Items: - A4 Papers - Printer Ink / Toner Cartridges - Job Completion Report Templates (printed or digital) | - Classroom and workshop |

## 0713E&E0203 Prepare Estimates for Electrical Work

Objective:

This module identifies the competencies required to prepare estimates in accordance with client’s guidelines. The Trainee will be expected to estimate, ensuring cost effectiveness, conforming to standards and regulations. The underpinning knowledge regarding calculations and estimation will be sufficient to provide the basis for your work. Module is also focused to re-think more about green practices while calculating and developing basic drawings.

Duration: 80 Hours		Theory: 16 Hours		Practice: 64 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Develop Basic Drawing | - Collect information - Take accurate measurements regarding work specifications - Develop drawing according to job requirement - Use relevant electrical symbols and signs as per standards - Confirm the job specifications and drawing from client or supervisor - Make necessary adjustments, where required - Calculate electrical load based on the electrical installations provided in the specifications | - Introduction to Electrical Estimation and its Importance - Basic Electrical Symbols - Basic Electrical Drawings (lighting, power, distribution) - Interpret Layout Plans, Wiring Diagrams & Technical Sketches - Electrical Circuit Characteristics (current, voltage, resistance, power) - Basic Electrical Formulas & Numeracy for Estimation (Ohm’s law, Power formulas, kWh calculations) - Load Calculation Techniques for Electrical Installations Practical Activity: - Prepare basic wiring drawing of domestic installations (lighting & power circuits). - Calculate electrical load for the installation based on appliances/ electrical installations. | Theory: 6Hrs. Practical: 24 Hrs. Total: 30 Hrs. | - Template Sheets for Electrical Symbols - Calculator (for load calculation) - Multimedia Projector or Screen (optional, for showing sample layouts) Consumable Items: - Drawing Sheets | - Classroom - Workshop |
| LU2. Perform Estimation of material | - Identify requirements of the material(s) to be utilized for the work in accordance with the job specifications and drawing - Check and confirm the requirement of the materials from the client or supervisor for accurate estimation. - Quantify the material as per drawing - Use appropriate methods to calculate the of cost of material and accessories keeping in view the current market prices - Check and present the cost estimate to the client or supervisor for agreement | - Classification & Selection of Electrical Materials (cables, conduits, switchgear, protective devices, accessories) - Material Quantification Methods based on Drawings & Specifications - Pricing Survey and Cost Comparison Techniques - Cost Calculation Methods (unit rate, per point system, per circuit system) - Estimation Methods and Standard BOQ Formats - Green Practices in Estimation (cost saving, energy-efficient equipment, eco-friendly materials) Practical Activity - Identify required materials (cables, conduits, switches, sockets, DBs, fuses, etc.) from the prepared drawing. - Prepare a list of materials and accessories (quantification). - Conduct a small market survey for current prices of cables, conduits, and switches. - Calculate cost of materials using market prices. - Prepare and present a BOQ (Bill of Quantities) for the given project. | Theory: 6Hrs. Practical: 24 Hrs. Total: 30 Hrs. | - Drawing sheets / Wiring diagrams (prepared installation drawings) - Material catalogues (from local market or suppliers) - Market price lists - Printed quotations from vendors - Computer or Laptop (for BOQ preparation in MS Excel/Word) - Calculator Consumable Items: - A4 sheets / notebooks (for notes & calculations) - Printed BOQ formats / estimation | - Classroom - Workshop |
| LU3. Calculate Labor Cost | - Make necessary adjustments in estimates, where required. - Calculate hours required for the task in accordance with the job requirements - Prepare labor cost for the task using appropriate procedures. | - Labor Cost Concepts (skilled, semi-skilled, unskilled labor) - Methods of Labor Hours Calculation (task analysis, productivity rates) - Procedures of Labor Costing (per point, per job, hourly rate system) - Adjustments in Estimation based on Site Conditions & Client Requirements Practical Activity: - Estimate the man-hours required for installing a given wiring system. - Calculate labor cost using per hour or per point method. - Make adjustments in estimation if client changes requirements (extra points, conduit length, etc.). - Prepare a combined cost estimate (material + labor) for a small project. - Present the final estimate to the instructor (acting as client) for approval. | Theory: 4Hrs. Practical: 16 Hrs. Total: 20 Hrs. | - Prepared wiring layout - Computer / Laptop (for preparing combined estimates in Excel/Word) - Calculator - Task cards - job sheets (with client requirement scenarios and \changes) Consumable Items: - A4 sheets / notebooks - Printed estimation templates (labor + material cost sheets) | - Classroom - Workshop |

## 0713E&E0204- Follow Basic Green Practices for Domestic/General Electrician

Objective:

This competency standard will provide skill, knowledge and attitude required to ensure the basic green practices in the Electrical Field.

Duration: 40 Hours			Theory: 8 Hours				Practice: 32 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Help in organizing working environment | - Clean all equipment/machinery - Clean whole workplaces/work sites as instructed by management. - Maintain tools and equipment Regularly - Store equipment/machinery Properly as instructed by management. | - Importance of Clean and Safe Workplaces - Methods of Cleaning Tools, Equipment, and Machines - Safe Storage of Tools, Equipment, and Machinery - Preventive Maintenance of Tools and Equipment Practical activity - Clean and maintain a set of electrician’s tools and equipment. - Demonstrate storage of tools in toolboxes/racks. - Perform preventive maintenance of a machine (lubrication, dusting, tightening, etc.). | Theory: 1Hrs. Practical: 4Hrs. Total: 5Hrs | - Toolboxes - Cleaning brushes - Compressed air blower - Oiling can - grease gun Consumable Items: - Lubricating oil - Multipurpose grease - Rust remover spray (WD-40 or equivalent) - Cotton waste - Mild detergent solution (for cleaning plastic/insulated handles) - Sandpaper / emery cloth (for rust cleaning) - Tags or labels (for marking serviced tools) | - Classroom and workshop |
| LU2. Perform disposal of electrical waste in designated area as per SOP | - Segregate disposable and non-disposable material - Segregate materials according to disposal SOP - Dispose waste accordingly at allocated site. - Clean the workplace. | - Types of Electrical Waste (hazardous & non-hazardous) - Color Coding and Types of Waste Bins - Standard Operating Procedures (SOPs) for Waste Disposal Practical activity - Segregate different types of electrical waste (plastic, copper wires, metal scrap, insulation material, etc.). - Demonstrate use of color-coded bins for proper disposal. - Clean a designated workplace after an electrical task. | Theory: 2Hrs. Practical: 8Hrs. Total: 10Hrs | - Color-coded dustbins (Plastic, Metal, Paper, Hazardous, General Waste) - Safety gloves and masks (for handling waste safely) - Safety goggles (if handling sharp metal scrap) Consumable Items: - Waste collection bags (different colors for segregation) - Labels (to mark bins: Plastic, Copper, Metal, Hazardous, etc.) - Cleaning cloths - Disposable gloves (for one-time use during waste handling) | - Classroom and workshop |
| LU3. Reuse training material (consumables) | - Collect used material after performing tasks. - Segregate the useful material from the waste. - Store the useful material at appropriate storing place for reusing. | - Benefits of Reusing Materials in Electrical Work - Concept of Reduce, Reuse, Recycle (3Rs) - Consumable and Non-Consumable Materials - Store and Manage Reusable Materials Practical Activity - Collect leftover consumables (wires, insulation tapes, screws, connectors). - Separate reusable and non-reusable materials. - Store reusable items in an organized way for future use. | Theory: 1Hrs. Practical: 4Hrs. Total: 5Hrs | - Sorting trays / bins (for wires, screws, connectors, etc.) - Storage racks / shelves - Small drawer cabinets (for screws, nuts, bolts, connectors) - Transparent storage jars / plastic boxes (for organized storage) - Labeling machine / permanent markers & tags (to identify reusable items) - Cutting pliers / wire cutters (to trim reusable wire pieces) - Measuring tape (to measure leftover wire lengths) - Magnetic tray (for collecting small metallic items like screws/bolts) Consumable Items: - Leftover wires, insulation tapes, screws, connectors (from practice jobs) - Zip lock bags / polythene bags (to store small reusable items) - Adhesive labels / stickers (for marking bags or boxes) - Masking tape (to bundle small wire pieces neatly) | - Classroom and workshop |
| LU4. Comprehend knowledge of Renewable Energy Recourses | - Demonstrate Solar, Wind, Hydro, Geothermal energy etc. for alternate energy source. - Promote the use of natural sunlight more instead of artificial lights. - Use low carbon emission vehicles and machines | - Introduction to Renewable Energy Resources (Solar, Wind, Hydro, Geothermal, Biomass) - Benefits of Renewable Energy vs. Non-Renewable Sources - Solar Energy in Domestic Wiring - Introduction to Low Carbon Emission Vehicles and Machines - Green Transportation and Machinery for Sustainable Environment Practical Activity - Identify renewable energy resources using charts/models. - Demonstrate solar panel setup for basic lighting. | Theory: 2Hrs. Practical: 8Hrs. Total: 10Hrs | - Electrician Tool Kit - Charts / posters / models of renewable energy resources (solar, wind, hydro, biomass, etc.) - Small solar panel kit (10W–20W for demonstration) - Charge controller (suitable for the solar panel) - 12V rechargeable battery (for storing solar energy) - LED light(s) (for basic lighting demonstration) - Multimeter (for checking voltage/current from the panel and battery) - Wiring board / mounting frame (for setting up the solar panel) Consumable Items: - Connecting wires (suitable gauge for solar setup) - Electrical tape / insulation tape - Cable ties (for neat wiring) - Labels / markers (for identifying components | - Classroom and workshop |
| LU5. Practice Green Skills at Workplace | - Turn off extra lights and putting signs to switch off lights before leaving the room etc. - Minimize the use of plastic bags and other hazardous materials. - Use LED lights instead of other bulbs for power saving. - Minimize the use of paper - Use e-channel for communication | - Energy Conservation Practices at Workplace - Use of LED Lights vs. Conventional Bulbs - Minimizing Plastic and Paper Use (Green Communication) - Role of Electricians in Promoting Green Environment Practical Activity - Turn off extra lights/fans after completing a class activity. - Install a “Save Energy – Switch Off When Not in Use” signboard. - Replace a conventional bulb with an LED bulb. - Send a class notice/report through email/WhatsApp instead of paper (digital practice). | Theory: 2Hrs. Practical: 8Hrs. Total: 10Hrs | - Switchboards (with connected lights/fans for demonstration) - Sample signboard frame / display board (for mounting “Save Energy” messages) - Screwdriver set (for replacing bulbs) - Step stool / small ladder (for safe bulb replacement practice) - Computer / Laptop / Smartphone (for sending digital notices/reports via Email/WhatsApp) - Projector / screen (optional, to highlight digital practice and awareness message) Consumable Items: - “Save Energy – Switch Off When Not in Use” printed sign/poster - Conventional incandescent bulb (for demo replacement) - LED bulb (energy-efficient replacement) - Insulation tape / cable ties (if needed for bulb holder connection demo) | - Classroom and workshop |

## 0713E&E0205 - Install single-phase Electrical wiring.

Objective:

This module identifies the competencies required to install single phase domestic wiring according to the client’s demand. The trainee will be able to Maintain Tools & Equipment for Single Phase Wiring, Make Cable/Wire Joints for Single Phase Wiring, Prepare and Install Distribution Boards for Single Phase, lay cables, practice single phase electrical circuits and perform single phase electrical domestic wiring. Module is also focused to re think more about green practices while installing single phase electrical wiring.

Duration: 310 Hours        	Theory: 60 Hours 	Practice: 250 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Maintain Tools & Equipment for Single Phase Wiring electrical domestic wiring. | - Identify tools and equipment - Prepare list of tools and equipment as per requirement - Arrange Tools and Equipment - Interpret job card - Insulate Tools and Equipment - Calibrate measuring tools - Manage Inventory of tools and equipment - Maintain Tool Box | - Types and functions of electrical tools and equipment. - Tool box management and storage methods. - Preventive vs. corrective maintenance. - Insulation procedures and types. - Calibration methods for measuring instruments. - Tool/equipment inventory management. - Job card/work order – definition and importance. Practical activity - Identify and list tools & equipment for single phase wiring. - Arrange tools in tool box systematically. - Perform maintenance of selected faulty tool (corrective). - Perform insulation of hand tools. - Calibrate multimeter/measuring instruments. - Prepare inventory report for tools. | Theory: 10Hrs. Practical: 40Hrs. Total: 50Hrs. | - Toolboxes (for systematic arrangement practice) - Screwdriver set (flat & Phillips) - Pliers set (combination, long nose, side cutter) - Wire stripper & crimper tool - Hammer and measuring tape - Testers (neon tester, line tester) - Electric drill (for maintenance demonstration) - Hand tools requiring corrective maintenance (e.g., damaged screwdrivers, pliers) - Multimeter (digital & analog) - Calibration reference equipment (standard resistors, voltage source, etc.) - Insulation resistance tester (Megger) - Inventory register / computer with spreadsheet software Consumable Items: - Insulation tape (for tool insulation practice) - Heat-shrink sleeves / tubing - Lubricating oil / grease (for preventive & corrective maintenance of tools) - Cleaning cloths - Brushes - Labels / stickers (for inventory marking) - Printed inventory forms / sheets | - Classroom and workshop |
| LU2. Make Cable/Wire Joints for Single Phase Wiring |  | - Select the cable. - Strip the wire according to 50mm. - Make Cross/Twist joint - Make Straight/Married joint - Make T- Joint - Make Rat tail joint - Make Britannia joint | - Definition of conductor, wire, and cable. - Difference between cable and wire. - Types of insulation and stripping techniques. - Types of joints (straight, married, cross/twist, T-joint, Britannia, rat-tail). - Soldering – definition, types, procedure, and Safety measures. - Composition of solder and flux. - Safety measures during jointing and soldering. Practical Activity - Practice making different joints (cross, straight, T, rat-tail, Britannia). - Perform soldering on joints. - Insulate joints with proper material. - Test joints for continuity. | Theory: 10Hrs. Practical: 40Hrs. Total: 50Hrs. | - Wire stripper & cutter - Combination pliers / long-nose pliers - Screwdriver set - Bench vise / workbench (for holding wires during jointing) - Soldering iron with stand - Soldering station (if available, for temperature control) - Multimeter (for continuity testing) - Wire holders / clamps - Safety goggles & gloves - Fire extinguisher (safety during soldering) Consumable Items: - PVC insulated copper wires (different gauges) - Soldering wire (lead/tin alloy) - Flux / soldering paste - Insulation tape (PVC) - Heat-shrink sleeves / tubing - Emery paper / sandpaper (for cleaning wire ends) | - Classroom and workshop |
| LU3. Prepare and Install Distribution Boards for Single Phase |  | - Develop Basic Drawing - Prepare estimate for wiring material. - Prepare Distribution Board - Install Distribution Board. - Test Distribution board. | - Definition and purpose of Distribution Board (DB). - Components of DB (MCB, RCCB, Busbar, Neutral link). - Difference between fuse and circuit breaker. - Safety considerations in DB installation. Practical Activity - Draw a basic DB diagram. - Prepare material estimate for DB installation. - Assemble DB with MCB, RCCB, Busbar. - Mount DB on board/wall. - Connect incoming and outgoing circuits. - Test DB using tester/multimeter | Theory: 10Hrs. Practical: 40Hrs. Total: 50Hrs. | - Screwdriver set (flat, star, insulated) - Combination pliers / long-nose pliers - Wire stripper & cutter - Electric drill machine with drill bits (for mounting DB) - Measuring tape & marker - Multimeter (for testing circuits) - Test lamp / tester screwdriver - Bench vise / workbench - Safety gloves & goggles Consumable Items: - Distribution Board (metal/plastic casing) - MCBs (Miniature Circuit Breakers) – different ratings - RCCB (Residual Current Circuit Breaker) - Busbar (neutral & phase) - Copper wires (single-core, different gauges) - Cable lugs & thimbles - Insulation tape (PVC) - Screws, Rawl plugs, wall plugs & nuts/bolts (for mounting DB) - Name tags / labels (for circuit identification) | - Classroom and workshop |
| LU4. Lay cables |  | - Interpret electrical drawing/document - Identify cables - Lay cables - Perform earthling | - Types of cables and gauges used in Domestic Wiring. - Color codes for wiring. - Methods of wiring (surface, conduit, casing & capping, duct). - Earthing: need, methods, and safety. Practical Activity - Interpret wiring drawing - Lay cables in conduit/casing/duct. - Perform earthing installation. | Theory: 6Hrs. Practical: 24Hrs. Total: 30Hrs | - Wiring drawings / circuit layout charts (for interpretation practice) - Measuring tape & chalk/marker (for marking conduit paths) - Hacksaw / conduit cutter - Pipe bender (manual) - Hammer & pliers set - Screwdriver set (flat & star, insulated) - Electric drill machine with drill bits - Wire stripper & cutter - Spanner set / adjustable wrench - Earth resistance tester / multimeter - Safety gloves, safety shoes, and goggles Consumable Items: - PVC conduits, casing & capping, ducts (different sizes) - PVC bends, tees, couplers, elbows, junction boxes - Copper wires (different gauges, as per drawing) - Saddles, clamps, screws, wall plugs (for fixing conduits/casing) - Earthing rod / GI pipe with clamp - Earthing wire (green/yellow) - Charcoal, salt, and water (for earthing pit) - Insulation tape (PVC) - Cable ties / tags (for neatness & identification) | - Classroom and workshop |
| LU5. Practice single phase electrical circuit |  | - Draw wiring diagram of single-phase circuit. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | - Circuit theory (current, voltage, power, resistance). - Types of circuits: series, parallel, series-parallel. - Wiring diagrams and symbols. - Switches and control circuits (single pole, two-way, intermediate, push button). Practical Activity - Draw wiring diagrams of simple circuits. - Install different (single pole, two-way, intermediate, push button, Lamp holders, socket) circuits. - Test/Check completed circuits. | Theory: 10Hrs. Practical: 40Hrs. Total: 50Hrs. | - Whiteboard / chart papers with markers (for drawing circuit diagrams) - Sample wiring diagrams (reference sheets) - Screwdriver set (insulated, flat & star) - Pliers (combination, long-nose, side cutter) - Wire stripper & cutter - Electric drill machine with bits (for mounting boards/sockets) - Measuring tape & marker/chalk (for marking positions) - Multimeter / continuity tester - Test lamp / line tester - Hammer and spanner set - Small step ladder (for mounting lamps) - Safety gloves, safety shoes Consumable Items: - PVC insulated copper wires (different colors for phase, neutral, earth) - Switches (single pole, two-way, intermediate, push button) - Socket outlets (5A/15A) - Lamp holders (batten, pendant) with bulbs - Mounting boards / switchboards (for practice installation) - Junction boxes, casing-capping / PVC conduit with accessories (elbows, tees, couplers) - Screws, wall plugs, saddles, clamps - Insulation tape - Cable ties / labels for identification | - Classroom and workshop |
| LU6. Perform single phase electrical domestic wiring. |  | - Draw wiring diagram for single phase. - Draw Current path diagram for single phase. - Draw layout diagram for single phase. - Mark on working board according to layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | - Domestic wiring systems (surface, concealed). - Accessories and material for domestic wiring. Practical Activity - Draw single-phase wiring layout for a room/house. - Mark layout on practice board/wall. - Install accessories as per drawing (switches, sockets, holders, DB). - Lay wires in conduit/duct according to layout ad make connections. - Connect circuit to DB and main supply. | Theory: 14Hrs. Practical: 66Hrs. Total: 80Hrs. | - Drawing board / chart papers / markers (for preparing layout diagrams) - Practice wiring boards / demo wall panels (for mounting layout) - Measuring tape, chalk/marker, pencil (for marking layout) - Screwdriver set (flat & Phillips, insulated) - Pliers (combination, long-nose, side cutter) - Wire stripper & cutter - Electric drill machine with drill bits (for fixing conduit/boards) - Multimeter (for voltage, current, resistance check) - Continuity tester / test lamp - Spirit level (for alignment of boards and switches) - Hammer, spanners, adjustable wrench - Step stool / ladder (for mounting accessories at height) - Safety gloves, safety shoes, goggles Consumable Items: - PVC insulated copper wires (different colors for phase, neutral, earth) - PVC conduit pipes / casing-capping with bends, elbows, tees, couplers - Switches (single pole, two-way as required) - Socket outlets (5A/15A) - Lamp holders (batten/pendant) with bulbs/tubes - Distribution Board (DB) with MCBs, RCCB, busbar - Junction boxes, surface boards, back boxes - Screws, wall plugs, saddles, clamps, rawl bolts - Insulation tape (different colors if possible) - Cable ties / ferrules for wire identification - Name plates/labels for DB circuits | - Classroom and workshop |

## 0713E&E0206- Perform Testing of Electrical Wiring

Objective:

This module covers the skills and knowledge required to Perform Earth leakage Test, Perform Open Circuit Test, Perform Short Circuit Test, Perform Continuity/Loop Test, Perform Visual Test, Perform Insulation Test, Perform Polarity Test, Perform Earth Resistance Test, Perform Murray Loop Test, and Perform BLAVIER & Earth Loop Test.

Duration: 40 Hours        	Theory: 8 Hours 	Practice: 32 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Perform Earth leakage Test. | - Ensure the socket must be at least 13A for RCD plug in. - Adjust the sensitivity of RCD. - Ensure tripping time must not exceed than 200msec. - Plug the RCD in socket and switch on socket outlet. - Ensure P-N and P-E light up. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. - Move the selection switch to 180o. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. - Move selection switch to 00. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. | - Introduction to Electrical Wiring Testing - Concept of Earth leakage current. - Hazards of leakage current (electric shock, fire risk). - Introduction to RCD (Residual Current Device) - Sensitivity and tripping time of RCD - Importance of P-E (Phase–Earth) and P-N (Phase–Neutral) connections - Procedure of testing Earth Leakage. - Safety precautions during testing. Practical activity - Connect and operate RCD plug in a 13A socket - Adjust sensitivity of RCD - Perform Earth leakage test at 0°, 180° and 0° switch positions - Record tripping time and verify if ≤ 200 msec - Record results and compare with standard values. | Theory: 1Hrs. Practical: 4Hrs. Total: 5Hrs. | - 13A socket outlet (installed on practice board) - RCD plug (portable type, 30mA sensitivity) - Test bench wiring board / training panel - Digital multimeter (for voltage/current checks) - RCD / Earth Leakage Tester (to measure tripping time and leakage current) - Stopwatch (optional, if manual time recording is required) - Screwdriver set (insulated) - Pliers (combination, long-nose) - Insulation resistance tester (Megger) – optional for verification - Computer / notebook for recording results Consumable Items: - Flexible copper wire with plugs (for test connections) - Insulation tape (for safe joints, if required) - Labels/markers (for recording socket and test positions) - Record sheets / printed test log format (for entering tripping time & results | - Classroom and workshop |

| LU2. Perform Open Circuit Test | - Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. - Connect ohmmeter between starting and ending terminals of live conductor. - Ensure the reading must be near to 0 ohm. - Repeat P2 to P3 for neutral and earth conductor. | - Definition of open circuit. - Causes of open circuit faults (loose connections, broken conductor, faulty switches). - Identification methods of open circuits. - Megger application for open circuit detection. Practical Activity - Perform open circuit test using continuity tester/multimeter. - Perform open circuit test using Megger. - Trace and locate fault point in a wiring setup. | Theory: 0.5Hrs. Practical: 2Hrs. Total: 2.5Hrs. | - Continuity tester - Digital multimeter (for voltage, resistance, and continuity checks) - Insulation resistance tester (Megger) - Practice wiring board (with deliberately introduced open-circuit faults) - Screwdriver set (insulated) - Pliers (combination, long-nose) - Wire stripper/cutter - Small torch/flashlight (for fault tracing in ducts or boards) Consumable Items: - Test wires/leads (with crocodile clips) - Insulation tape (for safe insulation after fault correction) - Markers/labels (to identify faulty circuits and trace points) - Fault record sheet (printed format for documenting tests and results) | - Classroom and workshop |
| --- | --- | --- | --- | --- | --- |
| LU3. Perform Short Circuit Test | - Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. - Connect one terminal of ohmmeter with live conductor. - Connect the other terminals of ohmmeter with neutral conductor. - Ensure the reading must be infinity (No reading). - Connect ohmmeter between live conductor and earth conductor. - Ensure the reading must be infinity (No reading) | - Definition of open circuit - Causes of short circuit (damaged insulation, wrong connections) and its dangers. - Identification methods of short circuits. - Megger application for short circuit detection. Practical Activity - Identify short circuit fault using multimeter/megger. - Demonstrate short circuit protection through fuse/MCB operation. - Record results and suggest corrective action. | Theory: 0.5Hrs. Practical: 2Hrs. Total: 2.5Hrs. | - Digital multimeter (for continuity and short-circuit detection) - Insulation resistance tester (Megger) - Distribution Board (DB) with MCBs & fuses (for demo of tripping) - Practice wiring board (with deliberate short-circuit fault) - Screwdriver set (insulated) - Pliers (combination & long nose) - Wire stripper/cutter - Clamp meter (optional – for measuring current during short circuit demo) Consumable Items: - Test wires/leads with crocodile clips - Fuse wire (for demonstrating fuse operation) - Insulation tape (for corrective repair after short circuit removal) - Fault simulation sheet (showing type/location of fault) - Record sheet (to note readings, tripping behavior, corrective action) | - Classroom and workshop |
| LU4. Perform Continuity/Loop Test | - Connect all metal clad switches, metal parts, conduits with earth. - Open the main switch. - Turn on all the switches. - Connect earth continuity tester with conduit and independent earth. - Measure the resistance value with tester which must not be more than 1 ohm. | - Definition of continuity in circuits. - Importance of earth continuity in safety. - Understanding of Continuity/Loop Test. - Megger application for Continuity/Loop Test. Practical Activity - Perform continuity test of conductors using ohmmeter/multimeter. - Perform earth continuity test using Megger. - Record and interpret results. | Theory: 0.5Hrs. Practical: 2Hrs. Total: 2.5Hrs. | - Digital/Analog Multimeter (with Ohmmeter function) - Insulation Resistance Tester (Megger) - Practice Wiring Board (with conductors & earthing arrangement) - Screwdriver set (insulated) - Pliers (combination & long nose) - Wire stripper/cutter - Crocodile clips & test leads Consumable Items: - Wires/conductors (for continuity testing practice) - Earth wire connected to electrode (for earth continuity test) - Insulation tape (for repairing/testing connections) - Record sheet / Test logbook (for entering measured values and interpretation) | - Classroom and workshop |
| LU5. Perform Visual Test | - Check the wires joints. - Check if there is any spark. - Check over heating of wires. - Check all the appliances are on or fluctuating. - Check all indications of meters. - Check Voltages on all phases. - Check the DB and Breakers. - Check the main supply is coming properly. | - Importance of visual inspection before energizing installation. - Checklist for visual test (wiring, insulation, sockets, switches, earthing). - IEC/NEC/Pakistan Electrical Safety Code references. Practical Activity - Perform visual inspection of wiring board/lab wiring. - Identify visible faults (loose joints, improper connections, damaged insulation). - Prepare inspection report. | Theory: 0.5Hrs. Practical: 2Hrs. Total: 2.5Hrs. | - Practice Wiring Board / Lab Wiring Setup - Insulated Screwdriver Set (for tightening loose connections) - Torch / Inspection Lamp (for visibility in concealed/low-light areas) - Magnifying glass (optional, for close inspection) - Digital Camera / Smartphone (for taking pictures of faults as evidence) - Computer / Laptop (for preparing inspection report) Consumable Items: - Inspection Checklist Sheet / Printed Proforma - Fault Reporting Logbook - Insulation Tape (for temporary correction of minor insulation issues) - Tags / Labels / Markers (to mark faulty points during inspection) | - Classroom and workshop |
| LU6. Perform Insulation Test | - Switch off the main breaker. - Short circuit all lighting connections. - Connect megger between line and earth. - Rotate the merger to generate the voltage. - Read the merger dial and ensure that the insulation resistance should not be less than 50M ohm of any single circuit. | - Definition and concept of insulation resistance. - Factors affecting insulation resistance (temperature, humidity, material). - Standard values of insulation resistance (as per NEC/IEC). - Megger application insulation test. Practical Activity - Perform insulation resistance test between L–N, L–E, N–E using Megger. - Interpret readings (>50 MΩ = acceptable). - Record test report. | Theory: 1Hrs. Practical: 4Hrs. Total: 5Hrs. | - Megger / Insulation Resistance Tester - Test Leads / Probes (compatible with Megger) - Practice Wiring Board / Lab Wiring Setup - Personal Protective Equipment (Insulated Gloves, Safety Goggles) - Multimeter (for cross-verification if required) - Computer / Laptop (for recording test report) Consumable Items: - Insulation Tape (for temporary correction if needed) - Test Report Sheet / Printed Proforma - Tags / Labels (to mark tested circuits) | - Classroom and workshop |
| LU7. Perform Polarity Test | - Switch off the main switch. - Disconnect all loads. - Switch on all circuit control switches. - Connect ohm meter between main line and all the terminal of sockets and load points one by one. - Ensure meter reading value must be less than 1 ohm. | - Definition and concept of polarity in electrical wiring. - Importance of correct polarity (for safety of appliances). - Procedure for polarity test. Practical Activity - Perform polarity test of single-phase sockets using Megger/Continuity tester. - Verify phase and neutral positions with test lamp. - Record and analyze results | Theory: 1Hrs. Practical: 4Hrs. Total: 5Hrs. | - Megger / Continuity Tester - Test Lamp / Socket Tester - Practice Wiring Board / Lab Socket Setup - Insulated Screwdriver (for safe probing if required) - Personal Protective Equipment (Insulated Gloves, Safety Goggles) - Multimeter (optional for verification) - Computer / Laptop (for recording results) Consumable Items: - Test Report Sheet / Printed Proforma - Tags / Labels (to mark tested sockets) - Insulation Tape (if minor corrections needed during testing) | - Classroom and workshop |
| LU8. Perform Earth Resistance Test | - Place 3 electrodes in earth at distance of 10m apart between every electrode. - Connect terminal E of earth resistance tester to first electrode. - Connect terminal P of earth resistance tester to the second electrode. - Connect terminal C of the earth resistance tester with third electrode. - Measure the resistances after applying specific voltage. - Repeat P1 to P5 by interacting earthling regions. - Ensure 3 readings must be equal. | - Purpose of earthing and its importance in electrical safety. - Methods of earth resistance measurement. - Standard values of earth resistance. Practical Activity - Perform earth resistance measurement using Earth Tester - Demonstrate three-point method with auxiliary electrodes. - Record test report and suggest improvements. | Theory: 1Hrs. Practical: 4Hrs. Total: 5Hrs. | - Earth Resistance Tester / Earth Megger - Auxiliary Electrodes (3 rods for three-point method) - Connecting Leads / Test Wires - Hammer / Mallet (to insert electrodes in the ground) - Measuring Tape (to maintain correct electrode spacing) - Personal Protective Equipment (Insulated Gloves, Safety Goggles) - Multimeter (optional for verification) - Computer / Laptop (for recording results) Consumable Items: - Test Report Sheet / Printed Proforma - Tags / Labels (to mark tested points) - Chalk / Marker (for marking electrode positions) | - Classroom and workshop |
| LU9. Perform Murray Loop Test | - Connect galvanometer with Wheatstone bridge. - Connect positive terminal of DC source with Wheatstone bridge. - Connect negative terminal of DC source with ground. - Connect remaining two terminal of Wheatstone bridge with two cores of the cable. - Short the other end of these two cores of cable. - Note the reading of galvanometer. - Calculate Rx. - Repeat the P1 to P7 for other cores of the cable. | - Concept of underground cable fault location. - Principle of Wheatstone bridge in fault detection. - Procedure of Murray loop test. Practical Activity - Set up Murray loop test circuit with galvanometer. - Locate simulated fault in underground cable model. - Record and interpret results. | Theory: 1Hrs. Practical: 4Hrs. Total: 5Hrs. | - Galvanometer (sensitive, for Murray loop test) - DC Power Supply - Wheatstone Bridge Setup (for Murray loop) - Underground Cable Model / Sample Cable with simulated fault - Connecting Leads / Test Wires - Switches (for opening/closing circuit) - Multimeter (optional for verification) - Insulated Gloves & Safety Goggles - Measuring Tape (for cable length reference) - Notebook / Laptop (for recording readings) Consumable Items: - Tags / Labels (to mark fault points) - Chalk / Marker (for cable labeling) - Test Report Sheet / Printed Proforma | - Classroom and workshop |
| LU10. Perform BLAVIER & Earth Loop Test | - Connect galvanometer with Wheatstone bridge. - Connect positive terminal of DC source with Wheatstone bridge. - Connect negative terminal of DC source with ground. - Connect remaining two terminal of Wheatstone bridge with two cores of the cable. - Short the other end of these two cores of cable. - Note the reading of galvanometer. - Calculate Rx. - Repeat the P1 to P7 for other cores of the cable. | - Faults in underground cables. - Working principle of Blavier test. - Difference between Murray loop and Blavier test. Practical Activity - Perform Blavier test using standard circuit. - Locate fault position in underground cable model. - Record findings and compare with expected results. | Theory: 1Hrs. Practical: 4Hrs. Total: 5Hrs. | - Galvanometer (sensitive, for Blavier test) - DC Power Supply - Wheatstone Bridge Setup (for Blavier loop) - Underground Cable Model / Sample Cable with simulated fault - Connecting Leads / Test Wires - Switches (for opening/closing circuit) - Multimeter (optional for verification) - Insulated Gloves & Safety Goggles - Measuring Tape (for cable length reference) - Notebook / Laptop (for recording readings) Consumable Items: - Tags / Labels (to mark fault points) - Chalk / Marker (for cable labeling) - Test Report Sheet / Printed Proforma | - Classroom and workshop |

## 0713E&E0207 - Install Security & Electrical Communication Systems

Objective:

This module identifies the competencies required to install security & communication system in domestic and commercial buildings. The underpinning knowledge regarding the installation of Security & Communication System will be sufficient to provide the basis for your work. The module also focuses on maintaining green TVET concept by adopting 6 Rs of Green Skills i.e. Recycle, Reduce, Reuse, Renew, Repair, Rethink concepts.

Duration: 40 Hours        	Theory: 8 Hours 	Practice: 32 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials (Tools & Equipment) | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Select the type of Safety / Security & Communication System | - Inspect the premises for installation of safety / security and communication system as per requirement - Select the most appropriate safety / security/ communication system considering the practicality of the system, cost and client requirements | - Introduction to Security & Communication Systems (importance, applications, domestic vs commercial use). - Types of Safety / Security Systems (CCTV, fire alarms, intruder alarms, access control). - Types of Communication Systems (intercoms, telephone exchange, data networking basics). - Client requirements, cost factors, practicality of different systems. Practical Activity: - Inspect & prepare a layout/sketch the premises to identify installation requirements. - Select and enlist the most appropriate safety/security/communication system considering practicality, cost & client requirements. | Theory: 2Hrs. Practical: 8Hrs. Total: 10Hrs. | - Measuring Tape / Laser Distance Meter (for layout measurements) - Ruler / Scale / Graph Paper (for sketching) - Clipboard / Drawing Board - Sample Security / Communication Devices (CCTV camera, sensors, intercom, alarm) - Electrical Calculator / Laptop (for cost calculations) - Markers / Pencils / Erasers (for drawing/layout) - Safety Gloves & Goggles (for handling sample devices) Consumable Items: - Drawing Sheets / A4 Paper - Sticky Notes / Labels (to mark locations) - Printed Manufacturer Specifications / Catalogs - Tape (for marking premises layout on floor/walls) | - Classroom and workshop |
| LU2. Install Safety / Security & Communication System | - Select Tools, test instruments & material as needed for the work - Select Conduits/ trunk, cables, wire & switch gear and accessories according to the requirements - Mark the Location for safety / security and communication fixtures for installation, Conduits / casing and capping laid / fixed according to the wiring diagram avoiding possible electrical interferences on other systems - Lay the Wires / cables according to wiring diagram - Mount the safety / security and communication fixtures at the specified locations as per manufacturer’s specifications and considering client’s requirements - Install the standby power back up system as per requirement | - Tools & testing instruments used in installation (multimeter, CCTV tester, clamp meter). - Wires & cables (power vs communication, ratings, color coding, shielding). - Conduits, trunking, switchgear & accessories. - Types of cameras (IP, analog, PTZ, dome, bullet), sensors (motion, smoke, heat, glass break). - Power backup systems (UPS, batteries, solar). - Installation procedures (reading diagrams, marking, cable routing, mounting). Practical Activity: - Select required tools, instruments, and materials. - Mark locations for fixtures and lay conduits/casing neatly. - Lay wires/cables according to wiring diagram. - Mount devices (CCTV cameras, sensors, alarms, intercoms) per manufacturer’s specs. - Install standby power backup system. | Theory: 4Hrs. Practical: 16Hrs. Total: 20Hrs. | - Screwdriver Set / Power Drill - Conduit Bender / Pipe Cutter - Measuring Tape / Laser Distance Meter - Wire Stripper / Cable Cutter - Pliers / Crimping Tool - Multimeter / Continuity Tester - Ladder / Step Stool (for mounting devices) - Clamp / Fastening Tools (for conduits and devices) - Sample CCTV Cameras, Sensors, Alarms, Intercoms - UPS / Backup Power Supply (for standby installation) - Safety Gloves & Goggles Consumable Items: - Conduits / Casing / Trunking - Electrical Wires / Cables - Cable Ties / Insulation Tape - Screws, Anchors, Mounting Brackets - Labels / Markers (for identifying circuits and devices) | - Classroom and workshp |
| LU3. Test the Installed system | - Connect the system to the power source as recommended by the manufacturer. - Adjust Settings, directions where necessary for correct functioning of the system - Check the standby power backup for its proper functioning - Perform testing of the system - Inform the client on the operating procedure and periodic testing of the system | - Testing of electrical & communication systems (continuity, insulation, voltage checks). - Adjustments & Settings (camera direction, alarm sensitivity, intercom clarity). - Importance of regular inspections & preventive maintenance. - Documentation & reporting procedures. Practical Activity: - Connect installed system to the power source safely. - Adjust settings and directions where necessary for proper operation. - Check backup system operation. - Perform complete system testing and demonstrate results. - Inform client on operation, periodic testing & maintenance procedures. | Theory: 2Hrs. Practical: 8Hrs. Total: 10Hrs. | - Multimeter / Voltage Tester - Clamp Meter (for current measurement) - Screwdriver Set / Power Drill - Laptop or Tablet (for system configuration, if required) - Ladder / Step Stool (for adjusting devices) - Safety Gloves & Goggles - UPS / Backup Power Supply (already installed) Consumable Items: - Electrical Wires / Cables (for final connections) - Cable Ties / Insulation Tape - Labels / Markers (for devices and circuits) - User Manual / Instruction Sheet (for client demonstration) | - Classroom and workshop |

# List of Personal Protective Equipment (For a Class Of 25 Students)

| Name of Trade |  | General/Domestic Electrician Level-2 |  |
| --- | --- | --- | --- |
| Duration of Course |  | 6 Months |  |
| Sr. No. | Tools and Equipment |  | Quantity (for 25 Students) |
| 1 | Safety Helmet |  | 25 |
| 2 | Safety Goggles |  | 25 |
| 3 | Face Shield |  | 25 |
| 4 | Insulated Gloves |  | 25 |
| 5 | Safety Shoes |  | 25 |
| 6 | Ear Protection (Ear Muffs / Ear Plugs) |  | 25 |
| 7 | Dust Mask (Reusable) |  | 25 |
| 8 | Safety Harness |  | 25 |
| 9 | High-visibility Jacket |  | 25 |
| 10 | Apron |  | 25 |
| 11 | Insulated Mats |  | 5 |
| 12 | Safety Sign Boards (Metal/Plastic) |  | 10 |
| 13 | PPE Storage Cabinet |  | 2 |
| 14 | Electrician Tool Kit (128 items) |  | 25 |
| 15 | Torque Wrench |  | 5 |
| 16 | Circuit Breaker Cover |  | 10 |
| 17 | Torch (Rechargeable, heavy duty) |  | 10 |
| 18 | CPR Manikin (Adult) |  | 2 |
| 19 | CPR Manikin (Child/Infant) |  | 1 |
| 20 | AED Training Unit (Demo) |  | 1 |
| 21 | Training Mat (for CPR practice) |  | 2 |
| 22 | Stopwatch / Timer |  | 5 |
| 23 | Multimedia Projector / Screen |  | 1 |
| 24 | Emergency Alarm System (Sirens / Flash Alarms) |  | 2 |
| 25 | Fire Alarm Switch / Manual Call Point |  | 2 |
| 26 | Public Address (PA) System / Megaphone |  | 2 |
| 27 | Emergency Exit Signs (Illuminated/Glow) |  | 10 |
| 29 | Safety Cones / Barricade Tape |  | 10 |
| 30 | Rescue Tools (Fire Blanket) |  | 1 set |
| 31 | Desktop Computers / Laptops (with MS Office) |  | 5 |
| 32 | Printer |  | 1 |
| 38 | Ladder (small) |  | 5 |
| 39 | Megger Meter |  | 2 |
| 40 | Insulation Resistance Tester (digital) |  | 2 |
| 41 | Digital Multimeter |  | 5 |
| 42 | Clamp on Meter |  | 5 |
| 43 | Galvanometer (for cable fault test) |  | 5 |
| 44 | DC Power Supply (for test setup) |  | 2 |
| 45 | Wheatstone Bridge Setup |  | 2 |
| 46 | Measuring Tape |  | 25 |
| 47 | Soldering Iron with Stand |  | 10 |
| 48 | Bench Wise / Workbench |  | 5 |
| 49 | Pedestal Electric Drill Machine with Bits |  | 1 |
| 50 | Color-coded Dustbins (5 types) |  | 10 |
| 51 | Small Solar Panel PV |  | 10 |
| 52 | Charge Controller |  | 5 |
| 53 | 12V Rechargeable Battery |  | 5 |
| 54 | CCTV Cameras / Sensors / Alarms (Demo Units) |  | 3 |
| 55 | UPS / Backup Power Supply (Demo) |  | 10 sets |
| 56 | Network CCTV IP Cameras (6 MP) |  | 05 |
| 57 | NVR (Network Video Recorder) |  | 02 |
| 58 | Network Switches (8 Port Gigabit POE Switch) |  | 02 |
| 59 | Network Switches Rack / Network Switches Rack |  | 02 |
| 60 | Smart LED: Size -32 INCHS |  | 01 |
| 61 | Crimping Tool RJ 45 (LAN Connector Tool) |  | 02 |

List of Consumable Materials:

| Sr. No. | Consumable | Quantity (for 25 Students) |
| --- | --- | --- |
| 1 | Safety Posters | 25 |
| 2 | Disposable Gloves | 500 pairs |
| 3 | Disposable Masks | 500 |
| 4 | Hand Sanitizer Bottles (500 ml) | 25 |
| 5 | Disinfectant Spray | 10 |
| 6 | Floor Safety Marking Tape | 20 rolls |
| 7 | Cleaning Cloths | 50 |
| 8 | First Aid Box | 2 |
| 9 | Scissors (Medical) | 5 |
| 10 | Tweezers | 5 |
| 11 | Cotton Rolls | 10 packs |
| 12 | Antiseptic Solution (Dettol) | 5 liters |
| 13 | Pyodine Solution | 10 bottles |
| 14 | Antiseptic Cream | 10 tubes |
| 15 | Ointment | 10 tubes |
| 16 | Burn Cream | 10 tubes |
| 17 | Pain Relief Spray / Gel | 10 |
| 18 | Sterile Gloves (Disposable) | 250 pairs |
| 19 | Adhesive / Medical Tape | 20 rolls |
| 20 | Elastic Bandages (Crepe) | 20 |
| 21 | Burn Dressings / Gel Packs | 10 |
| 22 | Instant Cold Pack | 10 |
| 23 | Medicines (Painkillers, ORS, etc.) | As required |
| 24 | Fire Extinguishers (Water, CO₂, Dry Powder, Foam) | 4 |
| 25 | Inspection Tags | 50 |
| 26 | Checklist Sheets | 100 |
| 27 | Lubricating Oil | 5 liters |
| 28 | Grease | 2 kg |
| 29 | Rust Remover Spray | 5 |
| 30 | Sandpaper / Emery Cloth | 25 sheets |
| 31 | A4 / Chart Papers | 500 sheets |
| 32 | Notebooks & Pens/Pencils | 25 |
| 33 | Sticky Notes | 10 pads |
| 34 | Printed Role-Play / Client Scenarios | 25 |
| 35 | Name Tags | 25 |
| 36 | Printer Ink / Toner | 2 |
| 37 | Job Report Templates (Printed) | 50 |
| 38 | Drawing Sheets | 200 |
| 39 | Market Price Lists / Quotations (Printed) | 25 sets |
| 40 | Estimation Templates (Printed) | 25 |
| 41 | Mild Detergent Solution | 5 liters |
| 42 | Zip Lock Bags (for storage) | 50 |
| 43 | Adhesive Labels / Stickers | 50 |
| 44 | Connecting Wires (for Solar Kit) | 50 m |
| 45 | Electrical Tape | 50 rolls |
| 46 | Cable Ties | 500 |
| 47 | “Save Energy” Posters | 25 |
| 48 | Conventional Bulbs | 10 |
| 49 | LED Bulbs | 10 |
| 50 | PVC Wire 1/0.044” | 5 Coil |
| 51 | PVC Wire 3/0.029” | 10 Coil |
| 52 | PVC Wire 7/0.029” | 2 Coil |
| 53 | PVC Wire 23/0.076” | 4 Coil |
| 54 | Switches (Single/Two-Way) | 50 |
| 55 | Socket Outlets (5A/15A) | 25 |
| 56 | Lamp Holders + Bulbs | 25 |
| 57 | Junction Boxes | 25 |
| 58 | Screws / Wall Plugs / Clamps | 200 |
| 59 | Cable Lugs & Thimbles | 50 |
| 60 | Charcoal, Salt & Water (for earthing) | As required |
| 61 | Fuse (Rewire able) | 20 |
| 62 | Fault Simulation Sheets | 25 |
| 63 | Record Sheets / Test Logbooks | 50 |
| 64 | Network (LAN ) Cable | 01 Coil |

# Members of Qualification Development Committee

The Qualifications Development Committee consisted of the following members:

| Sr. # | Name | Designation | Organization |
| --- | --- | --- | --- |
| 1 | Engr. Syed Waqar ed Din | Director Curriculum | TEVTA Lahore |
| 2 | Ms. Saima Asghar | DACUM Facilitator | LAHORE |
| 3 | Engr. Hafiz Waqas Hashmi | Assistant Director | P-TEVTA |
| 4 | Syed Salman Nasir Ali Shah | DACUM Expert/ Director (AA) Academics | P-TEVTA |
| 5 | Hamza Nadeem | Representative | NAVTTC Islamabad |
| 6 | Muhammad Rehan Qureshi | Senior Instructor Electrical | P-TEVTA |
| 7 | Muhammad Naveed Bashir | Instructor Electrical | P-TEVTA |
| 8 | Muhammad. Saeed | Senior Instructor Electrical | P-TEVTA |
| 9 | Mr. Maqsood Ahmad | Senior Instructor Electrical | PVTC |
| 10 | Mr. Sohaib Hassan | Instructor Electrical | PVTC |